May 25, 2001

STATE WATER RESOURCES CONTROL BOARD

WORKSHOP -- OFFICE OF CHIEF COUNSEL

JUNE 6, 2001

# ITEM 5

## SUBJECT

PETITION OF VOICES OF THE WETLANDS, MONTEREY PARKWAY, AND CAROLYN NIELON FOR REVIEW OF Waste Discharge Requirements No. 00-041 (NPDES No. CA0006254; Moss Landing Power Plant) Issued by the California Regional Water Quality Control Board, Central Coast Region.  SWRCB/OCC FILE A-1339, A-1339(a), AND A-1339(b)

## LOCATION

The power plant and the water bodies potentially affected by its operation are located in Monterey County.

## DISCUSSION

The Central Coast Regional Water Quality Control Board issued a permit to Duke Energy for the operation of the Moss Landing Power Plant.  Of seven generating units operated by PG&E, the former owner of Moss Landing, only two remained in service.  Duke proposes to replace the five non-operating units with two new ones.  Because the new generating units constitute a new discharge, Duke was required to comply with the terms of the State Board’s Thremal Plan.

Three petitions for review were received.  Among them one significant issue was raised:  whether the waste discharge requirements contained enforceable conditions that will assure compliance with the Thermal Plan.

The proposed order concludes that additional language should be added to the order to assure compliance with the Thermal Plan and amends the order to include such language.

## POLICY ISSUE

Is it necessary to amend the waste discharge requirements to assure compliance with the Thermal Plan?

## FISCAL IMPACT

Slight increase in the level of required monitoring.

## RWQCB IMPACT

None.

## STAFF RECOMMENDATION

Adopte the order as proposed.

STATE OF CALIFORNIA

STATE WATER RESOURCES CONTROL BOARD

ORDER WQ 2001-xx

In the Matter of the Petition of

# VOICES OF THE WETLANDS, MONTEREY PARKWAY,
AND CAROLYN NIELSON

For Review of Waste Discharge Requirements No. 00-041 (NPDES No. CA0006254)

Issued by the

California Regional Water Quality Control Board,

Central Coast Region

SWRCB/OCC FILE A-1339, A-1339(a), and A-1339(b)

BY THE BOARD:

The Central Coast Regional Water Quality Control Board (Regional Board) issued waste discharge requirements to Duke Energy North America (Duke) for the operation of the Moss Landing Power Plant, Units 1, 2, 6, and 7 in Monterey County.  The requirements were adopted by the Regional Board on October 27, 2000.

Timely petitions were received from a group called Voices of the Wetlands, another group called Monterey Parkway, and an individual named Carolyn Nielson.

I.  BACKGROUND

The Moss Landing Power Plant has been in operation since 1950.  Duke purchased the plant from Pacific Gas and Electric Company (PG&E) in July 1998.  At that time the plant was regulated by the Regional Board pursuant to an order issued in 1995.  The plant had seven generating units but only two were in operation at the time the last permit was issued.  Duke proposes to modernize the plant by replacing the five retired steam-turbine generators with two new natural gas-fired combined-cycle generators.  The two existing generators will remain in use.

The Regional Board has coordinated its review of the waste discharge requirements with the permit approval process of the California Energy Commission (CEC).  Together the Regional Board and the CEC established a Technical Working Group consisting of three independent scientists.  The Group met on a regular basis and reviewed the technical aspects of the proposed waste discharge requirements and the CEC permit.  The CEC acted as lead agency for purposes of compliance with the California Environmental Quality Act (CEQA).

The Regional Board held two lengthy public hearings to consider issuance of the waste discharge requirements.  The first hearing took place on September 15, 2000.  The Regional Board then continued the hearing to October 27 so that the Regional Board could obtain additional information concerning two issues:  the offshore intake station and the Environmental Enhancement Program.  Thereafter, the Regional Board adopted the waste discharge requirements.

II.  CONTENTIONS AND FINDINGS

The three petitions raise a number of issues.  However, with one exception, those issues are non-substantial and will not be discussed in this order.  Most of the issues raised by the three petitions concern either the CEC process or CEQA compliance.  As was noted above, the CEC was the lead agency for purposes of CEQA compliance.  Other contentions are mere assertions that are not supported by evidence or argument.

Contention:  The waste discharge requirements contain no enforceable conditions that will assure compliance with the Thermal Plan requirements.

Finding:  This contention has merit.

The Regional Board determined that the modifications to the facility require that the plant be treated as a “new discharge” for purposes of compliance with the State Water Resources Control Board’s Water Quality Control Plan for Control of Temperature in the Coastal and Interstate Waters and Enclosed Bays and Estuaries of California (Thermal Plan).  In Finding No. 34 of the waste discharge requirements, the Regional Board accurately sets forth what the Thermal Plan requires for new elevated temperature discharges.

FINDING 34.  The upgraded facility is a “new discharge” pursuant to the Thermal Plan.  The Thermal Plan requires the following for new elevated temperature discharges:

a.  Elevated temperature wastes shall be discharged to the open ocean away from the shoreline to achieve dispersion through the vertical column.

b.  Elevated temperature wastes shall be discharged a sufficient distance from areas of special biological significance to assure the maintenance of natural temperature in these areas.

c.  The maximum temperature of the thermal waste discharge shall not exceed the natural temperature of the receiving water by more than 20º F.

d.  The discharge of elevated temperature wastes shall not result in increases in the natural water temperature exceeding 4º F at 1) the shoreline, 2) the surface of any ocean substrate, 3) the ocean surface beyond 1,000 feet from the discharging system.  The surface temperature limitation shall be maintained at least 50% of the duration of any complete tidal cycle.

e.  Additional limitations shall be imposed when necessary to assure protection of beneficial uses.

The fundamental problem with the waste discharge requirements is that the order portion of the waste discharge requirements does not include provisions that assure compliance with the conditions listed in Finding 34.  The order deals with thermal discharges in three ways.  First, the discharger is required to meet a series of temperature related effluent limitations.  Second, there is a brief narrative statement in the receiving water limitations to the effect that “temperature of the receiving water [shall not] adversely affect beneficial uses.”  Finally, there is a requirement in the monitoring program that the discharger submit a “comprehensive plan for determining the dispersion of the thermal plume under actual operating conditions six months prior to the start-up of the new unit(s).”  The provision of the Thermal Plan requiring that the maximum temperature of the thermal waste be no more than 20° F above the natural temperature of the receiving water (provision c in Finding 34) is not considered in this order.  It was the subject of a March 7, 2001 resolution (No. 2001-034) issued by this Board granting a limited exception to the Thermal Plan.

While it is certainly possible, even likely, that this three-pronged approach will achieve compliance with the Thermal Plan, there is nothing in the order to assure that the requirements of Finding 34 will be met.  Language must be added to the order that provides for compliance with the Thermal Plan.  The plan required in the Monitoring and Reporting Program should be modified to assure compliance with these changes.

/ / /

/ / /

/ / /

III.  CONCLUSION

The waste discharge requirements issued by the Regional Board fail to assure compliance with the Thermal Plan.  Additional language must be inserted in the order to assure such compliance.

IV. ORDER

IT IS HEREBY ORDERED THAT the permit be amended to add the following language:

C.  RECEIVING WATER LIMITATIONS

19.	i.	Elevated temperature wastes shall be discharged to the open ocean away from the shoreline to achieve dispersion through the vertical column.

ii.	Elevated temperature wastes shall be discharged a sufficient distance from areas of special biological significance to assure the maintenance of natural temperature in these areas.

iii.	The discharge of elevated temperature wastes shall not result in increases in the natural water temperature exceeding 4º F at 1) the shoreline, 2) the surface of any ocean substrate, 3) the ocean surface beyond 1,000 feet from the discharging system.  The surface temperature limitation shall be maintained at least 50% of the duration of any complete tidal cycle.

D.  PROVISIONS

11.  Discharger shall submit to the Executive Officer, before start-up of the new units, monitoring data or other information demonstrating that:

i.	Elevated temperature wastes will be discharged to the open ocean away from the shoreline to achieve dispersion through the vertical column.

ii.	Elevated temperature wastes will be discharged a sufficient distance from areas of special biological significance to assure the maintenance of natural temperature in these areas.

iii.	The discharge of elevated temperature wastes will not result in increases in the natural water temperature exceeding 4º F at 1) the shoreline, 2) the surface of any ocean substrate, 3) the ocean surface beyond 1,000 feet from the discharging system.  The surface temperature limitation shall be maintained at least 50% of the duration of any complete tidal cycle.

If the monitoring data or other information submitted to the Executive Officer indicate that non-compliance with any of these requirements will result from the discharge, the Executive Officer shall propose additional limitations to the Board that will assure protection of beneficial uses.

CERTIFICATION

The undersigned, Clerk to the Board, does hereby certify that the foregoing is a full, true, and correct copy of an order duly and regularly adopted at a meeting of the State Water Resources Control Board held on June 21, 2001.

AYE:

NO:

ABSENT:

ABSTAIN:

DRAFT

Maureen Marché

Clerk to the Board

See People v. Berry (1987) 194 Cal.App.3d 158 [239 Cal.Rptr.349], California Code of Regulations, title 23, section 2052.

The discharge will be classified as “new” only when effluent is being discharged from the two new generators.  Otherwise, the discharge from the facility is subject to less stringent thermal discharge limitations.

The State Board regards these modifications to the permit as minor in nature.  40 Code of Federal Regulations 122.63.