## IntroTab
State Water Resources Control Board
Cost-Benefit Analysis Model: Water Loss Performance Standards
Version 4.0: April 14, 2021
The primary objective of this model is to calculate water loss performance standards for urban retail water suppliers in California pursuant to Water Code 10608.34. This spreadsheet was developed to conduct a cost-benefit analysis for any additional actions anticipated to be taken by urban retail water suppliers to reduce water loss from leakage to an economically feasible levels. The model uses data from water loss audit reports submitted annually in California from 2016 to 2019, industry and literature based estimates for costs and benefits associated with water loss control actions that are anticipated to be accrued. The model calculates water loss performance standards based on economically feasible water loss reductions by 2028 from active leak detection and repair only due to availability of data.
Spreadsheet tabs
Inputs: All inputs to the model are summarized here. Any changes to inputs can be made in this tab. Inputs are color-coded to show which cells are from water loss audits, user-inputs, calculated,or determined by the State Water Board.
Calculations: This tab uses the inputs from the input tab to calculate the system-specific background, reported and unreported leakage, an economic intervention frequency for leakage surveying, and the associated cost-benefit analysis.
Output: This tab summarizes the economic level of leakage for each year beginning 2022, with a view to determine the economically feasible level of leakage for 2028, and the Benefit-Cost ratio across the time horizon, including the compliance period.
Equations: This tab provides all equations with unit conversions in detail. An additional detailed guidance document with a change sheet describes the working of the model
CollectedData_References: This tab summarizes all data that the Water Board used to develop the model and the respective references.
For questions, please contact:
Bethany Robinson at bethany.robinson@waterboards.ca.gov
Max Gomberg at max.gomberg@waterboards.ca.gov
Changes to this Model Version
1. Text clarification suggestions by peer reviewers were added.
2. The CPI was changed from the "commodities" to the "all prices" CPI, which affected the average avoided cost of water and the average annual rise in price of water.
3. An inverted inflation calculation was corrected, which affected the average avoided cost of water.
4. Additional information from Lambert (2009) was added the the References tab on how the minimum reported and unreported leakage equations were developed.
5. Several inputs were not linked to the Calculations tab. This has been fixed.
6. Several stated equations in the Equations tab have been fixed.

## Inputs
Water loss performance standard - Input
Superscripted numbers denote a numbered reference in the "CollectedData_References" tab.
Color code for cells
From water loss audit reports submitted per Water Code §10608.34
Default inputs or supplier-specific inputs if known
Water Board determined input values
1. From water loss audit reports submitted by urban retail water suppliers as per Water Code 10608.34 to the California Department of Water Resources1
Average baseline real loss | 10171 | acre-feet per year | Average of current annual real loss reported in annual water loss audits (2017 to 2020)
Average length of mains | 3347 | miles | Average of length of mains reported in annual water loss audits (2017 to 2020)
Average number of service connections | 284399 | # | Average of number of active and inactive service connections reported in annual water loss audits (2017 to 2020)
Average variable production cost of water | 1282 | $ per acre-feet | Average of variable production cost reported in annual water loss audits (2017 to 2020)
Average operating pressure | 90 | psi | Average of average operating pressure reported in annual water loss audits (2017 to 2020)
2. Default values determined by Water Board that can be replaced by supplier-specific inputs provided by urban retail water supplier with supporting supplier records
This model determines the background leakage (undetectable by active leak detection and repair), reported leakage (visible) and unreported leakage (hidden but detectable by active leak detection equipment) for the distribution system. These components are calculated based on the length of distribution mains and number of connections owned by the supplier and the average operational pressure. The model calculates the unreported leakage component, which is can be reduced by active leak detection and repair by surveying the distribution system using specialized equipment. It uses established equations and estimates for typical flow rates and number of leaks for each type of leakage (background, reported and unreported) as applicable from the AWWA M36 manual (2016)2, the Water Research Foundation 4372a Report (2015)3, and a publication by AWWA's Water Loss Control Committee4 on the IWA International Methodology for determining these leakage components. The following default inputs (green cells) are based on these references, and can be adjusted by the supplier if the supplier has supplier-specific data based on field measurements and analysis.
Note: For a summary of the data collected by the State Water Board, see 'CollectedData_References' tab
2. (a) Leakage profile of urban retail water supplier
Rate of rise of leakage, if known |  | gallons per connection per day per year | The cell here is blank for possible supplier input. A default rise of 4 gallons per connection per day per year, adapted from the EU Reference document: Good Practices on Leakage Management (Main Report)5 is used. To check applicability to North American water systems, references of a California and a Tenessee system are used from the Water Research foundation Report 4372a, 20153, which had rates of rise of leakage of 3 and 3.9 gallons per connection per day per year. As per the EU Report, this value is very low as compared to water systems in the U.K., and is selected as a representative rate for California systems, based on field experience of technical experts. The low rate of rise of leakage means that the model relies more on the backlog of leakage (represented by the real loss reported by suppliers) than the default value for rate of rise in leakage.
Background leakage: If supplier has information, enter as volume below, or enter infrastructure condition factor below
Infrastructure Condition Factor (ICF) | 1 |  | For background leakage calculation; Adapted from Water Research Foundation 4372a Leakage Component Analysis Model3. ICF should be increased based on the age of the distribution network.
Or
Annual background leakage, if known |  | acre-feet per year | The cell here is blank for possible supplier input. By default, the 'Calculations' tab calculates the background leakage volume, using Equation (7-5), AWWA M36 Manual, 20162
Reported leakage: If supplier has information, enter as volume below, or enter average flow rates and number of leaks per mile below
Reported leaks on mains
Average duration between reporting of and repair of reported leaks | 3 | days | For reported leakage calculation From AWWA M36 Manual, Fourth Edition (2016)2 (Table 3-22), AWWA Water Loss Control Committee Report: Applying worldwide BMPs in water loss control, 20036 (Table 4); Lambert, 19994 (Table 3); Lambert, 2009 (Table 1).
Number of reported leaks per year | 0.2 | leaks per mile per year
Average flow rate for reported leaks | 50 | gallons per minute per leak
Reported leaks on service connections (main to curb stop)
Average duration between reporting of and repair of reported leaks | 8 | days
Number of reported leaks per year | 2.25 | leaks per 1000 connections per year
Average flow rate for reported leaks | 7 | gallons per minute per leak
Or
Annual reported leakage, if known |  | acre-feet per year | The cell here is blank for possible supplier input. By default, the 'Calculations' tab calculates the reported leakage volume, using the values in cells B24 - B26 and B28 - B30 (Inputs tab)
Unreported leakage: If supplier has information, enter as volume below (Background leakage + Reported leakage + Unreported leakage) must equal Three-year average real loss
Annual unreported leakage, if known |  | acre-feet per year | The cell here is blank for possible supplier input. By default, the 'Calculations' tab calculates the unreported leakage volume based on the average baseline real loss, annual background and annual reported leakage.
Or
Number of unreported leaks per year on mains | 0.01 | leaks per 100 miles of mains | Adapted from AWWA M36 Manual, Fourth Edition (2016)2 (Table 3-22); Lambert, 2009 (Table 1).
Number of unreported leaks per year on service connections (main to curb stop) | 0.75 | leaks per 1000 service connections
2. (b) Associated unit costs and marginal avoided cost of water
Average leak detection survey frequency |  | miles per month | Average survey rate based on communications with vendors, and water suppliers. The cell here is blank for possible supplier input. By default, the 'Calculations' tab calculates the average survey frequency for the following system sizes based on the following default survey frequencies: 6000 miles and above - 130 miles per month; 4000 miles and above - 114 miles per month; 1000 miles and above: Once in three years; 500 miles and above: Once in 2.5 years; Below 500 miles: Once every 2 years. Refer to the 'CollectedData_References' for data establishing these survey rates. These survey rates can include all types of proactive leak detection including visual surveying.
Unit average cost of leak detection surveying per mile (including upfront and maintenance costs) | 595 | $ per mile | For calculation of intervention costs for reducing unreported leakage, includes surveying and pinpointing (see rows 46 and 47 for repair costs)
Efficiency of leak detection equipment | 70% | in percent | Represents the average number of actual leaks found on excavation as a percent of the total detected leaks including false positives expected to be pinpointed by leak detection equipment over the time horizon. As per vendor and water supplier knowledge based on field implementation, this efficiency increases with higher training and experience. This parameter adds the cost of additional excavation associated with locating leaks pinpointed by false positives, without the benefits of water loss reduction, to the overall costs of leak detection and repair.
Average unit leak repair costs for mains | 5946 | $ per leak | Based on data from Irvine Ranch Water District, Kunkel Water Efficiency Consulting and PGE Report ET13PGE1451: Water System Leak Identification and Control Field Evaluation7
Average unit cost of leak repair costs for laterals and service lines (mains to curb stop) | 2330 | $ per leak | Based on estimates from Kunkel Water Efficiency Consulting and Water System Optimization, Inc. All suppliers reported that the meter was located at the curbstop or property line in the water loss audits.
Marginal avoided cost of water | 1275 | $ per acre-feet | Based on the average cost of alternative suplies for stormwater capture, brackish desalination, nonpotable reuse, indirect potable reuse, based on a Pacific Institute study, suported by an NRDC issue brief (2016)8,9 and imported water costs as per historical rates from the Metropolitan Water District
Note: For a summary of the data collected by the Water BoardSee 'CollectedData_References' tab
3. Input values on real rise in value of water and costs associated with water loss reduction (determined by the Water Board)
The model conducts a cost-benefit analysis to evaluate cost-effectiveness between reducing real loss and maintaining current real loss. The time horizon for the cost-benefit analysis is 30 years, which includes the lifecycles of water loss control actions and covers costs and benefits occuring beyond the compliance timeline of the regulation. The benefits associated with real loss reduction depend on the rise of price water, discount rate, value of avoided cost of water (previous section) and the volume of real loss reduced. The rise in price of water and discount rate are determined by State Water Board staff and are fixed for the model. Additional details are presented in the 'CollectedData_References' tab.
Real discount rate | 3.5% | percent | State Water Board staff proposal based on stakeholder input
Average annual rise in price of water | 4.6% | in percent | Based on Historical data from Metropolitan Water District: 2008 - 2018 - Converted to real prices in 2020$
Effective timeline for lifecycle benefit-cost analysis | 30 | years | Anticipated timeline as lifecycle for accruing costs and benefits associated with real loss reduction. This timeline covers the lifecycle of active leak detection and repair implementation, and associated leakage reduction or maintenance and continued maintenance of leakage per the standard.

## Calculations
Water loss performance standard - Leakage Reduction and Benefit-Cost Analysis
Notes
Calculations to determine unreported leakage volume are below.
The benefit-cost analysis and standard calculation begin at row 66 of this tab.
The 'Output' tab provides the Cost-Benefit ratios and calculated standards
Detailed equations are available in the 'Equations' tab.
Parameter | Value | Unit of Measurement | Explanation/Formula
System leakage characteristics
Three-year average real loss for supplier | 10171 | acre-feet per year | Three-year average, From water loss audits submitted annually (2017 to 2019)
Total length of mains | 3347 | miles | Three-year average, From water loss audits submitted annually (2017 to 2019)
Rate of rise of leakage | 1274.2712 | acre-feet per year | Based on Table 6 of EU Reference document: Good Practices on Leakage Management (Main Report)5, and Water Research foundation Report 4372a, (2015)3, if supplier does not have system-specific estimate.
Average operating pressure | 90 | psi | Three-year average, From water loss audits submitted annually (2017 to 2019)
Number of service connections | 284399 | # | Three-year average, From water loss audits submitted annually (2017 to 2019)
Calculation of leakage components - Background, Reported and Unreported leakage
This section calculates the different components associated with the unavoidable annual real loss: Background, reported and unreported leakage using the AWWA M36 Manual, 2014. The background (undetectable leakage) is calculated first using an established formula. The Reported leakage is calculated based on typical flow rates and break rates. The unreported leakage is calculated as the leakage that remains after deducting reported and background leakage from the total leakage. The calculation is based on typical flow rates and number of leaks per mile associated with these different types of leakages from the AWWA M36 manual.
Infrastructure Condition Factor (ICF) | 1 |  | Default = 1, Adapted from Water Research Foundation 4372a Leakage Component Analysis Model3
Total background leakage | 4808.5666 | acre-feet per year | Equation (7-5), AWWA M36 Manual, 20162 or supplier input
Estimated number of reported leaks | 0.2 | leaks per mile per year | From AWWA M36 Manual, Fourth Edition (2016)2 (Table 3-22); 0.2 leaks per mile per year at 50 gallons per minute over 3 days' duration
Average time between reporting and repair of reported leaks | 3 | days
Estimated average flow rate for reported leaks | 64.2857 | gallons per minute per leak
Reported leakage from mains | 570.5121 | acre-feet per year
Average time between reporting of and repair of reported leaks | 8 | days | From AWWA M36 Manual, Fourth Edition (2016)2 (Table 3-22); 2.3 leaks per 1000 connections per year at 9.5 gallons per minute over 8 days' duration
Number of reported leaks per year | 2.25 | leaks per 1000 connections per year
Estimate average flow rate for reported leaks | 7 | gallons per minute per leak
Reported leakage from service connections (main to curb stop) | 203.6041 | acre-feet per year
Annual reported leakage | 774.1162 | acre-feet per year | Average flowrate for reported leakage x Number of reported leaks per mile x Total length of mains
Annual unreported leakage | 4588.3172 | acre-feet per year | Total leakage - (background leakage + reported leakage)
Annual unreported leakage | 1495107734.2281 | gallons per year
Calculation of anticipated number of unreported leaks for the system
Unreported leakage fraction for the system | 0.45112 | fraction of total annual leakage | Unreported leakage / (Unreported+Reported+Background) leakages
Estimated average flow rate for unreported leaks | 32.1429 | gallons per minute per leak | Adapted from AWWA M36 Manual, Fourth Edition (2016)2 (Table 3-22); 0.01 leaks per mile per year at 25 gallons per minute
Number of unreported leaks on mains | 0.01 | leaks per mile of main
Number of total unreported leaks on mains | 33.47
Estimated average flow rate for unreported leaks | 9 | gallons per minute per leak | Adapted from AWWA M36 Manual, Fourth Edition (2016)2 (Table 3-22); 0.75 leaks per 1000 service connections per year at 9.5 gallons per minute
Number of unreported leaks on service connections (main to curb stop) | 0.75 | leaks per 1000 service connections
Number of total unreported leaks on service connections | 213.2993
Value of water for supplier
Nominal discount rate | 3.5% | percent | State Water Board staff proposal based on stakeholder input
Variable production cost of water | 1282 | $ per acre-feet | Three-year average, From water loss audits submitted annually (2017 to 2020)
Avoided cost of alternative supplies | 1275 | $/acre-feet | User-reported or default value, used to value the volume of real loss reduced
Average annual rise in price of water | 4.6% | percent | Historical data from Metropolitan Water District: 2008 - 2020
Assumed effective timeline | 30 | years | Expected timeline for costs and benefits associated with real loss reduction
Active leak detection and repair costs
Based on data collected by State Water Board staff or data provided by supplier,supported by supplier records. See 'CollectedData_References' tab for a summary of the data collected by the Water Board
Leak surveying and pinpointing costs per mile | 595 | $ per mile of mains surveyed | Based on data from vendors and water suppliers
Efficiency of leak detection equipment | 70% | in percent | Represents the average percentage of actual leaks found on excavation v/s the total detected leaks, including false positives expected to be pinpointed by leak detection equipment over the time horizon. As per vendor and water supplier knowledge based on field implementation, this efficiency increases with higher training and experience. This parameter adds the cost of additional excavation associated with locating leaks pinpointed by false positives, without the benefits of water loss reduction, to the overall costs of leak detection and repair.
Repair costs for leaks on mains | 5946 | $ per leak repaired | Based on data from Irvine Ranch Water District and PGE Report ET13PGE1451: Water System Leak Identification and Control Field Evaluation7
Repair costs for leaks on laterals | 2330 | $ per leak repaired
Estimate time taken to survey full distribution system | 36 | months | This represents an average frequency for leak detection surveying based on the miles of pipe in a water distribution system. This average frequency is derived from vendor and water supplier estimates, and used as a basis to calculate the economically recoverable leakage. Complying with this survey frequency is not a regulatory requirement.
Tracking leakage reduction across time horizon
This method is used such that the model can consider cases of partial distribution system surveys. This is a simplifying method for the calculations, and calculates benefit and cost after each month.
Assumptions: (1) The system is divided into parts based on how many parts can be reasonably surveyed in each time step. (2) The leakage is spread out uniformly throughout the system.
Time step | 0.083333 | year | Time step of one month to allow for incremental and partial surveys
Average number of miles surveyed in each month | 92.9722 | miles | Total length of mains / Economic Intervention frequency
Months taken to survey whole system | 36 | # | Total length of mains / Average number of miles surveyed each month
Unreported leakage per month | 127.4533 | acre-feet per year | Average detectable leakage for supplier / Number of parts of system
Annual average rise in leakage per month | 35.3964 | acre-feet per year per part per year | Rate of rise of leakage / Number of parts of system
Cost for leak detection per month | 55318.4722 | $ | Cost of leak detection per mile x Total length of mains / Number of parts of system
Note: Repair costs per mile included in cost-benefit analysis, based on leakage corresponding to each survey cycle and leaks/mile
Calculation of Leakage reduction and Benefit-Cost Analysis across 30 years
| Water lost during implementation of additional intervention (from residual backlog and natural rise of leakage) |  |  |  |  | Baseline - Without additional intervention |  | Water savings and cost for additional intervention |  | Calculations for leaks repaired during active leak detection |  |  |  |  | Analysis of additional benefits or costs due to additional intervention for leakage reduction
(1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13) | (14) | (15) | (16) | (17) | (18) | (19) | (20) | (21)
Month of implementation since 2022 (Based on a 30 year time horizon) | Water loss due to backlog of leakage from unsurveyed parts in each month | Water loss due to natural rise in leakage in never surveyed parts in each month | Water loss due to natural rise in leakage in previously surveyed parts in each month | Total water loss occuring per month with intervention | Cumulative water loss occurring with intervention | Water loss occuring without intervention in each month | Cumulative water loss occuring without intervention | Water saved due to water loss control in each month with intervention | Cost associated with leak detection in each month with intervention | Initial leakage level for part surveyed each month (to calculate number of leaks) with intervention | Leaks found per part of the system with intervention | Incremental cost associated with leak repair in each month with intervention | Total cost of leak detection and repair in each month with intervention | Present value of total cost of leak detection and repair for each month with intervention | Marginal cost of water including rise in cost of water and avoided cost of alternative supplies in each month (begins in year 2022) | Value of water loss reduced in each month with intervention | Present value of water loss reduced for each month with intervention | Net benefit for each month with intervention | Present value of net benefit (Benefit - Cost) corresponding to each month with intervention (red indicates negative) | Year | Years of implementation (for reference)
# | (acre-feet) | (acre-feet) | (acre-feet) | (acre-feet) | (acre-feet) | (acre-feet) | (acre-feet) | (acre-feet) | ($) | (acre-feet) | # | ($) | ($) |  | ($ per acre-feet) | ($) |  | ($) | ($) in 2020
1 | 382.3598 | 4.4246 | 0 | 386.7843 | 386.7843 | 386.7843 | 386.7843 | 0 | 55318.4722 | 130.403 | 7.0133 | 28258.2411 | 83576.7134 | 77934.351 | 1399.944 | -7.9578e-11 | -7.4205e-11 | -83576.7134 | -77934.351 | 2022 | 0.083333
2 | 371.7387 | 12.9049 | 0.1229 | 384.7665 | 771.5508 | 386.7843 | 773.5686 | 2.0178 | 55318.4722 | 133.3527 | 7.172 | 28897.4397 | 84215.912 | 78302.0156 | 1405.3105 | 2835.6461 | 2636.5184 | -81380.2659 | -75665.4972 | 2022 | 0.16667
3 | 361.1176 | 20.8937 | 0.49162 | 382.5029 | 1154.0537 | 386.7843 | 1160.3529 | 4.2814 | 55318.4722 | 136.3024 | 7.3306 | 29536.6383 | 84855.1105 | 78666.8827 | 1410.6769 | 6039.7054 | 5599.2479 | -78815.4051 | -73067.6348 | 2022 | 0.25
4 | 350.4964 | 28.3909 | 1.1061 | 379.9935 | 1534.0472 | 386.7843 | 1547.1373 | 6.7908 | 55318.4722 | 139.2521 | 7.4893 | 30175.8369 | 85494.3091 | 79028.9653 | 1416.0434 | 9616.1354 | 8888.9335 | -75878.1737 | -70140.0318 | 2022 | 0.33333
5 | 339.8753 | 35.3964 | 1.9665 | 377.2382 | 1911.2854 | 386.7843 | 1933.9216 | 9.5461 | 55318.4722 | 142.2018 | 7.6479 | 30815.0355 | 86133.5077 | 79388.2766 | 1421.4098 | 13568.8934 | 12506.2951 | -72564.6143 | -66881.9815 | 2022 | 0.41667
6 | 329.2542 | 41.9103 | 3.0726 | 374.2372 | 2285.5226 | 386.7843 | 2320.7059 | 12.5471 | 55318.4722 | 145.1515 | 7.8065 | 31454.2341 | 86772.7063 | 79744.8296 | 1426.7763 | 17901.9368 | 16452.0269 | -68870.7695 | -63292.8027 | 2022 | 0.5
7 | 318.6331 | 47.9327 | 4.4246 | 370.9903 | 2656.513 | 386.7843 | 2707.4902 | 15.794 | 55318.4722 | 148.1012 | 7.9652 | 32093.4327 | 87411.9049 | 80098.6373 | 1432.1427 | 22619.2228 | 20726.7983 | -64792.6821 | -59371.839 | 2022 | 0.58333
8 | 308.012 | 53.4633 | 6.0223 | 367.4977 | 3024.0106 | 386.7843 | 3094.2745 | 19.2866 | 55318.4722 | 151.0509 | 8.1238 | 32732.6313 | 88051.1035 | 80449.7127 | 1437.5092 | 27724.709 | 25331.2541 | -60326.3945 | -55118.4586 | 2022 | 0.66667
9 | 297.3909 | 58.5024 | 7.8659 | 363.7592 | 3387.7699 | 386.7843 | 3481.0588 | 23.0251 | 55318.4722 | 154.0006 | 8.2825 | 33371.8298 | 88690.3021 | 80798.0687 | 1442.8756 | 33222.3526 | 30266.014 | -55467.9495 | -50532.0547 | 2022 | 0.75
10 | 286.7698 | 63.0499 | 9.9552 | 359.7749 | 3747.5448 | 386.7843 | 3867.8432 | 27.0094 | 55318.4722 | 156.9503 | 8.4411 | 34011.0284 | 89329.5006 | 81143.7181 | 1448.2421 | 39116.111 | 35531.6738 | -50213.3897 | -45612.0443 | 2022 | 0.83333
11 | 276.1487 | 67.1057 | 12.2904 | 355.5449 | 4103.0897 | 386.7843 | 4254.6275 | 31.2395 | 55318.4722 | 159.9 | 8.5998 | 34650.227 | 89968.6992 | 81486.6737 | 1453.6085 | 45409.9415 | 41128.805 | -44558.7577 | -40357.8687 | 2022 | 0.91667
12 | 265.5276 | 70.6699 | 14.8714 | 351.069 | 4454.1586 | 386.7843 | 4641.4118 | 35.7153 | 55318.4722 | 162.8497 | 8.7584 | 35289.4256 | 90607.8978 | 81826.9483 | 1458.975 | 52107.8016 | 47057.9551 | -38500.0963 | -34768.9932 | 2022 | 1
13 | 254.9065 | 73.7425 | 17.6982 | 346.3473 | 4800.5059 | 386.7843 | 5028.1961 | 40.4371 | 55318.4722 | 165.7994 | 8.917 | 35928.6242 | 91247.0964 | 82164.5546 | 1464.3414 | 59213.6485 | 53319.6479 | -32033.4479 | -28844.9067 | 2023 | 1.0833
14 | 244.2854 | 76.3235 | 20.7708 | 341.3798 | 5141.8856 | 386.7843 | 5414.9804 | 45.4046 | 55318.4722 | 168.7491 | 9.0757 | 36567.8228 | 91886.295 | 82499.5051 | 1469.7079 | 66731.4396 | 59914.3839 | -25154.8553 | -22585.1213 | 2023 | 1.1667
15 | 233.6643 | 78.4129 | 24.0892 | 336.1664 | 5478.0521 | 386.7843 | 5801.7647 | 50.6179 | 55318.4722 | 171.6988 | 9.2343 | 37207.0214 | 92525.4936 | 82831.8126 | 1475.0743 | 74665.1324 | 66842.64 | -17860.3612 | -15989.1726 | 2023 | 1.25
16 | 223.0432 | 80.0107 | 27.6535 | 330.7073 | 5808.7594 | 386.7843 | 6188.5491 | 56.077 | 55318.4722 | 174.6485 | 9.393 | 37846.2199 | 93164.6922 | 83161.4895 | 1480.4408 | 83018.6841 | 74104.8702 | -10146.0081 | -9056.6193 | 2023 | 1.3333
17 | 212.4221 | 81.1168 | 31.4635 | 325.0024 | 6133.7618 | 386.7843 | 6575.3334 | 61.7819 | 55318.4722 | 177.5982 | 9.5516 | 38485.4185 | 93803.8908 | 83488.5483 | 1485.8072 | 91796.0521 | 81701.5058 | -2007.8387 | -1787.0425 | 2023 | 1.4167
18 | 201.801 | 81.7313 | 35.5193 | 319.0516 | 6452.8134 | 386.7843 | 6962.1177 | 67.7327 | 55318.4722 | 180.5479 | 9.7102 | 39124.6171 | 94443.0893 | 83813.0015 | 1491.1737 | 101001.1937 | 89632.9552 | 6558.1044 | 5819.9538 | 2023 | 1.5
19 | 191.1799 | 81.8542 | 39.821 | 312.8551 | 6765.6685 | 386.7843 | 7348.902 | 73.9292 | 55318.4722 | 183.4976 | 9.8689 | 39763.8157 | 95082.2879 | 84134.8614 | 1496.5401 | 110638.0664 | 97899.6045 | 15555.7785 | 13764.7431 | 2023 | 1.5833
20 | 180.5588 | 81.4855 | 44.3684 | 306.4127 | 7072.0812 | 386.7843 | 7735.6863 | 80.3716 | 55318.4722 | 186.4473 | 10.0275 | 40403.0143 | 95721.4865 | 84454.1405 | 1501.9066 | 120710.6274 | 106501.8175 | 24989.1409 | 22047.677 | 2023 | 1.6667
21 | 169.9377 | 80.6252 | 49.1617 | 299.7246 | 7371.8058 | 386.7843 | 8122.4706 | 87.0598 | 55318.4722 | 189.397 | 10.1862 | 41042.2129 | 96360.6851 | 84770.8509 | 1507.273 | 131222.8342 | 115439.9359 | 34862.1491 | 30669.085 | 2023 | 1.75
22 | 159.3166 | 79.2732 | 54.2008 | 292.7906 | 7664.5963 | 386.7843 | 8509.2549 | 93.9937 | 55318.4722 | 192.3467 | 10.3448 | 41681.4115 | 96999.8837 | 85085.0049 | 1512.6395 | 142178.6441 | 124714.2797 | 45178.7604 | 39629.2749 | 2023 | 1.8333
23 | 148.6955 | 77.4297 | 59.4857 | 285.6108 | 7950.2071 | 386.7843 | 8896.0393 | 101.1735 | 55318.4722 | 195.2964 | 10.5034 | 42320.61 | 97639.0823 | 85396.6147 | 1518.0059 | 153582.0144 | 134325.1474 | 55942.9322 | 48928.5327 | 2023 | 1.9167
24 | 138.0744 | 75.0945 | 65.0163 | 278.1852 | 8228.3923 | 386.7843 | 9282.8236 | 108.5991 | 55318.4722 | 198.2461 | 10.6621 | 42959.8086 | 98278.2809 | 85705.6925 | 1523.3724 | 165436.9026 | 144272.8157 | 67158.6217 | 58567.1232 | 2023 | 2
25 | 127.4533 | 72.2677 | 70.7928 | 270.5138 | 8498.9061 | 386.7843 | 9669.6079 | 116.2705 | 55318.4722 | 201.1958 | 10.8207 | 43599.0072 | 98917.4794 | 86012.2504 | 1528.7388 | 177747.2659 | 154557.5405 | 78829.7865 | 68545.2901 | 2024 | 2.0833
26 | 116.8321 | 68.9493 | 76.8152 | 262.5966 | 8761.5027 | 386.7843 | 10056.3922 | 124.1877 | 55318.4722 | 204.1455 | 10.9794 | 44238.2058 | 99556.678 | 86316.3003 | 1534.1053 | 190517.0617 | 165179.5564 | 90960.3837 | 78863.2561 | 2024 | 2.1667
27 | 106.211 | 65.1392 | 83.0833 | 254.4336 | 9015.9363 | 386.7843 | 10443.1765 | 132.3508 | 55318.4722 | 207.0952 | 11.138 | 44877.4044 | 100195.8766 | 86617.8543 | 1539.4718 | 203750.2475 | 176139.0772 | 103554.3709 | 89521.2229 | 2024 | 2.25
28 | 95.5899 | 60.8376 | 89.5972 | 246.0247 | 9261.961 | 386.7843 | 10829.9608 | 140.7596 | 55318.4722 | 210.0449 | 11.2967 | 45516.603 | 100835.0752 | 86916.9243 | 1544.8382 | 217450.7805 | 187436.2963 | 116615.7053 | 100519.3719 | 2024 | 2.3333
29 | 84.9688 | 56.0443 | 96.3569 | 237.3701 | 9499.3311 | 386.7843 | 11216.7452 | 149.4142 | 55318.4722 | 212.9946 | 11.4553 | 46155.8016 | 101474.2738 | 87213.5223 | 1550.2047 | 231622.618 | 199071.3863 | 130148.3442 | 111857.864 | 2024 | 2.4167
30 | 74.3477 | 50.7595 | 103.3625 | 228.4697 | 9727.8007 | 386.7843 | 11603.5295 | 158.3147 | 55318.4722 | 215.9443 | 11.6139 | 46795.0002 | 102113.4724 | 87507.66 | 1555.5711 | 246269.7176 | 211044.5 | 144156.2452 | 123536.8399 | 2024 | 2.5
31 | 63.7266 | 44.983 | 110.6138 | 219.3234 | 9947.1241 | 386.7843 | 11990.3138 | 167.4609 | 55318.4722 | 218.894 | 11.7726 | 47434.1987 | 102752.671 | 87799.3493 | 1560.9376 | 261396.0364 | 223355.7697 | 158643.3655 | 135556.4204 | 2024 | 2.5833
32 | 53.1055 | 38.7148 | 118.111 | 209.9313 | 10157.0555 | 386.7843 | 12377.0981 | 176.853 | 55318.4722 | 221.8437 | 11.9312 | 48073.3973 | 103391.8695 | 88088.602 | 1566.304 | 277005.532 | 236005.3083 | 173613.6624 | 147916.7063 | 2024 | 2.6667
33 | 42.4844 | 31.9551 | 125.8539 | 200.2935 | 10357.3489 | 386.7843 | 12763.8824 | 186.4909 | 55318.4722 | 224.7934 | 12.0899 | 48712.5959 | 104031.0681 | 88375.4296 | 1571.6705 | 293102.1615 | 248993.2086 | 189071.0934 | 160617.779 | 2024 | 2.75
34 | 31.8633 | 24.7038 | 133.8427 | 190.4098 | 10547.7587 | 386.7843 | 13150.6667 | 196.3745 | 55318.4722 | 227.7431 | 12.2485 | 49351.7945 | 104670.2667 | 88659.844 | 1577.0369 | 309689.8825 | 262319.5443 | 205019.6158 | 173659.7003 | 2024 | 2.8333
35 | 21.2422 | 16.9608 | 142.0773 | 180.2803 | 10728.039 | 386.7843 | 13537.4511 | 206.504 | 55318.4722 | 230.6928 | 12.4071 | 49990.9931 | 105309.4653 | 88941.8566 | 1582.4034 | 326772.6522 | 275984.3696 | 221463.1869 | 187042.5129 | 2024 | 2.9167
36 | 10.6211 | 8.7262 | 150.5577 | 169.905 | 10897.944 | 386.7843 | 13924.2354 | 216.8793 | 55318.4722 | 233.6425 | 12.5658 | 50630.1917 | 105948.6639 | 89221.4792 | 1587.7698 | 344354.4281 | 289987.7196 | 238405.7642 | 200766.2404 | 2024 | 3
37 | 0 | 0 | 159.2839 | 159.2839 | 11057.2279 | 386.7843 | 14311.0197 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 65771.1012 | 1593.1363 | 362439.1674 | 304329.6105 | 284109.546 | 238558.5093 | 2025 | 3.0833
38 | 0 | 0 | 159.2839 | 159.2839 | 11216.5118 | 386.7843 | 14697.804 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 65579.8267 | 1598.5027 | 363660.0374 | 304466.7117 | 285330.4161 | 238886.885 | 2025 | 3.1667
39 | 0 | 0 | 159.2839 | 159.2839 | 11375.7957 | 386.7843 | 15084.5883 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 65389.1085 | 1603.8692 | 364880.9075 | 304600.4415 | 286551.2862 | 239211.333 | 2025 | 3.25
40 | 0 | 0 | 159.2839 | 159.2839 | 11535.0796 | 386.7843 | 15471.3726 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 65198.9449 | 1609.2356 | 366101.7776 | 304730.8184 | 287772.1563 | 239531.8736 | 2025 | 3.3333
41 | 0 | 0 | 159.2839 | 159.2839 | 11694.3635 | 386.7843 | 15858.157 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 65009.3343 | 1614.6021 | 367322.6477 | 304857.8609 | 288993.0263 | 239848.5266 | 2025 | 3.4167
42 | 0 | 0 | 159.2839 | 159.2839 | 11853.6474 | 386.7843 | 16244.9413 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 64820.2752 | 1619.9685 | 368543.5177 | 304981.5872 | 290213.8964 | 240161.312 | 2025 | 3.5
43 | 0 | 0 | 159.2839 | 159.2839 | 12012.9313 | 386.7843 | 16631.7256 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 64631.7659 | 1625.335 | 369764.3878 | 305102.0155 | 291434.7665 | 240470.2496 | 2025 | 3.5833
44 | 0 | 0 | 159.2839 | 159.2839 | 12172.2152 | 386.7843 | 17018.5099 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 64443.8048 | 1630.7014 | 370985.2579 | 305219.1639 | 292655.6365 | 240775.3591 | 2025 | 3.6667
45 | 0 | 0 | 159.2839 | 159.2839 | 12331.4991 | 386.7843 | 17405.2942 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 64256.3903 | 1636.0679 | 372206.1279 | 305333.0505 | 293876.5066 | 241076.6602 | 2025 | 3.75
46 | 0 | 0 | 159.2839 | 159.2839 | 12490.783 | 386.7843 | 17792.0785 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 64069.5209 | 1641.4343 | 373426.998 | 305443.6934 | 295097.3767 | 241374.1725 | 2025 | 3.8333
47 | 0 | 0 | 159.2839 | 159.2839 | 12650.0669 | 386.7843 | 18178.8628 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 63883.1949 | 1646.8008 | 374647.8681 | 305551.1103 | 296318.2468 | 241667.9154 | 2025 | 3.9167
48 | 0 | 0 | 159.2839 | 159.2839 | 12809.3508 | 386.7843 | 18565.6472 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 63697.4108 | 1652.1672 | 375868.7382 | 305655.3191 | 297539.1168 | 241957.9084 | 2025 | 4
49 | 0 | 0 | 159.2839 | 159.2839 | 12968.6347 | 386.7843 | 18952.4315 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 63512.1669 | 1657.5337 | 377089.6082 | 305756.3377 | 298759.9869 | 242244.1707 | 2026 | 4.0833
50 | 0 | 0 | 159.2839 | 159.2839 | 13127.9186 | 386.7843 | 19339.2158 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 63327.4618 | 1662.9001 | 378310.4783 | 305854.1835 | 299980.857 | 242526.7217 | 2026 | 4.1667
51 | 0 | 0 | 159.2839 | 159.2839 | 13287.2025 | 386.7843 | 19726.0001 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 63143.2939 | 1668.2666 | 379531.3484 | 305948.8744 | 301201.727 | 242805.5805 | 2026 | 4.25
52 | 0 | 0 | 159.2839 | 159.2839 | 13446.4864 | 386.7843 | 20112.7844 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 62959.6616 | 1673.6331 | 380752.2184 | 306040.4277 | 302422.5971 | 243080.7661 | 2026 | 4.3333
53 | 0 | 0 | 159.2839 | 159.2839 | 13605.7703 | 386.7843 | 20499.5687 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 62776.5633 | 1678.9995 | 381973.0885 | 306128.8609 | 303643.4672 | 243352.2976 | 2026 | 4.4167
54 | 0 | 0 | 159.2839 | 159.2839 | 13765.0542 | 386.7843 | 20886.3531 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 62593.9974 | 1684.366 | 383193.9586 | 306214.1914 | 304864.3373 | 243620.1939 | 2026 | 4.5
55 | 0 | 0 | 159.2839 | 159.2839 | 13924.3381 | 386.7843 | 21273.1374 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 62411.9625 | 1689.7324 | 384414.8287 | 306296.4365 | 306085.2073 | 243884.4739 | 2026 | 4.5833
56 | 0 | 0 | 159.2839 | 159.2839 | 14083.622 | 386.7843 | 21659.9217 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 62230.457 | 1695.0989 | 385635.6987 | 306375.6134 | 307306.0774 | 244145.1563 | 2026 | 4.6667
57 | 0 | 0 | 159.2839 | 159.2839 | 14242.9059 | 386.7843 | 22046.706 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 62049.4794 | 1700.4653 | 386856.5688 | 306451.7392 | 308526.9475 | 244402.2598 | 2026 | 4.75
58 | 0 | 0 | 159.2839 | 159.2839 | 14402.1898 | 386.7843 | 22433.4903 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 61869.0281 | 1705.8318 | 388077.4389 | 306524.8311 | 309747.8175 | 244655.8031 | 2026 | 4.8333
59 | 0 | 0 | 159.2839 | 159.2839 | 14561.4737 | 386.7843 | 22820.2746 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 61689.1015 | 1711.1982 | 389298.309 | 306594.9061 | 310968.6876 | 244905.8046 | 2026 | 4.9167
60 | 0 | 0 | 159.2839 | 159.2839 | 14720.7576 | 386.7843 | 23207.059 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 61509.6982 | 1716.5647 | 390519.179 | 306661.981 | 312189.5577 | 245152.2828 | 2026 | 5
61 | 0 | 0 | 159.2839 | 159.2839 | 14880.0415 | 386.7843 | 23593.8433 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 61330.8167 | 1721.9311 | 391740.0491 | 306726.0728 | 313410.4278 | 245395.2561 | 2027 | 5.0833
62 | 0 | 0 | 159.2839 | 159.2839 | 15039.3254 | 386.7843 | 23980.6276 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 61152.4553 | 1727.2976 | 392960.9192 | 306787.1981 | 314631.2978 | 245634.7428 | 2027 | 5.1667
63 | 0 | 0 | 159.2839 | 159.2839 | 15198.6093 | 386.7843 | 24367.4119 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 60974.6127 | 1732.664 | 394181.7892 | 306845.3738 | 315852.1679 | 245870.7611 | 2027 | 5.25
64 | 0 | 0 | 159.2839 | 159.2839 | 15357.8932 | 386.7843 | 24754.1962 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 60797.2873 | 1738.0305 | 395402.6593 | 306900.6165 | 317073.038 | 246103.3292 | 2027 | 5.3333
65 | 0 | 0 | 159.2839 | 159.2839 | 15517.1771 | 386.7843 | 25140.9805 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 60620.4776 | 1743.3969 | 396623.5294 | 306952.9427 | 318293.908 | 246332.4651 | 2027 | 5.4167
66 | 0 | 0 | 159.2839 | 159.2839 | 15676.461 | 386.7843 | 25527.7648 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 60444.182 | 1748.7634 | 397844.3995 | 307002.3689 | 319514.7781 | 246558.1869 | 2027 | 5.5
67 | 0 | 0 | 159.2839 | 159.2839 | 15835.7449 | 386.7843 | 25914.5492 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 60268.3992 | 1754.1298 | 399065.2695 | 307048.9116 | 320735.6482 | 246780.5124 | 2027 | 5.5833
68 | 0 | 0 | 159.2839 | 159.2839 | 15995.0288 | 386.7843 | 26301.3335 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 60093.1276 | 1759.4963 | 400286.1396 | 307092.5871 | 321956.5183 | 246999.4595 | 2027 | 5.6667
69 | 0 | 0 | 159.2839 | 159.2839 | 16154.3127 | 386.7843 | 26688.1178 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 59918.3657 | 1764.8627 | 401507.0097 | 307133.4116 | 323177.3883 | 247215.046 | 2027 | 5.75
70 | 0 | 0 | 159.2839 | 159.2839 | 16313.5966 | 386.7843 | 27074.9021 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 59744.112 | 1770.2292 | 402727.8797 | 307171.4015 | 324398.2584 | 247427.2895 | 2027 | 5.8333
71 | 0 | 0 | 159.2839 | 159.2839 | 16472.8805 | 386.7843 | 27461.6864 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 59570.3651 | 1775.5956 | 403948.7498 | 307206.5728 | 325619.1285 | 247636.2077 | 2027 | 5.9167
72 | 0 | 0 | 159.2839 | 159.2839 | 16632.1644 | 386.7843 | 27848.4707 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 59397.1235 | 1780.9621 | 405169.6199 | 307238.9417 | 326839.9985 | 247841.8181 | 2027 | 6
73 | 0 | 0 | 159.2839 | 159.2839 | 16791.4483 | 386.7843 | 28235.2551 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 59224.3857 | 1786.3285 | 406390.49 | 307268.524 | 328060.8686 | 248044.1383 | 2028 | 6.0833
74 | 0 | 0 | 159.2839 | 159.2839 | 16950.7322 | 386.7843 | 28622.0394 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 59052.1503 | 1791.695 | 407611.36 | 307295.3358 | 329281.7387 | 248243.1855 | 2028 | 6.1667
75 | 0 | 0 | 159.2839 | 159.2839 | 17110.0161 | 386.7843 | 29008.8237 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 58880.4157 | 1797.0614 | 408832.2301 | 307319.393 | 330502.6088 | 248438.9772 | 2028 | 6.25
76 | 0 | 0 | 159.2839 | 159.2839 | 17269.3 | 386.7843 | 29395.608 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 58709.1806 | 1802.4279 | 410053.1002 | 307340.7112 | 331723.4788 | 248631.5306 | 2028 | 6.3333
77 | 0 | 0 | 159.2839 | 159.2839 | 17428.5838 | 386.7843 | 29782.3923 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 58538.4435 | 1807.7944 | 411273.9702 | 307359.3063 | 332944.3489 | 248820.8628 | 2028 | 6.4167
78 | 0 | 0 | 159.2839 | 159.2839 | 17587.8677 | 386.7843 | 30169.1766 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 58368.2029 | 1813.1608 | 412494.8403 | 307375.1939 | 334165.219 | 249006.9909 | 2028 | 6.5
79 | 0 | 0 | 159.2839 | 159.2839 | 17747.1516 | 386.7843 | 30555.961 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 58198.4574 | 1818.5273 | 413715.7104 | 307388.3895 | 335386.0891 | 249189.9321 | 2028 | 6.5833
80 | 0 | 0 | 159.2839 | 159.2839 | 17906.4355 | 386.7843 | 30942.7453 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 58029.2056 | 1823.8937 | 414936.5805 | 307398.9088 | 336606.9591 | 249369.7032 | 2028 | 6.6667
81 | 0 | 0 | 159.2839 | 159.2839 | 18065.7194 | 386.7843 | 31329.5296 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 57860.4459 | 1829.2602 | 416157.4505 | 307406.7671 | 337827.8292 | 249546.3212 | 2028 | 6.75
82 | 0 | 0 | 159.2839 | 159.2839 | 18225.0033 | 386.7843 | 31716.3139 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 57692.1771 | 1834.6266 | 417378.3206 | 307411.98 | 339048.6993 | 249719.8029 | 2028 | 6.8333
83 | 0 | 0 | 159.2839 | 159.2839 | 18384.2872 | 386.7843 | 32103.0982 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 57524.3976 | 1839.9931 | 418599.1907 | 307414.5625 | 340269.5693 | 249890.1649 | 2028 | 6.9167
84 | 0 | 0 | 159.2839 | 159.2839 | 18543.5711 | 386.7843 | 32489.8825 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 57357.106 | 1845.3595 | 419820.0607 | 307414.5301 | 341490.4394 | 250057.4241 | 2028 | 7
85 | 0 | 0 | 159.2839 | 159.2839 | 18702.855 | 386.7843 | 32876.6669 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 57190.301 | 1850.726 | 421040.9308 | 307411.898 | 342711.3095 | 250221.597 | 2029 | 7.0833
86 | 0 | 0 | 159.2839 | 159.2839 | 18862.1389 | 386.7843 | 33263.4512 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 57023.981 | 1856.0924 | 422261.8009 | 307406.6811 | 343932.1796 | 250382.7001 | 2029 | 7.1667
87 | 0 | 0 | 159.2839 | 159.2839 | 19021.4228 | 386.7843 | 33650.2355 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 56858.1448 | 1861.4589 | 423482.671 | 307398.8947 | 345153.0496 | 250540.7499 | 2029 | 7.25
88 | 0 | 0 | 159.2839 | 159.2839 | 19180.7067 | 386.7843 | 34037.0198 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 56692.7908 | 1866.8253 | 424703.541 | 307388.5536 | 346373.9197 | 250695.7628 | 2029 | 7.3333
89 | 0 | 0 | 159.2839 | 159.2839 | 19339.9906 | 386.7843 | 34423.8041 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 56527.9177 | 1872.1918 | 425924.4111 | 307375.6729 | 347594.7898 | 250847.7552 | 2029 | 7.4167
90 | 0 | 0 | 159.2839 | 159.2839 | 19499.2745 | 386.7843 | 34810.5884 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 56363.5241 | 1877.5582 | 427145.2812 | 307360.2673 | 348815.6598 | 250996.7432 | 2029 | 7.5
91 | 0 | 0 | 159.2839 | 159.2839 | 19658.5584 | 386.7843 | 35197.3727 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 56199.6086 | 1882.9247 | 428366.1512 | 307342.3517 | 350036.5299 | 251142.7431 | 2029 | 7.5833
92 | 0 | 0 | 159.2839 | 159.2839 | 19817.8423 | 386.7843 | 35584.1571 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 56036.1698 | 1888.2911 | 429587.0213 | 307321.9408 | 351257.4 | 251285.7711 | 2029 | 7.6667
93 | 0 | 0 | 159.2839 | 159.2839 | 19977.1262 | 386.7843 | 35970.9414 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 55873.2062 | 1893.6576 | 430807.8914 | 307299.0492 | 352478.2701 | 251425.843 | 2029 | 7.75
94 | 0 | 0 | 159.2839 | 159.2839 | 20136.4101 | 386.7843 | 36357.7257 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 55710.7166 | 1899.024 | 432028.7615 | 307273.6917 | 353699.1401 | 251562.975 | 2029 | 7.8333
95 | 0 | 0 | 159.2839 | 159.2839 | 20295.694 | 386.7843 | 36744.51 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 55548.6996 | 1904.3905 | 433249.6315 | 307245.8825 | 354920.0102 | 251697.1829 | 2029 | 7.9167
96 | 0 | 0 | 159.2839 | 159.2839 | 20454.9779 | 386.7843 | 37131.2943 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 55387.1537 | 1909.7569 | 434470.5016 | 307215.6364 | 356140.8803 | 251828.4827 | 2029 | 8
97 | 0 | 0 | 159.2839 | 159.2839 | 20614.2618 | 386.7843 | 37518.0786 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 55226.0777 | 1915.1234 | 435691.3717 | 307182.9677 | 357361.7503 | 251956.89 | 2030 | 8.0833
98 | 0 | 0 | 159.2839 | 159.2839 | 20773.5457 | 386.7843 | 37904.863 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 55065.4701 | 1920.4898 | 436912.2417 | 307147.8906 | 358582.6204 | 252082.4206 | 2030 | 8.1667
99 | 0 | 0 | 159.2839 | 159.2839 | 20932.8296 | 386.7843 | 38291.6473 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 54905.3295 | 1925.8563 | 438133.1118 | 307110.4196 | 359803.4905 | 252205.0901 | 2030 | 8.25
100 | 0 | 0 | 159.2839 | 159.2839 | 21092.1135 | 386.7843 | 38678.4316 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 54745.6547 | 1931.2227 | 439353.9819 | 307070.5688 | 361024.3606 | 252324.9141 | 2030 | 8.3333
101 | 0 | 0 | 159.2839 | 159.2839 | 21251.3974 | 386.7843 | 39065.2159 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 54586.4442 | 1936.5892 | 440574.852 | 307028.3524 | 362245.2306 | 252441.9082 | 2030 | 8.4167
102 | 0 | 0 | 159.2839 | 159.2839 | 21410.6813 | 386.7843 | 39452.0002 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 54427.6968 | 1941.9557 | 441795.722 | 306983.7845 | 363466.1007 | 252556.0877 | 2030 | 8.5
103 | 0 | 0 | 159.2839 | 159.2839 | 21569.9652 | 386.7843 | 39838.7845 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 54269.411 | 1947.3221 | 443016.5921 | 306936.8791 | 364686.9708 | 252667.4681 | 2030 | 8.5833
104 | 0 | 0 | 159.2839 | 159.2839 | 21729.2491 | 386.7843 | 40225.5689 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 54111.5855 | 1952.6886 | 444237.4622 | 306887.6502 | 365907.8408 | 252776.0647 | 2030 | 8.6667
105 | 0 | 0 | 159.2839 | 159.2839 | 21888.533 | 386.7843 | 40612.3532 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 53954.2191 | 1958.055 | 445458.3322 | 306836.1117 | 367128.7109 | 252881.8927 | 2030 | 8.75
106 | 0 | 0 | 159.2839 | 159.2839 | 22047.8169 | 386.7843 | 40999.1375 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 53797.3102 | 1963.4215 | 446679.2023 | 306782.2775 | 368349.581 | 252984.9672 | 2030 | 8.8333
107 | 0 | 0 | 159.2839 | 159.2839 | 22207.1008 | 386.7843 | 41385.9218 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 53640.8577 | 1968.7879 | 447900.0724 | 306726.1613 | 369570.4511 | 253085.3035 | 2030 | 8.9167
108 | 0 | 0 | 159.2839 | 159.2839 | 22366.3847 | 386.7843 | 41772.7061 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 53484.8602 | 1974.1544 | 449120.9425 | 306667.7768 | 370791.3211 | 253182.9166 | 2030 | 9
109 | 0 | 0 | 159.2839 | 159.2839 | 22525.6686 | 386.7843 | 42159.4904 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 53329.3164 | 1979.5208 | 450341.8125 | 306607.1379 | 372012.1912 | 253277.8215 | 2031 | 9.0833
110 | 0 | 0 | 159.2839 | 159.2839 | 22684.9525 | 386.7843 | 42546.2747 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 53174.2249 | 1984.8873 | 451562.6826 | 306544.2579 | 373233.0613 | 253370.033 | 2031 | 9.1667
111 | 0 | 0 | 159.2839 | 159.2839 | 22844.2364 | 386.7843 | 42933.0591 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 53019.5845 | 1990.2537 | 452783.5527 | 306479.1505 | 374453.9313 | 253459.5661 | 2031 | 9.25
112 | 0 | 0 | 159.2839 | 159.2839 | 23003.5203 | 386.7843 | 43319.8434 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 52865.3937 | 1995.6202 | 454004.4228 | 306411.8293 | 375674.8014 | 253546.4355 | 2031 | 9.3333
113 | 0 | 0 | 159.2839 | 159.2839 | 23162.8042 | 386.7843 | 43706.6277 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 52711.6514 | 2000.9866 | 455225.2928 | 306342.3075 | 376895.6715 | 253630.6561 | 2031 | 9.4167
114 | 0 | 0 | 159.2839 | 159.2839 | 23322.0881 | 386.7843 | 44093.412 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 52558.3562 | 2006.3531 | 456446.1629 | 306270.5986 | 378116.5416 | 253712.2424 | 2031 | 9.5
115 | 0 | 0 | 159.2839 | 159.2839 | 23481.372 | 386.7843 | 44480.1963 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 52405.5068 | 2011.7195 | 457667.033 | 306196.7159 | 379337.4116 | 253791.2091 | 2031 | 9.5833
116 | 0 | 0 | 159.2839 | 159.2839 | 23640.6559 | 386.7843 | 44866.9806 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 52253.1019 | 2017.086 | 458887.903 | 306120.6726 | 380558.2817 | 253867.5707 | 2031 | 9.6667
117 | 0 | 0 | 159.2839 | 159.2839 | 23799.9398 | 386.7843 | 45253.765 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 52101.1403 | 2022.4524 | 460108.7731 | 306042.482 | 381779.1518 | 253941.3417 | 2031 | 9.75
118 | 0 | 0 | 159.2839 | 159.2839 | 23959.2237 | 386.7843 | 45640.5493 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 51949.6205 | 2027.8189 | 461329.6432 | 305962.1571 | 383000.0218 | 254012.5365 | 2031 | 9.8333
119 | 0 | 0 | 159.2839 | 159.2839 | 24118.5076 | 386.7843 | 46027.3336 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 51798.5415 | 2033.1853 | 462550.5133 | 305879.711 | 384220.8919 | 254081.1695 | 2031 | 9.9167
120 | 0 | 0 | 159.2839 | 159.2839 | 24277.7915 | 386.7843 | 46414.1179 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 51647.9017 | 2038.5518 | 463771.3833 | 305795.1568 | 385441.762 | 254147.255 | 2031 | 10
121 | 0 | 0 | 159.2839 | 159.2839 | 24437.0754 | 386.7843 | 46800.9022 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 51497.7001 | 2043.9182 | 464992.2534 | 305708.5074 | 386662.6321 | 254210.8073 | 2032 | 10.0833
122 | 0 | 0 | 159.2839 | 159.2839 | 24596.3593 | 386.7843 | 47187.6865 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 51347.9353 | 2049.2847 | 466213.1235 | 305619.7757 | 387883.5021 | 254271.8404 | 2032 | 10.1667
123 | 0 | 0 | 159.2839 | 159.2839 | 24755.6432 | 386.7843 | 47574.4709 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 51198.606 | 2054.6511 | 467433.9935 | 305528.9746 | 389104.3722 | 254330.3685 | 2032 | 10.25
124 | 0 | 0 | 159.2839 | 159.2839 | 24914.9271 | 386.7843 | 47961.2552 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 51049.711 | 2060.0176 | 468654.8636 | 305436.1168 | 390325.2423 | 254386.4057 | 2032 | 10.3333
125 | 0 | 0 | 159.2839 | 159.2839 | 25074.211 | 386.7843 | 48348.0395 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 50901.2491 | 2065.384 | 469875.7337 | 305341.2151 | 391546.1123 | 254439.966 | 2032 | 10.4167
126 | 0 | 0 | 159.2839 | 159.2839 | 25233.4949 | 386.7843 | 48734.8238 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 50753.2189 | 2070.7505 | 471096.6038 | 305244.2821 | 392766.9824 | 254491.0632 | 2032 | 10.5
127 | 0 | 0 | 159.2839 | 159.2839 | 25392.7788 | 386.7843 | 49121.6081 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 50605.6191 | 2076.117 | 472317.4738 | 305145.3305 | 393987.8525 | 254539.7113 | 2032 | 10.5833
128 | 0 | 0 | 159.2839 | 159.2839 | 25552.0627 | 386.7843 | 49508.3924 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 50458.4487 | 2081.4834 | 473538.3439 | 305044.3728 | 395208.7226 | 254585.9241 | 2032 | 10.6667
129 | 0 | 0 | 159.2839 | 159.2839 | 25711.3466 | 386.7843 | 49895.1767 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 50311.7062 | 2086.8499 | 474759.214 | 304941.4215 | 396429.5926 | 254629.7154 | 2032 | 10.75
130 | 0 | 0 | 159.2839 | 159.2839 | 25870.6305 | 386.7843 | 50281.9611 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 50165.3905 | 2092.2163 | 475980.084 | 304836.4892 | 397650.4627 | 254671.0987 | 2032 | 10.8333
131 | 0 | 0 | 159.2839 | 159.2839 | 26029.9144 | 386.7843 | 50668.7454 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 50019.5002 | 2097.5828 | 477200.9541 | 304729.588 | 398871.3328 | 254710.0878 | 2032 | 10.9167
132 | 0 | 0 | 159.2839 | 159.2839 | 26189.1982 | 386.7843 | 51055.5297 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 49874.0343 | 2102.9492 | 478421.8242 | 304620.7306 | 400092.2029 | 254746.6962 | 2032 | 11
133 | 0 | 0 | 159.2839 | 159.2839 | 26348.4821 | 386.7843 | 51442.314 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 49728.9914 | 2108.3157 | 479642.6943 | 304509.9289 | 401313.0729 | 254780.9375 | 2033 | 11.0833
134 | 0 | 0 | 159.2839 | 159.2839 | 26507.766 | 386.7843 | 51829.0983 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 49584.3703 | 2113.6821 | 480863.5643 | 304397.1955 | 402533.943 | 254812.8251 | 2033 | 11.1667
135 | 0 | 0 | 159.2839 | 159.2839 | 26667.0499 | 386.7843 | 52215.8826 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 49440.1698 | 2119.0486 | 482084.4344 | 304282.5423 | 403754.8131 | 254842.3724 | 2033 | 11.25
136 | 0 | 0 | 159.2839 | 159.2839 | 26826.3338 | 386.7843 | 52602.667 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 49296.3887 | 2124.415 | 483305.3045 | 304165.9815 | 404975.6831 | 254869.5928 | 2033 | 11.3333
137 | 0 | 0 | 159.2839 | 159.2839 | 26985.6177 | 386.7843 | 52989.4513 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 49153.0257 | 2129.7815 | 484526.1745 | 304047.5252 | 406196.5532 | 254894.4995 | 2033 | 11.4167
138 | 0 | 0 | 159.2839 | 159.2839 | 27144.9016 | 386.7843 | 53376.2356 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 49010.0797 | 2135.1479 | 485747.0446 | 303927.1854 | 407417.4233 | 254917.1058 | 2033 | 11.5
139 | 0 | 0 | 159.2839 | 159.2839 | 27304.1855 | 386.7843 | 53763.0199 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 48867.5493 | 2140.5144 | 486967.9147 | 303804.9741 | 408638.2934 | 254937.4248 | 2033 | 11.5833
140 | 0 | 0 | 159.2839 | 159.2839 | 27463.4694 | 386.7843 | 54149.8042 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 48725.4335 | 2145.8808 | 488188.7848 | 303680.9031 | 409859.1634 | 254955.4696 | 2033 | 11.6667
141 | 0 | 0 | 159.2839 | 159.2839 | 27622.7533 | 386.7843 | 54536.5885 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 48583.7309 | 2151.2473 | 489409.6548 | 303554.9843 | 411080.0335 | 254971.2534 | 2033 | 11.75
142 | 0 | 0 | 159.2839 | 159.2839 | 27782.0372 | 386.7843 | 54923.3729 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 48442.4405 | 2156.6137 | 490630.5249 | 303427.2295 | 412300.9036 | 254984.789 | 2033 | 11.8333
143 | 0 | 0 | 159.2839 | 159.2839 | 27941.3211 | 386.7843 | 55310.1572 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 48301.5609 | 2161.9802 | 491851.395 | 303297.6504 | 413521.7736 | 254996.0895 | 2033 | 11.9167
144 | 0 | 0 | 159.2839 | 159.2839 | 28100.605 | 386.7843 | 55696.9415 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 48161.0911 | 2167.3466 | 493072.265 | 303166.2588 | 414742.6437 | 255005.1677 | 2033 | 12
145 | 0 | 0 | 159.2839 | 159.2839 | 28259.8889 | 386.7843 | 56083.7258 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 48021.0297 | 2172.7131 | 494293.1351 | 303033.0662 | 415963.5138 | 255012.0365 | 2034 | 12.0833
146 | 0 | 0 | 159.2839 | 159.2839 | 28419.1728 | 386.7843 | 56470.5101 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 47881.3757 | 2178.0795 | 495514.0052 | 302898.0843 | 417184.3839 | 255016.7086 | 2034 | 12.1667
147 | 0 | 0 | 159.2839 | 159.2839 | 28578.4567 | 386.7843 | 56857.2944 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 47742.1278 | 2183.446 | 496734.8753 | 302761.3246 | 418405.2539 | 255019.1968 | 2034 | 12.25
148 | 0 | 0 | 159.2839 | 159.2839 | 28737.7406 | 386.7843 | 57244.0788 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 47603.2849 | 2188.8124 | 497955.7453 | 302622.7986 | 419626.124 | 255019.5137 | 2034 | 12.3333
149 | 0 | 0 | 159.2839 | 159.2839 | 28897.0245 | 386.7843 | 57630.8631 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 47464.8458 | 2194.1789 | 499176.6154 | 302482.5177 | 420846.9941 | 255017.6719 | 2034 | 12.4167
150 | 0 | 0 | 159.2839 | 159.2839 | 29056.3084 | 386.7843 | 58017.6474 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 47326.8093 | 2199.5453 | 500397.4855 | 302340.4932 | 422067.8641 | 255013.684 | 2034 | 12.5
151 | 0 | 0 | 159.2839 | 159.2839 | 29215.5923 | 386.7843 | 58404.4317 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 47189.1742 | 2204.9118 | 501618.3555 | 302196.7366 | 423288.7342 | 255007.5624 | 2034 | 12.5833
152 | 0 | 0 | 159.2839 | 159.2839 | 29374.8762 | 386.7843 | 58791.216 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 47051.9393 | 2210.2783 | 502839.2256 | 302051.259 | 424509.6043 | 254999.3197 | 2034 | 12.6667
153 | 0 | 0 | 159.2839 | 159.2839 | 29534.1601 | 386.7843 | 59178.0003 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 46915.1036 | 2215.6447 | 504060.0957 | 301904.0718 | 425730.4744 | 254988.9681 | 2034 | 12.75
154 | 0 | 0 | 159.2839 | 159.2839 | 29693.444 | 386.7843 | 59564.7846 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 46778.6658 | 2221.0112 | 505280.9658 | 301755.186 | 426951.3444 | 254976.5202 | 2034 | 12.8333
155 | 0 | 0 | 159.2839 | 159.2839 | 29852.7279 | 386.7843 | 59951.569 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 46642.6249 | 2226.3776 | 506501.8358 | 301604.6129 | 428172.2145 | 254961.988 | 2034 | 12.9167
156 | 0 | 0 | 159.2839 | 159.2839 | 30012.0118 | 386.7843 | 60338.3533 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 46506.9795 | 2231.7441 | 507722.7059 | 301452.3634 | 429393.0846 | 254945.3839 | 2034 | 13
157 | 0 | 0 | 159.2839 | 159.2839 | 30171.2957 | 386.7843 | 60725.1376 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 46371.7286 | 2237.1105 | 508943.576 | 301298.4486 | 430613.9546 | 254926.72 | 2035 | 13.0833
158 | 0 | 0 | 159.2839 | 159.2839 | 30330.5796 | 386.7843 | 61111.9219 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 46236.8711 | 2242.477 | 510164.446 | 301142.8796 | 431834.8247 | 254906.0085 | 2035 | 13.1667
159 | 0 | 0 | 159.2839 | 159.2839 | 30489.8635 | 386.7843 | 61498.7062 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 46102.4057 | 2247.8434 | 511385.3161 | 300985.6671 | 433055.6948 | 254883.2614 | 2035 | 13.25
160 | 0 | 0 | 159.2839 | 159.2839 | 30649.1474 | 386.7843 | 61885.4905 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 45968.3314 | 2253.2099 | 512606.1862 | 300826.8221 | 434276.5649 | 254858.4907 | 2035 | 13.3333
161 | 0 | 0 | 159.2839 | 159.2839 | 30808.4313 | 386.7843 | 62272.2749 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 45834.647 | 2258.5763 | 513827.0563 | 300666.3554 | 435497.4349 | 254831.7084 | 2035 | 13.4167
162 | 0 | 0 | 159.2839 | 159.2839 | 30967.7152 | 386.7843 | 62659.0592 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 45701.3514 | 2263.9428 | 515047.9263 | 300504.2778 | 436718.305 | 254802.9264 | 2035 | 13.5
163 | 0 | 0 | 159.2839 | 159.2839 | 31126.9991 | 386.7843 | 63045.8435 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 45568.4435 | 2269.3092 | 516268.7964 | 300340.6 | 437939.1751 | 254772.1565 | 2035 | 13.5833
164 | 0 | 0 | 159.2839 | 159.2839 | 31286.283 | 386.7843 | 63432.6278 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 45435.922 | 2274.6757 | 517489.6665 | 300175.3327 | 439160.0451 | 254739.4106 | 2035 | 13.6667
165 | 0 | 0 | 159.2839 | 159.2839 | 31445.5669 | 386.7843 | 63819.4121 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 45303.786 | 2280.0421 | 518710.5366 | 300008.4865 | 440380.9152 | 254704.7005 | 2035 | 13.75
166 | 0 | 0 | 159.2839 | 159.2839 | 31604.8508 | 386.7843 | 64206.1964 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 45172.0342 | 2285.4086 | 519931.4066 | 299840.072 | 441601.7853 | 254668.0377 | 2035 | 13.8333
167 | 0 | 0 | 159.2839 | 159.2839 | 31764.1347 | 386.7843 | 64592.9808 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 45040.6656 | 2290.775 | 521152.2767 | 299670.0997 | 442822.6554 | 254629.4341 | 2035 | 13.9167
168 | 0 | 0 | 159.2839 | 159.2839 | 31923.4186 | 386.7843 | 64979.7651 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 44909.6791 | 2296.1415 | 522373.1468 | 299498.5801 | 444043.5254 | 254588.901 | 2035 | 14
169 | 0 | 0 | 159.2839 | 159.2839 | 32082.7025 | 386.7843 | 65366.5494 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 44779.0734 | 2301.5079 | 523594.0168 | 299325.5237 | 445264.3955 | 254546.4503 | 2036 | 14.0833
170 | 0 | 0 | 159.2839 | 159.2839 | 32241.9864 | 386.7843 | 65753.3337 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 44648.8476 | 2306.8744 | 524814.8869 | 299150.9408 | 446485.2656 | 254502.0932 | 2036 | 14.1667
171 | 0 | 0 | 159.2839 | 159.2839 | 32401.2703 | 386.7843 | 66140.118 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 44519.0005 | 2312.2408 | 526035.757 | 298974.8418 | 447706.1356 | 254455.8413 | 2036 | 14.25
172 | 0 | 0 | 159.2839 | 159.2839 | 32560.5542 | 386.7843 | 66526.9023 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 44389.5311 | 2317.6073 | 527256.6271 | 298797.237 | 448927.0057 | 254407.7059 | 2036 | 14.3333
173 | 0 | 0 | 159.2839 | 159.2839 | 32719.8381 | 386.7843 | 66913.6866 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 44260.4381 | 2322.9737 | 528477.4971 | 298618.1366 | 450147.8758 | 254357.6985 | 2036 | 14.4167
174 | 0 | 0 | 159.2839 | 159.2839 | 32879.122 | 386.7843 | 67300.471 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 44131.7206 | 2328.3402 | 529698.3672 | 298437.5508 | 451368.7459 | 254305.8302 | 2036 | 14.5
175 | 0 | 0 | 159.2839 | 159.2839 | 33038.4059 | 386.7843 | 67687.2553 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 44003.3774 | 2333.7066 | 530919.2373 | 298255.4898 | 452589.6159 | 254252.1124 | 2036 | 14.5833
176 | 0 | 0 | 159.2839 | 159.2839 | 33197.6898 | 386.7843 | 68074.0396 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 43875.4075 | 2339.0731 | 532140.1073 | 298071.9637 | 453810.486 | 254196.5562 | 2036 | 14.6667
177 | 0 | 0 | 159.2839 | 159.2839 | 33356.9737 | 386.7843 | 68460.8239 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 43747.8097 | 2344.4396 | 533360.9774 | 297886.9826 | 455031.3561 | 254139.1729 | 2036 | 14.75
178 | 0 | 0 | 159.2839 | 159.2839 | 33516.2576 | 386.7843 | 68847.6082 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 43620.583 | 2349.806 | 534581.8475 | 297700.5564 | 456252.2261 | 254079.9734 | 2036 | 14.8333
179 | 0 | 0 | 159.2839 | 159.2839 | 33675.5415 | 386.7843 | 69234.3925 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 43493.7263 | 2355.1725 | 535802.7176 | 297512.6951 | 457473.0962 | 254018.9688 | 2036 | 14.9167
180 | 0 | 0 | 159.2839 | 159.2839 | 33834.8254 | 386.7843 | 69621.1769 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 43367.2385 | 2360.5389 | 537023.5876 | 297323.4087 | 458693.9663 | 253956.1702 | 2036 | 15
181 | 0 | 0 | 159.2839 | 159.2839 | 33994.1093 | 386.7843 | 70007.9612 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 43241.1186 | 2365.9054 | 538244.4577 | 297132.7071 | 459914.8364 | 253891.5885 | 2037 | 15.0833
182 | 0 | 0 | 159.2839 | 159.2839 | 34153.3932 | 386.7843 | 70394.7455 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 43115.3654 | 2371.2718 | 539465.3278 | 296940.6 | 461135.7064 | 253825.2345 | 2037 | 15.1667
183 | 0 | 0 | 159.2839 | 159.2839 | 34312.6771 | 386.7843 | 70781.5298 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 42989.978 | 2376.6383 | 540686.1978 | 296747.0972 | 462356.5765 | 253757.1192 | 2037 | 15.25
184 | 0 | 0 | 159.2839 | 159.2839 | 34471.961 | 386.7843 | 71168.3141 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 42864.9552 | 2382.0047 | 541907.0679 | 296552.2086 | 463577.4466 | 253687.2533 | 2037 | 15.3333
185 | 0 | 0 | 159.2839 | 159.2839 | 34631.2449 | 386.7843 | 71555.0984 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 42740.296 | 2387.3712 | 543127.938 | 296355.9437 | 464798.3167 | 253615.6477 | 2037 | 15.4167
186 | 0 | 0 | 159.2839 | 159.2839 | 34790.5287 | 386.7843 | 71941.8828 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 42615.9994 | 2392.7376 | 544348.8081 | 296158.3123 | 466019.1867 | 253542.3129 | 2037 | 15.5
187 | 0 | 0 | 159.2839 | 159.2839 | 34949.8126 | 386.7843 | 72328.6671 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 42492.0642 | 2398.1041 | 545569.6781 | 295959.324 | 467240.0568 | 253467.2598 | 2037 | 15.5833
188 | 0 | 0 | 159.2839 | 159.2839 | 35109.0965 | 386.7843 | 72715.4514 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 42368.4894 | 2403.4705 | 546790.5482 | 295758.9882 | 468460.9269 | 253390.4988 | 2037 | 15.6667
189 | 0 | 0 | 159.2839 | 159.2839 | 35268.3804 | 386.7843 | 73102.2357 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 42245.274 | 2408.837 | 548011.4183 | 295557.3146 | 469681.7969 | 253312.0406 | 2037 | 15.75
190 | 0 | 0 | 159.2839 | 159.2839 | 35427.6643 | 386.7843 | 73489.02 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 42122.417 | 2414.2034 | 549232.2883 | 295354.3127 | 470902.667 | 253231.8957 | 2037 | 15.8333
191 | 0 | 0 | 159.2839 | 159.2839 | 35586.9482 | 386.7843 | 73875.8043 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 41999.9172 | 2419.5699 | 550453.1584 | 295149.9917 | 472123.5371 | 253150.0745 | 2037 | 15.9167
192 | 0 | 0 | 159.2839 | 159.2839 | 35746.2321 | 386.7843 | 74262.5887 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 41877.7737 | 2424.9363 | 551674.0285 | 294944.3613 | 473344.4072 | 253066.5875 | 2037 | 16
193 | 0 | 0 | 159.2839 | 159.2839 | 35905.516 | 386.7843 | 74649.373 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 41755.9854 | 2430.3028 | 552894.8986 | 294737.4305 | 474565.2772 | 252981.4451 | 2038 | 16.0833
194 | 0 | 0 | 159.2839 | 159.2839 | 36064.7999 | 386.7843 | 75036.1573 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 41634.5513 | 2435.6692 | 554115.7686 | 294529.2089 | 475786.1473 | 252894.6576 | 2038 | 16.1667
195 | 0 | 0 | 159.2839 | 159.2839 | 36224.0838 | 386.7843 | 75422.9416 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 41513.4704 | 2441.0357 | 555336.6387 | 294319.7056 | 477007.0174 | 252806.2353 | 2038 | 16.25
196 | 0 | 0 | 159.2839 | 159.2839 | 36383.3677 | 386.7843 | 75809.7259 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 41392.7415 | 2446.4021 | 556557.5088 | 294108.9299 | 478227.8874 | 252716.1884 | 2038 | 16.3333
197 | 0 | 0 | 159.2839 | 159.2839 | 36542.6516 | 386.7843 | 76196.5102 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 41272.3638 | 2451.7686 | 557778.3788 | 293896.8909 | 479448.7575 | 252624.5271 | 2038 | 16.4167
198 | 0 | 0 | 159.2839 | 159.2839 | 36701.9355 | 386.7843 | 76583.2945 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 41152.3362 | 2457.135 | 558999.2489 | 293683.5978 | 480669.6276 | 252531.2616 | 2038 | 16.5
199 | 0 | 0 | 159.2839 | 159.2839 | 36861.2194 | 386.7843 | 76970.0789 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 41032.6576 | 2462.5015 | 560220.119 | 293469.0596 | 481890.4977 | 252436.402 | 2038 | 16.5833
200 | 0 | 0 | 159.2839 | 159.2839 | 37020.5033 | 386.7843 | 77356.8632 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 40913.327 | 2467.8679 | 561440.9891 | 293253.2854 | 483111.3677 | 252339.9583 | 2038 | 16.6667
201 | 0 | 0 | 159.2839 | 159.2839 | 37179.7872 | 386.7843 | 77743.6475 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 40794.3435 | 2473.2344 | 562661.8591 | 293036.2842 | 484332.2378 | 252241.9406 | 2038 | 16.75
202 | 0 | 0 | 159.2839 | 159.2839 | 37339.0711 | 386.7843 | 78130.4318 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 40675.7061 | 2478.6009 | 563882.7292 | 292818.0649 | 485553.1079 | 252142.3589 | 2038 | 16.8333
203 | 0 | 0 | 159.2839 | 159.2839 | 37498.355 | 386.7843 | 78517.2161 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 40557.4136 | 2483.9673 | 565103.5993 | 292598.6366 | 486773.9779 | 252041.223 | 2038 | 16.9167
204 | 0 | 0 | 159.2839 | 159.2839 | 37657.6389 | 386.7843 | 78904.0004 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 40439.4652 | 2489.3338 | 566324.4693 | 292378.008 | 487994.848 | 251938.5428 | 2038 | 17
205 | 0 | 0 | 159.2839 | 159.2839 | 37816.9228 | 386.7843 | 79290.7848 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 40321.8597 | 2494.7002 | 567545.3394 | 292156.1879 | 489215.7181 | 251834.3282 | 2039 | 17.0833
206 | 0 | 0 | 159.2839 | 159.2839 | 37976.2067 | 386.7843 | 79677.5691 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 40204.5963 | 2500.0667 | 568766.2095 | 291933.1853 | 490436.5882 | 251728.589 | 2039 | 17.1667
207 | 0 | 0 | 159.2839 | 159.2839 | 38135.4906 | 386.7843 | 80064.3534 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 40087.674 | 2505.4331 | 569987.0796 | 291709.0088 | 491657.4582 | 251621.3349 | 2039 | 17.25
208 | 0 | 0 | 159.2839 | 159.2839 | 38294.7745 | 386.7843 | 80451.1377 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 39971.0916 | 2510.7996 | 571207.9496 | 291483.6672 | 492878.3283 | 251512.5756 | 2039 | 17.3333
209 | 0 | 0 | 159.2839 | 159.2839 | 38454.0584 | 386.7843 | 80837.922 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 39854.8483 | 2516.166 | 572428.8197 | 291257.1691 | 494099.1984 | 251402.3208 | 2039 | 17.4167
210 | 0 | 0 | 159.2839 | 159.2839 | 38613.3423 | 386.7843 | 81224.7063 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 39738.943 | 2521.5325 | 573649.6898 | 291029.5232 | 495320.0684 | 251290.5802 | 2039 | 17.5
211 | 0 | 0 | 159.2839 | 159.2839 | 38772.6262 | 386.7843 | 81611.4907 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 39623.3749 | 2526.8989 | 574870.5598 | 290800.738 | 496540.9385 | 251177.3632 | 2039 | 17.5833
212 | 0 | 0 | 159.2839 | 159.2839 | 38931.9101 | 386.7843 | 81998.275 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 39508.1428 | 2532.2654 | 576091.4299 | 290570.8221 | 497761.8086 | 251062.6794 | 2039 | 17.6667
213 | 0 | 0 | 159.2839 | 159.2839 | 39091.194 | 386.7843 | 82385.0593 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 39393.2458 | 2537.6318 | 577312.3 | 290339.7841 | 498982.6787 | 250946.5383 | 2039 | 17.75
214 | 0 | 0 | 159.2839 | 159.2839 | 39250.4779 | 386.7843 | 82771.8436 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 39278.683 | 2542.9983 | 578533.1701 | 290107.6323 | 500203.5487 | 250828.9493 | 2039 | 17.8333
215 | 0 | 0 | 159.2839 | 159.2839 | 39409.7618 | 386.7843 | 83158.6279 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 39164.4533 | 2548.3647 | 579754.0401 | 289874.3753 | 501424.4188 | 250709.922 | 2039 | 17.9167
216 | 0 | 0 | 159.2839 | 159.2839 | 39569.0457 | 386.7843 | 83545.4122 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 39050.5559 | 2553.7312 | 580974.9102 | 289640.0214 | 502645.2889 | 250589.4655 | 2039 | 18
217 | 0 | 0 | 159.2839 | 159.2839 | 39728.3296 | 386.7843 | 83932.1965 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 38936.9897 | 2559.0976 | 582195.7803 | 289404.5789 | 503866.1589 | 250467.5892 | 2040 | 18.0833
218 | 0 | 0 | 159.2839 | 159.2839 | 39887.6135 | 386.7843 | 84318.9809 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 38823.7537 | 2564.4641 | 583416.6504 | 289168.0562 | 505087.029 | 250344.3025 | 2040 | 18.1667
219 | 0 | 0 | 159.2839 | 159.2839 | 40046.8974 | 386.7843 | 84705.7652 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 38710.8471 | 2569.8305 | 584637.5204 | 288930.4616 | 506307.8991 | 250219.6145 | 2040 | 18.25
220 | 0 | 0 | 159.2839 | 159.2839 | 40206.1813 | 386.7843 | 85092.5495 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 38598.2688 | 2575.197 | 585858.3905 | 288691.8032 | 507528.7692 | 250093.5344 | 2040 | 18.3333
221 | 0 | 0 | 159.2839 | 159.2839 | 40365.4652 | 386.7843 | 85479.3338 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 38486.0179 | 2580.5634 | 587079.2606 | 288452.0894 | 508749.6392 | 249966.0715 | 2040 | 18.4167
222 | 0 | 0 | 159.2839 | 159.2839 | 40524.7491 | 386.7843 | 85866.1181 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 38374.0935 | 2585.9299 | 588300.1306 | 288211.3282 | 509970.5093 | 249837.2347 | 2040 | 18.5
223 | 0 | 0 | 159.2839 | 159.2839 | 40684.033 | 386.7843 | 86252.9024 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 38262.4945 | 2591.2963 | 589521.0007 | 287969.5277 | 511191.3794 | 249707.0332 | 2040 | 18.5833
224 | 0 | 0 | 159.2839 | 159.2839 | 40843.3169 | 386.7843 | 86639.6868 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 38151.2201 | 2596.6628 | 590741.8708 | 287726.6961 | 512412.2494 | 249575.476 | 2040 | 18.6667
225 | 0 | 0 | 159.2839 | 159.2839 | 41002.6008 | 386.7843 | 87026.4711 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 38040.2693 | 2602.0292 | 591962.7409 | 287482.8414 | 513633.1195 | 249442.572 | 2040 | 18.75
226 | 0 | 0 | 159.2839 | 159.2839 | 41161.8847 | 386.7843 | 87413.2554 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 37929.6412 | 2607.3957 | 593183.6109 | 287237.9715 | 514853.9896 | 249308.3303 | 2040 | 18.8333
227 | 0 | 0 | 159.2839 | 159.2839 | 41321.1686 | 386.7843 | 87800.0397 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 37819.3348 | 2612.7622 | 594404.481 | 286992.0946 | 516074.8597 | 249172.7597 | 2040 | 18.9167
228 | 0 | 0 | 159.2839 | 159.2839 | 41480.4525 | 386.7843 | 88186.824 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 37709.3492 | 2618.1286 | 595625.3511 | 286745.2184 | 517295.7297 | 249035.8691 | 2040 | 19
229 | 0 | 0 | 159.2839 | 159.2839 | 41639.7364 | 386.7843 | 88573.6083 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 37599.6835 | 2623.4951 | 596846.2211 | 286497.3509 | 518516.5998 | 248897.6674 | 2041 | 19.0833
230 | 0 | 0 | 159.2839 | 159.2839 | 41799.0203 | 386.7843 | 88960.3927 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 37490.3367 | 2628.8615 | 598067.0912 | 286248.4999 | 519737.4699 | 248758.1632 | 2041 | 19.1667
231 | 0 | 0 | 159.2839 | 159.2839 | 41958.3042 | 386.7843 | 89347.177 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 37381.3079 | 2634.228 | 599287.9613 | 285998.6732 | 520958.3399 | 248617.3654 | 2041 | 19.25
232 | 0 | 0 | 159.2839 | 159.2839 | 42117.5881 | 386.7843 | 89733.9613 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 37272.5961 | 2639.5944 | 600508.8314 | 285747.8787 | 522179.21 | 248475.2826 | 2041 | 19.3333
233 | 0 | 0 | 159.2839 | 159.2839 | 42276.872 | 386.7843 | 90120.7456 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 37164.2005 | 2644.9609 | 601729.7014 | 285496.1241 | 523400.0801 | 248331.9235 | 2041 | 19.4167
234 | 0 | 0 | 159.2839 | 159.2839 | 42436.1559 | 386.7843 | 90507.5299 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 37056.1202 | 2650.3273 | 602950.5715 | 285243.417 | 524620.9502 | 248187.2968 | 2041 | 19.5
235 | 0 | 0 | 159.2839 | 159.2839 | 42595.4398 | 386.7843 | 90894.3142 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 36948.3542 | 2655.6938 | 604171.4416 | 284989.7652 | 525841.8202 | 248041.411 | 2041 | 19.5833
236 | 0 | 0 | 159.2839 | 159.2839 | 42754.7237 | 386.7843 | 91281.0985 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 36840.9015 | 2661.0602 | 605392.3116 | 284735.1762 | 527062.6903 | 247894.2747 | 2041 | 19.6667
237 | 0 | 0 | 159.2839 | 159.2839 | 42914.0076 | 386.7843 | 91667.8829 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 36733.7614 | 2666.4267 | 606613.1817 | 284479.6578 | 528283.5604 | 247745.8964 | 2041 | 19.75
238 | 0 | 0 | 159.2839 | 159.2839 | 43073.2915 | 386.7843 | 92054.6672 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 36626.9328 | 2671.7931 | 607834.0518 | 284223.2173 | 529504.4305 | 247596.2845 | 2041 | 19.8333
239 | 0 | 0 | 159.2839 | 159.2839 | 43232.5754 | 386.7843 | 92441.4515 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 36520.415 | 2677.1596 | 609054.9219 | 283965.8624 | 530725.3005 | 247445.4475 | 2041 | 19.9167
240 | 0 | 0 | 159.2839 | 159.2839 | 43391.8593 | 386.7843 | 92828.2358 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 36414.2068 | 2682.526 | 610275.7919 | 283707.6006 | 531946.1706 | 247293.3937 | 2041 | 20
241 | 0 | 0 | 159.2839 | 159.2839 | 43551.1431 | 386.7843 | 93215.0201 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 36308.3076 | 2687.8925 | 611496.662 | 283448.4392 | 533167.0407 | 247140.1316 | 2042 | 20.0833
242 | 0 | 0 | 159.2839 | 159.2839 | 43710.427 | 386.7843 | 93601.8044 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 36202.7164 | 2693.2589 | 612717.5321 | 283188.3858 | 534387.9107 | 246985.6694 | 2042 | 20.1667
243 | 0 | 0 | 159.2839 | 159.2839 | 43869.7109 | 386.7843 | 93988.5888 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 36097.4322 | 2698.6254 | 613938.4021 | 282927.4476 | 535608.7808 | 246830.0154 | 2042 | 20.25
244 | 0 | 0 | 159.2839 | 159.2839 | 44028.9948 | 386.7843 | 94375.3731 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 35992.4542 | 2703.9918 | 615159.2722 | 282665.6321 | 536829.6509 | 246673.1779 | 2042 | 20.3333
245 | 0 | 0 | 159.2839 | 159.2839 | 44188.2787 | 386.7843 | 94762.1574 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 35887.7815 | 2709.3583 | 616380.1423 | 282402.9465 | 538050.521 | 246515.165 | 2042 | 20.4167
246 | 0 | 0 | 159.2839 | 159.2839 | 44347.5626 | 386.7843 | 95148.9417 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 35783.4132 | 2714.7247 | 617601.0124 | 282139.3982 | 539271.391 | 246355.985 | 2042 | 20.5
247 | 0 | 0 | 159.2839 | 159.2839 | 44506.8465 | 386.7843 | 95535.726 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 35679.3484 | 2720.0912 | 618821.8824 | 281874.9943 | 540492.2611 | 246195.6459 | 2042 | 20.5833
248 | 0 | 0 | 159.2839 | 159.2839 | 44666.1304 | 386.7843 | 95922.5103 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 35575.5863 | 2725.4576 | 620042.7525 | 281609.7421 | 541713.1312 | 246034.1558 | 2042 | 20.6667
249 | 0 | 0 | 159.2839 | 159.2839 | 44825.4143 | 386.7843 | 96309.2947 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 35472.1259 | 2730.8241 | 621263.6226 | 281343.6487 | 542934.0012 | 245871.5228 | 2042 | 20.75
250 | 0 | 0 | 159.2839 | 159.2839 | 44984.6982 | 386.7843 | 96696.079 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 35368.9665 | 2736.1905 | 622484.4926 | 281076.7213 | 544154.8713 | 245707.7548 | 2042 | 20.8333
251 | 0 | 0 | 159.2839 | 159.2839 | 45143.9821 | 386.7843 | 97082.8633 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 35266.107 | 2741.557 | 623705.3627 | 280808.967 | 545375.7414 | 245542.86 | 2042 | 20.9167
252 | 0 | 0 | 159.2839 | 159.2839 | 45303.266 | 386.7843 | 97469.6476 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 35163.5466 | 2746.9235 | 624926.2328 | 280540.3928 | 546596.6115 | 245376.8461 | 2042 | 21
253 | 0 | 0 | 159.2839 | 159.2839 | 45462.5499 | 386.7843 | 97856.4319 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 35061.2846 | 2752.2899 | 626147.1029 | 280271.0057 | 547817.4815 | 245209.7212 | 2043 | 21.0833
254 | 0 | 0 | 159.2839 | 159.2839 | 45621.8338 | 386.7843 | 98243.2162 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 34959.3199 | 2757.6564 | 627367.9729 | 280000.8129 | 549038.3516 | 245041.493 | 2043 | 21.1667
255 | 0 | 0 | 159.2839 | 159.2839 | 45781.1177 | 386.7843 | 98630.0006 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 34857.6517 | 2763.0228 | 628588.843 | 279729.8212 | 550259.2217 | 244872.1695 | 2043 | 21.25
256 | 0 | 0 | 159.2839 | 159.2839 | 45940.4016 | 386.7843 | 99016.7849 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 34756.2792 | 2768.3893 | 629809.7131 | 279458.0375 | 551480.0917 | 244701.7583 | 2043 | 21.3333
257 | 0 | 0 | 159.2839 | 159.2839 | 46099.6855 | 386.7843 | 99403.5692 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 34655.2016 | 2773.7557 | 631030.5831 | 279185.4689 | 552700.9618 | 244530.2673 | 2043 | 21.4167
258 | 0 | 0 | 159.2839 | 159.2839 | 46258.9694 | 386.7843 | 99790.3535 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 34554.4179 | 2779.1222 | 632251.4532 | 278912.122 | 553921.8319 | 244357.7042 | 2043 | 21.5
259 | 0 | 0 | 159.2839 | 159.2839 | 46418.2533 | 386.7843 | 100177.1378 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 34453.9272 | 2784.4886 | 633472.3233 | 278638.0039 | 555142.702 | 244184.0766 | 2043 | 21.5833
260 | 0 | 0 | 159.2839 | 159.2839 | 46577.5372 | 386.7843 | 100563.9221 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 34353.7289 | 2789.8551 | 634693.1934 | 278363.1212 | 556363.572 | 244009.3923 | 2043 | 21.6667
261 | 0 | 0 | 159.2839 | 159.2839 | 46736.8211 | 386.7843 | 100950.7064 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 34253.8219 | 2795.2215 | 635914.0634 | 278087.4807 | 557584.4421 | 243833.6588 | 2043 | 21.75
262 | 0 | 0 | 159.2839 | 159.2839 | 46896.105 | 386.7843 | 101337.4908 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 34154.2054 | 2800.588 | 637134.9335 | 277811.0892 | 558805.3122 | 243656.8837 | 2043 | 21.8333
263 | 0 | 0 | 159.2839 | 159.2839 | 47055.3889 | 386.7843 | 101724.2751 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 34054.8787 | 2805.9544 | 638355.8036 | 277533.9533 | 560026.1822 | 243479.0746 | 2043 | 21.9167
264 | 0 | 0 | 159.2839 | 159.2839 | 47214.6728 | 386.7843 | 102111.0594 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 33955.8408 | 2811.3209 | 639576.6737 | 277256.0798 | 561247.0523 | 243300.2389 | 2043 | 22
265 | 0 | 0 | 159.2839 | 159.2839 | 47373.9567 | 386.7843 | 102497.8437 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 33857.091 | 2816.6873 | 640797.5437 | 276977.4752 | 562467.9224 | 243120.3842 | 2044 | 22.0833
266 | 0 | 0 | 159.2839 | 159.2839 | 47533.2406 | 386.7843 | 102884.628 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 33758.6283 | 2822.0538 | 642018.4138 | 276698.1462 | 563688.7925 | 242939.5178 | 2044 | 22.1667
267 | 0 | 0 | 159.2839 | 159.2839 | 47692.5245 | 386.7843 | 103271.4123 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 33660.452 | 2827.4202 | 643239.2839 | 276418.0993 | 564909.6625 | 242757.6473 | 2044 | 22.25
268 | 0 | 0 | 159.2839 | 159.2839 | 47851.8084 | 386.7843 | 103658.1967 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 33562.5612 | 2832.7867 | 644460.1539 | 276137.3411 | 566130.5326 | 242574.7799 | 2044 | 22.3333
269 | 0 | 0 | 159.2839 | 159.2839 | 48011.0923 | 386.7843 | 104044.981 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 33464.9551 | 2838.1531 | 645681.024 | 275855.8781 | 567351.4027 | 242390.923 | 2044 | 22.4167
270 | 0 | 0 | 159.2839 | 159.2839 | 48170.3762 | 386.7843 | 104431.7653 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 33367.6328 | 2843.5196 | 646901.8941 | 275573.7167 | 568572.2727 | 242206.0839 | 2044 | 22.5
271 | 0 | 0 | 159.2839 | 159.2839 | 48329.6601 | 386.7843 | 104818.5496 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 33270.5936 | 2848.886 | 648122.7642 | 275290.8634 | 569793.1428 | 242020.2698 | 2044 | 22.5833
272 | 0 | 0 | 159.2839 | 159.2839 | 48488.944 | 386.7843 | 105205.3339 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 33173.8366 | 2854.2525 | 649343.6342 | 275007.3246 | 571014.0129 | 241833.4881 | 2044 | 22.6667
273 | 0 | 0 | 159.2839 | 159.2839 | 48648.2279 | 386.7843 | 105592.1182 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 33077.3609 | 2859.6189 | 650564.5043 | 274723.1067 | 572234.883 | 241645.7458 | 2044 | 22.75
274 | 0 | 0 | 159.2839 | 159.2839 | 48807.5118 | 386.7843 | 105978.9026 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 32981.1659 | 2864.9854 | 651785.3744 | 274438.2161 | 573455.753 | 241457.0502 | 2044 | 22.8333
275 | 0 | 0 | 159.2839 | 159.2839 | 48966.7957 | 386.7843 | 106365.6869 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 32885.2506 | 2870.3518 | 653006.2444 | 274152.659 | 574676.6231 | 241267.4084 | 2044 | 22.9167
276 | 0 | 0 | 159.2839 | 159.2839 | 49126.0796 | 386.7843 | 106752.4712 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 32789.6142 | 2875.7183 | 654227.1145 | 273866.4417 | 575897.4932 | 241076.8275 | 2044 | 23
277 | 0 | 0 | 159.2839 | 159.2839 | 49285.3635 | 386.7843 | 107139.2555 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 32694.2559 | 2881.0848 | 655447.9846 | 273579.5705 | 577118.3632 | 240885.3145 | 2045 | 23.0833
278 | 0 | 0 | 159.2839 | 159.2839 | 49444.6474 | 386.7843 | 107526.0398 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 32599.175 | 2886.4512 | 656668.8547 | 273292.0516 | 578339.2333 | 240692.8766 | 2045 | 23.1667
279 | 0 | 0 | 159.2839 | 159.2839 | 49603.9313 | 386.7843 | 107912.8241 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 32504.3706 | 2891.8177 | 657889.7247 | 273003.8912 | 579560.1034 | 240499.5206 | 2045 | 23.25
280 | 0 | 0 | 159.2839 | 159.2839 | 49763.2152 | 386.7843 | 108299.6084 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 32409.8419 | 2897.1841 | 659110.5948 | 272715.0955 | 580780.9735 | 240305.2536 | 2045 | 23.3333
281 | 0 | 0 | 159.2839 | 159.2839 | 49922.4991 | 386.7843 | 108686.3928 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 32315.5881 | 2902.5506 | 660331.4649 | 272425.6706 | 582001.8435 | 240110.0825 | 2045 | 23.4167
282 | 0 | 0 | 159.2839 | 159.2839 | 50081.783 | 386.7843 | 109073.1771 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 32221.6084 | 2907.917 | 661552.3349 | 272135.6226 | 583222.7136 | 239914.0142 | 2045 | 23.5
283 | 0 | 0 | 159.2839 | 159.2839 | 50241.0669 | 386.7843 | 109459.9614 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 32127.902 | 2913.2835 | 662773.205 | 271844.9576 | 584443.5837 | 239717.0556 | 2045 | 23.5833
284 | 0 | 0 | 159.2839 | 159.2839 | 50400.3508 | 386.7843 | 109846.7457 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 32034.4682 | 2918.6499 | 663994.0751 | 271553.6816 | 585664.4537 | 239519.2135 | 2045 | 23.6667
285 | 0 | 0 | 159.2839 | 159.2839 | 50559.6347 | 386.7843 | 110233.53 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 31941.306 | 2924.0164 | 665214.9452 | 271261.8006 | 586885.3238 | 239320.4946 | 2045 | 23.75
286 | 0 | 0 | 159.2839 | 159.2839 | 50718.9186 | 386.7843 | 110620.3143 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 31848.4148 | 2929.3828 | 666435.8152 | 270969.3207 | 588106.1939 | 239120.9059 | 2045 | 23.8333
287 | 0 | 0 | 159.2839 | 159.2839 | 50878.2025 | 386.7843 | 111007.0987 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 31755.7937 | 2934.7493 | 667656.6853 | 270676.2477 | 589327.064 | 238920.4539 | 2045 | 23.9167
288 | 0 | 0 | 159.2839 | 159.2839 | 51037.4864 | 386.7843 | 111393.883 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 31663.442 | 2940.1157 | 668877.5554 | 270382.5876 | 590547.934 | 238719.1455 | 2045 | 24
289 | 0 | 0 | 159.2839 | 159.2839 | 51196.7703 | 386.7843 | 111780.6673 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 31571.3589 | 2945.4822 | 670098.4254 | 270088.3462 | 591768.8041 | 238516.9873 | 2046 | 24.0833
290 | 0 | 0 | 159.2839 | 159.2839 | 51356.0542 | 386.7843 | 112167.4516 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 31479.5436 | 2950.8486 | 671319.2955 | 269793.5296 | 592989.6742 | 238313.986 | 2046 | 24.1667
291 | 0 | 0 | 159.2839 | 159.2839 | 51515.3381 | 386.7843 | 112554.2359 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 31387.9952 | 2956.2151 | 672540.1656 | 269498.1434 | 594210.5443 | 238110.1481 | 2046 | 24.25
292 | 0 | 0 | 159.2839 | 159.2839 | 51674.622 | 386.7843 | 112941.0202 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 31296.7132 | 2961.5815 | 673761.0357 | 269202.1934 | 595431.4143 | 237905.4803 | 2046 | 24.3333
293 | 0 | 0 | 159.2839 | 159.2839 | 51833.9059 | 386.7843 | 113327.8046 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 31205.6965 | 2966.948 | 674981.9057 | 268905.6856 | 596652.2844 | 237699.989 | 2046 | 24.4167
294 | 0 | 0 | 159.2839 | 159.2839 | 51993.1898 | 386.7843 | 113714.5889 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 31114.9446 | 2972.3144 | 676202.7758 | 268608.6255 | 597873.1545 | 237493.6809 | 2046 | 24.5
295 | 0 | 0 | 159.2839 | 159.2839 | 52152.4736 | 386.7843 | 114101.3732 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 31024.4566 | 2977.6809 | 677423.6459 | 268311.019 | 599094.0245 | 237286.5624 | 2046 | 24.5833
296 | 0 | 0 | 159.2839 | 159.2839 | 52311.7575 | 386.7843 | 114488.1575 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 30934.2318 | 2983.0473 | 678644.5159 | 268012.8718 | 600314.8946 | 237078.64 | 2046 | 24.6667
297 | 0 | 0 | 159.2839 | 159.2839 | 52471.0414 | 386.7843 | 114874.9418 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 30844.2693 | 2988.4138 | 679865.386 | 267714.1893 | 601535.7647 | 236869.92 | 2046 | 24.75
298 | 0 | 0 | 159.2839 | 159.2839 | 52630.3253 | 386.7843 | 115261.7261 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 30754.5685 | 2993.7802 | 681086.2561 | 267414.9775 | 602756.6348 | 236660.409 | 2046 | 24.8333
299 | 0 | 0 | 159.2839 | 159.2839 | 52789.6092 | 386.7843 | 115648.5105 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 30665.1286 | 2999.1467 | 682307.1262 | 267115.2417 | 603977.5048 | 236450.1132 | 2046 | 24.9167
300 | 0 | 0 | 159.2839 | 159.2839 | 52948.8931 | 386.7843 | 116035.2948 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 30575.9487 | 3004.5131 | 683527.9962 | 266814.9876 | 605198.3749 | 236239.0389 | 2046 | 25
301 | 0 | 0 | 159.2839 | 159.2839 | 53108.177 | 386.7843 | 116422.0791 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 30487.0282 | 3009.8796 | 684748.8663 | 266514.2208 | 606419.245 | 236027.1926 | 2047 | 25.0833
302 | 0 | 0 | 159.2839 | 159.2839 | 53267.4609 | 386.7843 | 116808.8634 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 30398.3663 | 3015.2461 | 685969.7364 | 266212.9468 | 607640.115 | 235814.5805 | 2047 | 25.1667
303 | 0 | 0 | 159.2839 | 159.2839 | 53426.7448 | 386.7843 | 117195.6477 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 30309.9622 | 3020.6125 | 687190.6064 | 265911.171 | 608860.9851 | 235601.2088 | 2047 | 25.25
304 | 0 | 0 | 159.2839 | 159.2839 | 53586.0287 | 386.7843 | 117582.432 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 30221.8153 | 3025.979 | 688411.4765 | 265608.899 | 610081.8552 | 235387.0837 | 2047 | 25.3333
305 | 0 | 0 | 159.2839 | 159.2839 | 53745.3126 | 386.7843 | 117969.2163 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 30133.9247 | 3031.3454 | 689632.3466 | 265306.1361 | 611302.7253 | 235172.2115 | 2047 | 25.4167
306 | 0 | 0 | 159.2839 | 159.2839 | 53904.5965 | 386.7843 | 118356.0007 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 30046.2897 | 3036.7119 | 690853.2167 | 265002.8879 | 612523.5953 | 234956.5982 | 2047 | 25.5
307 | 0 | 0 | 159.2839 | 159.2839 | 54063.8804 | 386.7843 | 118742.785 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 29958.9095 | 3042.0783 | 692074.0867 | 264699.1595 | 613744.4654 | 234740.25 | 2047 | 25.5833
308 | 0 | 0 | 159.2839 | 159.2839 | 54223.1643 | 386.7843 | 119129.5693 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 29871.7835 | 3047.4448 | 693294.9568 | 264394.9566 | 614965.3355 | 234523.1731 | 2047 | 25.6667
309 | 0 | 0 | 159.2839 | 159.2839 | 54382.4482 | 386.7843 | 119516.3536 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 29784.9108 | 3052.8112 | 694515.8269 | 264090.2842 | 616186.2055 | 234305.3734 | 2047 | 25.75
310 | 0 | 0 | 159.2839 | 159.2839 | 54541.7321 | 386.7843 | 119903.1379 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 29698.2908 | 3058.1777 | 695736.6969 | 263785.1479 | 617407.0756 | 234086.8571 | 2047 | 25.8333
311 | 0 | 0 | 159.2839 | 159.2839 | 54701.016 | 386.7843 | 120289.9222 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 29611.9227 | 3063.5441 | 696957.567 | 263479.5527 | 618627.9457 | 233867.63 | 2047 | 25.9167
312 | 0 | 0 | 159.2839 | 159.2839 | 54860.2999 | 386.7843 | 120676.7066 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 29525.8058 | 3068.9106 | 698178.4371 | 263173.504 | 619848.8158 | 233647.6983 | 2047 | 26
313 | 0 | 0 | 159.2839 | 159.2839 | 55019.5838 | 386.7843 | 121063.4909 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 29439.9393 | 3074.277 | 699399.3072 | 262867.0071 | 621069.6858 | 233427.0678 | 2048 | 26.0833
314 | 0 | 0 | 159.2839 | 159.2839 | 55178.8677 | 386.7843 | 121450.2752 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 29354.3225 | 3079.6435 | 700620.1772 | 262560.067 | 622290.5559 | 233205.7445 | 2048 | 26.1667
315 | 0 | 0 | 159.2839 | 159.2839 | 55338.1516 | 386.7843 | 121837.0595 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 29268.9547 | 3085.0099 | 701841.0473 | 262252.689 | 623511.426 | 232983.7343 | 2048 | 26.25
316 | 0 | 0 | 159.2839 | 159.2839 | 55497.4355 | 386.7843 | 122223.8438 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 29183.8352 | 3090.3764 | 703061.9174 | 261944.8783 | 624732.296 | 232761.0431 | 2048 | 26.3333
317 | 0 | 0 | 159.2839 | 159.2839 | 55656.7194 | 386.7843 | 122610.6281 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 29098.9632 | 3095.7428 | 704282.7875 | 261636.6398 | 625953.1661 | 232537.6766 | 2048 | 26.4167
318 | 0 | 0 | 159.2839 | 159.2839 | 55816.0033 | 386.7843 | 122997.4125 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 29014.3381 | 3101.1093 | 705503.6575 | 261327.9788 | 627174.0362 | 232313.6407 | 2048 | 26.5
319 | 0 | 0 | 159.2839 | 159.2839 | 55975.2872 | 386.7843 | 123384.1968 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 28929.959 | 3106.4757 | 706724.5276 | 261018.9002 | 628394.9063 | 232088.9412 | 2048 | 26.5833
320 | 0 | 0 | 159.2839 | 159.2839 | 56134.5711 | 386.7843 | 123770.9811 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 28845.8254 | 3111.8422 | 707945.3977 | 260709.4092 | 629615.7763 | 231863.5839 | 2048 | 26.6667
321 | 0 | 0 | 159.2839 | 159.2839 | 56293.855 | 386.7843 | 124157.7654 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 28761.9364 | 3117.2086 | 709166.2677 | 260399.5107 | 630836.6464 | 231637.5744 | 2048 | 26.75
322 | 0 | 0 | 159.2839 | 159.2839 | 56453.1389 | 386.7843 | 124544.5497 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 28678.2914 | 3122.5751 | 710387.1378 | 260089.2098 | 632057.5165 | 231410.9184 | 2048 | 26.8333
323 | 0 | 0 | 159.2839 | 159.2839 | 56612.4228 | 386.7843 | 124931.334 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 28594.8896 | 3127.9415 | 711608.0079 | 259778.5113 | 633278.3865 | 231183.6217 | 2048 | 26.9167
324 | 0 | 0 | 159.2839 | 159.2839 | 56771.7067 | 386.7843 | 125318.1183 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 28511.7304 | 3133.308 | 712828.878 | 259467.4203 | 634499.2566 | 230955.6899 | 2048 | 27
325 | 0 | 0 | 159.2839 | 159.2839 | 56930.9906 | 386.7843 | 125704.9027 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 28428.813 | 3138.6744 | 714049.748 | 259155.9416 | 635720.1267 | 230727.1285 | 2049 | 27.0833
326 | 0 | 0 | 159.2839 | 159.2839 | 57090.2745 | 386.7843 | 126091.687 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 28346.1368 | 3144.0409 | 715270.6181 | 258844.0801 | 636940.9968 | 230497.9433 | 2049 | 27.1667
327 | 0 | 0 | 159.2839 | 159.2839 | 57249.5584 | 386.7843 | 126478.4713 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 28263.701 | 3149.4074 | 716491.4882 | 258531.8406 | 638161.8668 | 230268.1397 | 2049 | 27.25
328 | 0 | 0 | 159.2839 | 159.2839 | 57408.8423 | 386.7843 | 126865.2556 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 28181.5049 | 3154.7738 | 717712.3582 | 258219.2281 | 639382.7369 | 230037.7232 | 2049 | 27.3333
329 | 0 | 0 | 159.2839 | 159.2839 | 57568.1262 | 386.7843 | 127252.0399 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 28099.5479 | 3160.1403 | 718933.2283 | 257906.2474 | 640603.607 | 229806.6995 | 2049 | 27.4167
330 | 0 | 0 | 159.2839 | 159.2839 | 57727.4101 | 386.7843 | 127638.8242 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 28017.8292 | 3165.5067 | 720154.0984 | 257592.9031 | 641824.477 | 229575.0739 | 2049 | 27.5
331 | 0 | 0 | 159.2839 | 159.2839 | 57886.694 | 386.7843 | 128025.6086 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 27936.3482 | 3170.8732 | 721374.9685 | 257279.2001 | 643045.3471 | 229342.8519 | 2049 | 27.5833
332 | 0 | 0 | 159.2839 | 159.2839 | 58045.9779 | 386.7843 | 128412.3929 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 27855.1042 | 3176.2396 | 722595.8385 | 256965.1432 | 644266.2172 | 229110.039 | 2049 | 27.6667
333 | 0 | 0 | 159.2839 | 159.2839 | 58205.2618 | 386.7843 | 128799.1772 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 27774.0964 | 3181.6061 | 723816.7086 | 256650.7369 | 645487.0873 | 228876.6405 | 2049 | 27.75
334 | 0 | 0 | 159.2839 | 159.2839 | 58364.5457 | 386.7843 | 129185.9615 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 27693.3242 | 3186.9725 | 725037.5787 | 256335.9861 | 646707.9573 | 228642.6619 | 2049 | 27.8333
335 | 0 | 0 | 159.2839 | 159.2839 | 58523.8296 | 386.7843 | 129572.7458 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 27612.7869 | 3192.339 | 726258.4487 | 256020.8953 | 647928.8274 | 228408.1084 | 2049 | 27.9167
336 | 0 | 0 | 159.2839 | 159.2839 | 58683.1135 | 386.7843 | 129959.5301 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 27532.4838 | 3197.7054 | 727479.3188 | 255705.4693 | 649149.6975 | 228172.9854 | 2049 | 28
337 | 0 | 0 | 159.2839 | 159.2839 | 58842.3974 | 386.7843 | 130346.3145 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 27452.4143 | 3203.0719 | 728700.1889 | 255389.7125 | 650370.5675 | 227937.2982 | 2050 | 28.0833
338 | 0 | 0 | 159.2839 | 159.2839 | 59001.6813 | 386.7843 | 130733.0988 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 27372.5776 | 3208.4383 | 729921.059 | 255073.6297 | 651591.4376 | 227701.0521 | 2050 | 28.1667
339 | 0 | 0 | 159.2839 | 159.2839 | 59160.9652 | 386.7843 | 131119.8831 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 27292.9731 | 3213.8048 | 731141.929 | 254757.2254 | 652812.3077 | 227464.2523 | 2050 | 28.25
340 | 0 | 0 | 159.2839 | 159.2839 | 59320.2491 | 386.7843 | 131506.6674 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 27213.6001 | 3219.1712 | 732362.7991 | 254440.5041 | 654033.1778 | 227226.904 | 2050 | 28.3333
341 | 0 | 0 | 159.2839 | 159.2839 | 59479.533 | 386.7843 | 131893.4517 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 27134.4579 | 3224.5377 | 733583.6692 | 254123.4704 | 655254.0478 | 226989.0125 | 2050 | 28.4167
342 | 0 | 0 | 159.2839 | 159.2839 | 59638.8169 | 386.7843 | 132280.236 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 27055.5459 | 3229.9041 | 734804.5392 | 253806.1287 | 656474.9179 | 226750.5828 | 2050 | 28.5
343 | 0 | 0 | 159.2839 | 159.2839 | 59798.1008 | 386.7843 | 132667.0203 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 26976.8634 | 3235.2706 | 736025.4093 | 253488.4835 | 657695.788 | 226511.6201 | 2050 | 28.5833
344 | 0 | 0 | 159.2839 | 159.2839 | 59957.3847 | 386.7843 | 133053.8047 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 26898.4097 | 3240.637 | 737246.2794 | 253170.5393 | 658916.6581 | 226272.1296 | 2050 | 28.6667
345 | 0 | 0 | 159.2839 | 159.2839 | 60116.6686 | 386.7843 | 133440.589 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 26820.1842 | 3246.0035 | 738467.1495 | 252852.3005 | 660137.5281 | 226032.1163 | 2050 | 28.75
346 | 0 | 0 | 159.2839 | 159.2839 | 60275.9525 | 386.7843 | 133827.3733 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 26742.1861 | 3251.3699 | 739688.0195 | 252533.7715 | 661358.3982 | 225791.5853 | 2050 | 28.8333
347 | 0 | 0 | 159.2839 | 159.2839 | 60435.2364 | 386.7843 | 134214.1576 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 26664.4149 | 3256.7364 | 740908.8896 | 252214.9566 | 662579.2683 | 225550.5417 | 2050 | 28.9167
348 | 0 | 0 | 159.2839 | 159.2839 | 60594.5203 | 386.7843 | 134600.9419 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 26586.8699 | 3262.1028 | 742129.7597 | 251895.8603 | 663800.1383 | 225308.9904 | 2050 | 29
349 | 0 | 0 | 159.2839 | 159.2839 | 60753.8041 | 386.7843 | 134987.7262 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 26509.5504 | 3267.4693 | 743350.6297 | 251576.4868 | 665021.0084 | 225066.9365 | 2051 | 29.0833
350 | 0 | 0 | 159.2839 | 159.2839 | 60913.088 | 386.7843 | 135374.5106 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 26432.4557 | 3272.8357 | 744571.4998 | 251256.8406 | 666241.8785 | 224824.3849 | 2051 | 29.1667
351 | 0 | 0 | 159.2839 | 159.2839 | 61072.3719 | 386.7843 | 135761.2949 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 26355.5852 | 3278.2022 | 745792.3699 | 250936.9258 | 667462.7486 | 224581.3405 | 2051 | 29.25
352 | 0 | 0 | 159.2839 | 159.2839 | 61231.6558 | 386.7843 | 136148.0792 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 26278.9383 | 3283.5687 | 747013.24 | 250616.7467 | 668683.6186 | 224337.8083 | 2051 | 29.3333
353 | 0 | 0 | 159.2839 | 159.2839 | 61390.9397 | 386.7843 | 136534.8635 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 26202.5143 | 3288.9351 | 748234.11 | 250296.3076 | 669904.4887 | 224093.7932 | 2051 | 29.4167
354 | 0 | 0 | 159.2839 | 159.2839 | 61550.2236 | 386.7843 | 136921.6478 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 26126.3126 | 3294.3016 | 749454.9801 | 249975.6126 | 671125.3588 | 223849.3 | 2051 | 29.5
355 | 0 | 0 | 159.2839 | 159.2839 | 61709.5075 | 386.7843 | 137308.4321 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 26050.3325 | 3299.668 | 750675.8502 | 249654.6661 | 672346.2288 | 223604.3336 | 2051 | 29.5833
356 | 0 | 0 | 159.2839 | 159.2839 | 61868.7914 | 386.7843 | 137695.2165 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 25974.5733 | 3305.0345 | 751896.7202 | 249333.4721 | 673567.0989 | 223358.8989 | 2051 | 29.6667
357 | 0 | 0 | 159.2839 | 159.2839 | 62028.0753 | 386.7843 | 138082.0008 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 25899.0344 | 3310.4009 | 753117.5903 | 249012.0349 | 674787.969 | 223113.0005 | 2051 | 29.75
358 | 0 | 0 | 159.2839 | 159.2839 | 62187.3592 | 386.7843 | 138468.7851 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 25823.7153 | 3315.7674 | 754338.4604 | 248690.3585 | 676008.8391 | 222866.6432 | 2051 | 29.8333
359 | 0 | 0 | 159.2839 | 159.2839 | 62346.6431 | 386.7843 | 138855.5694 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 25748.6151 | 3321.1338 | 755559.3305 | 248368.4471 | 677229.7091 | 222619.8319 | 2051 | 29.9167
360 | 0 | 0 | 159.2839 | 159.2839 | 62505.927 | 386.7843 | 139242.3537 | 227.5004 | 55318.4722 | 106.1893 | 5.7111 | 23011.1491 | 78329.6213 | 25673.7334 | 3326.5003 | 756780.2005 | 248046.3047 | 678450.5792 | 222372.5713 | 2051 | 30

## Output
Water Loss Volumetric Performance Standard - Output
|  | Current leakage level (gallons per connection per day) | Current leakage level (gallons per mile per day) |  | Average annual leakage reduced with active leak detection and repair (acre-feet per year) | Water loss volumetric performance standard - 2028 (gallons per connection per day) | Water loss volumetric performance standard - 2028 (gallons per mile per day)
|  | 31.9273 | N/A |  | 2557.8809 | 23.5243 | N/A
| Years | Estimated real loss for distribution system |  |  | Benefit-Cost Ratio over 30 years
|  | (acre-feet per year) | (gallons per connection per day) | (gallons per mile per day) | 5.7812
| 2022 | 10171 | 31.9273 | N/A
| 2028 | 7494.0896 | 23.5243 | N/A | Benefit-Cost Ratio over 20 years
4.9695
Benefit-Cost Ratio over 10 years
3.757
Benefit-Cost Ratio (2022 to 2027)
2.8551
If there is no net benefit for additional interventions towards active leak detection and repair by the supplier, the volumetric standard remains the same as the current leakage level.
A Benefit-Cost Ratio less than 1 will be reported as N/A in cells G7, G10, G13, and G16.
The current leakage level and real loss standard can be provided in either gallons per connection per day or gallons per mile per day. N/A values can be ignored.

## Equations
Water loss Economic Model - Equations in the model
Term | Formula |  | References as applicable
Tab: Calculation
Annual background leakage (acre-feet per year)
Annual reported leakage (acre-feet per year) |  |  | Equation (7-5), AWWA M36 Manual, 2016
Annual unreported leakage (acre-feet per year) |  |  | Table 3-22, AWWA M36 Manual, 2016
Unreported leakage fraction for the system
Unreported leaks found per mile per year
Time taken to survey full distribution system (months)
Water loss due to backlog of leakage in unsurveyed parts in each month (acre-feet) |  |  | See row 32 for calculation
Water loss due to natural rise in leakage in never surveyed parts in each time step (acre-feet) |  |  | See row 32 for calculation
Water loss due to natural rise in leakage in previously surveyed parts in each time step (acre-feet) |  |  | See row 32 for calculation
Total water loss occuring in time step with intervention (acre-feet)
Water loss occuring without intervention in each time step (acre-feet) |  |  | See row 32 for calculation
Water saved due to water loss control in each time step (acre-feet) | Total water loss occuring in time step with intervention - Water loss occuring without intervention in each time step
Intitial leakage level for part surveyed during time step (acre-feet) |  |  | See row 32 for calculation
Leaks found per part per system |  | or default value
Incremental cost associated with leak repair in each time step ($)
Cost associated with leak repair in each time step ($)
Cost associated with leak detection and repair in each time step ($) | Cost associated with leak detection per month + Cost associated with leak repair per month
Marginal cost of water including rising cost and avoided cost of alternative supplies (at the beginning of 2022) ($ per acre-feet)
Marginal cost of water including rising cost and avoided cost of alternative supplies (for each incremental month after 2022 begins) ($ per acre-feet)
Value of water loss reduced in each time step ($)
Net benefit for each time step ($)
Net Present Value of net benefit corresponding to each time step ($)
Tab: Output
Benefit/Cost Ratio
Figure: Rise in leakage in parts of the system never surveyed before.
Figure: Rise in leakage in parts of the system that have been surveyed before.
(0.2×Total length of mains (miles)+0.008×Number of service connections)×((Average operational pressure)/70)^1.5
×Infrastructure Condition Factor
×(1000 gallons)/(325851 acrefeet)×(365 days)/year
(50 gallons )/(burst∙minute)×(1 acrefeet)/(325,851 gallons)×(0.2 leaks)/(mile∙year)×Total length of mains (miles)×(60 minutes)/hour×(24 hours)/day×(3 days)/year
Average baseline real loss−total background leakage−reported leakage
(Unreported leakage component)/((Background leakage component+Reported leakage component+Unreported leakage component))
(Average unreported leakage for supplier (acrefeet per year))/(Average total flow rate for unreported leaks (acrefeet per year)×Total length of mains (miles))
(Total length of mains (miles))/(Maximum average leak detection survey frequency (miles per month))
(Month taken to survey each system−month of implementation)×Unreported leakage per month×Time step
(Month taken to survey each system−month of implementation+1)×annual average rise in leakage per month
×(month of implementation−1/2)×(time step)^2
Before entire system is surveyed once:
Before entire system is surveyed once:
Rate of rise in leakage per month×〖time step〗^2×〖(month of implementation−1)^2/2 〗^
After entire system is surveyed once:
After entire system is surveyed once:
Rate of rise in leakage per month×〖time step〗^2×〖〖months taken to survey whole sy𝑠𝑡𝑒𝑚〗^2/2 〗^
Months taken to survey whole system×time step×(average baseline real loss per month+Rate of rise in leakage per month×(month of implementation− 1/2)×timestep)
Before entire system is surveyed once:
Before entire system is surveyed once:
(Unreported leakage for supplier)/(Months taken to survey whole system)
+𝑚𝑜𝑛𝑡ℎ 𝑜𝑓 𝑖𝑚𝑝𝑙𝑒𝑚𝑒𝑛𝑡𝑎𝑡𝑖𝑜𝑛×𝑡𝑖𝑚𝑒 𝑠𝑡𝑒𝑝×𝑅𝑎𝑡𝑒 𝑜𝑓 𝑟𝑖𝑠𝑒 𝑖𝑛 𝑙𝑒𝑎𝑘𝑎𝑔𝑒 𝑝𝑒𝑟 𝑚𝑜𝑛𝑡ℎ
After entire system is surveyed once:
After entire system is surveyed once:
Rate of rise in leakage per month×time step×Months taken to survey whole system
(Unreported leakage per month)/(Average flow rate for reported leaks per leak)
Leaks found per part of system×(Repair costs per mile)/(Efficiency of leak detection equipment)
(Cost of leak repair per mo𝑛𝑡ℎ)/(1+discount rate×time step)^((time step×month o𝑓 𝑖𝑚𝑝𝑙𝑒𝑚𝑒𝑛𝑡𝑎𝑡𝑖𝑜𝑛) )
Avoided cost of alternative supplies ∗ (1+Average annual rise in price of water×current incremental time step×24 months from 2020×time step)
*
Avoided cost of alternative supplies * (1+Average annual rise in price of water×(month of implementation−1)×time step)
Water saved due to water loss control in each time step×Marginal cost of water in each time step
Value of cost associated with leak detection and repair per month−Value of water loss reduced per month
(Total present value of value of water)/(Total present value of total cost of leak detection and repair)
The water loss occuring in any year is calculated by adding up the water loss occuring in each time step in that year.
Water loss due to backlog of leakage in unsurveyed parts in each time step
+ Water loss due to natural rise in leakage in never surveyed parts in each time step
+ Water loss due to natural rise in leakage in previously surveyed parts in each time step
The water loss occuring in any year is calculated by adding up the water loss occuring in each time step in that year.
Calculation of water lost at every time step with intervention
Variables used:
N = Number of parts into which the distribution system is divided (based on rate of surveying)
ΔT = time between surveys
Lo = Initial total unreported leakage
lo = Initial unreported leakage per part =
R = Natural rise in leakage for the entire system
r = Rate of natural rise of leakage per part =
The general method used is as follows:
It is assumed, for simplicity, that at any point in time, a part of the system is being surveyed. The rate of surveying is an average rate for the entire system.
The model determines the economically achievable volumetric water loss by calculating how much water loss occurs at that time. Thus, the 2027 standard is calculated by calculating the water loss occurring at the time step coinciding with the beginning of 2027.
The model divides the water lost during regular leak detection and surveying into three elements for ease of calculation:
  Water lost due to backlog of unreported leakage
  Water lost due to natural rise in leakage for the never surveyed parts of the system (for the first survey)
  Water lost due to natural rise in leakage for rest of the parts of the system not being surveyed in current time step
An equation is developed to represent water loss occurring in one part, after which the water loss is summed up to represent the entire system. ‘i’ represents the current time step, so that we can develop a general formula for each of these categories. The spreadsheet uses these formulae in columns 2 through 4 (B through D)
Water lost due to backlog of unreported leakage:
The schematic shows how the backlog unreported leakage for the entire system is impacted after each part of the system is surveyed. Note that the backlog element considered here does not include any rise in leakage, as elements including rising leakage are calculated separately.
Calculation of water lost at every time step with intervention
Variables used:
N = Number of parts into which the distribution system is divided (based on rate of surveying)
ΔT = time between surveys
Lo = Initial total unreported leakage
lo = Initial unreported leakage per part = Lo/N
R = Natural rise in leakage for the entire system
r = Rate of natural rise of leakage per part = R/N
The general method used is as follows:
It is assumed, for simplicity, that at any point in time, a part of the system is being surveyed. The rate of surveying is an average rate for the entire system.
The model determines the economically achievable volumetric water loss by calculating how much water loss occurs at that time. Thus, the 2027 standard is calculated by calculating the water loss occurring at the time step coinciding with the beginning of 2027.
The model divides the water lost during regular leak detection and surveying into three elements for ease of calculation:
  Water lost due to backlog of unreported leakage
  Water lost due to natural rise in leakage for the never surveyed parts of the system (for the first survey)
  Water lost due to natural rise in leakage for rest of the parts of the system not being surveyed in current time step
An equation is developed to represent water loss occurring in one part, after which the water loss is summed up to represent the entire system. ‘i’ represents the current time step, so that we can develop a general formula for each of these categories. The spreadsheet uses these formulae in columns 2 through 4 (B through D)
Water lost due to backlog of unreported leakage:
The schematic shows how the backlog unreported leakage for the entire system is impacted after each part of the system is surveyed. Note that the backlog element considered here does not include any rise in leakage, as elements including rising leakage are calculated separately.
Figure: Decrease in backlog unreported leakage as each part of the distribution system is surveyed
As parts of the system are surveyed serially, the overall backlog of unreported leakage drops by lo in each time step (the backlog unreported leakage per part).
At time step ‘i’, the survey would begin for the ith part of the system. Thus, the only leakage would be from the parts that have not been surveyed yet (N - i), and the one part to be surveyed by the end of the current time step.
As parts of the system are surveyed serially, the overall backlog of unreported leakage drops by lo in each time step (the backlog unreported leakage per part).
At time step ‘i’, the survey would begin for the ith part of the system. Thus, during each time step, leakage would occur be from the parts that have not been surveyed yet (N - i), and one additionally part to be surveyed by the end of the current time step.
Number of parts not surveyed yet = (N – i) + 1
Each part will leak at lo during the current time step ΔT as shown in the dashed part of the schematic. The water loss occurring in time step ‘i’ from all parts in the system due to only backlog leakage is represented as:
ΔT x lo x (N – i + 1)
Water loss in parts of the system never surveyed:
Leakage level for each part increases as the rate of rise of leakage, till that part is surveyed. Thus, all the parts which have not been surveyed before are at the same leakage level by a particular time step.
The rise in leakage to the beginning of the time step is represented by:
Rate of rise of leakage x time passed prior to current time step
If ‘j’ time steps have passed, time passed after ‘j’ time steps = j × ΔT
The leakage level only due to natural rise in leakage, at the beginning of the ‘j’th step, or at the end of the (j-1)th step is = r × (j-1) × ΔT
The leakage level at the end of the ‘j’th step is = r × j × ΔT.
The leakage volume lost during this time step is represented by the transition from the lower leakage level to the higher leakage level across time step ΔT, which is the area under the curve, which is a trapezoid, summed for all the parts of the system. Each part of the system will contribute to the overall leakage in this component as follows:
; ; …;
Simplifying the leakage volume lost during the ‘j’th step for a single part as follows:
If the distribution system is being surveyed for the first time, only ‘(j-1)’ parts have been surveyed when the ‘j’th step begins, and will contribute to this element of leakage:
The summation of an integer is represented by:
The summation of a constant is represented by:
Thus,
If the system has undergone a complete survey and this is the next round of surveying, ‘N’ parts have been surveyed before, and all will contribute to this element of leakage. After one survey, and the backlog of leakage is reduced, this element of leakage is the only one that constitutes the overall leakage for the distribution system:
The rise in leakage to the beginning of the time step is represented by:
Rate of rise of leakage x time passed prior to current time step
If ‘j’ time steps have passed, time passed after ‘j’ time steps = j × ΔT
The leakage level only due to natural rise in leakage, at the beginning of the ‘j’th step, or at the end of the (j-1)th step is = r × (j-1) × ΔT
The leakage level at the end of the ‘j’th step is = r × j × ΔT.
The leakage volume lost during this time step is represented by the transition from the lower leakage level to the higher leakage level across time step ΔT, which is the area under the curve, which is a trapezoid, summed for all the parts of the system. Each part of the system will contribute to the overall leakage in this component as follows:
𝑃𝑎𝑟𝑡 1:1/2×(𝟎+𝑟×𝟏×∆𝑇); 𝑃𝑎𝑟𝑡 2: 1/2×(𝑟×𝟏×∆𝑇+𝑟×𝟐×∆𝑇)×∆𝑇; 𝑃𝑎𝑟𝑡 3: 1/2×(𝑟×𝟐×∆𝑇+𝑟×𝟑×∆𝑇)…; 𝑃𝑎𝑟𝑡 𝑖: 1/2×(𝑟×(𝒋−𝟏)×∆𝑇+𝑟×𝒋×∆𝑇)
Simplifying the leakage volume lost during the ‘j’th step for a single part as follows:
=1/2×(𝑟×(𝒋−𝟏)×∆𝑇+𝑟×𝒋×∆𝑇) ×∆𝑇
=1/2×(𝑟×𝑗×∆𝑇−𝑟×∆𝑇+𝑟×𝑗×∆𝑇) ×∆𝑇
=1/2×(2×𝑟×𝑗×∆𝑇−𝑟×∆𝑇)×∆𝑇
=(𝑟×𝑗×∆𝑇−1/2×𝑟×∆𝑇)×∆𝑇
=𝑟×〖∆𝑇〗^2×(𝑗−1/2)
If the distribution system is being surveyed for the first time, only ‘(j-1)’ parts have been surveyed when the ‘j’th step begins, and will contribute to this element of leakage:
=𝑟×〖∆𝑇〗^2×∑1_(𝑗=1)^(𝑖−1)▒(𝑗−1/2)
The summation of an integer is represented by:
∑1_(𝑥=1)^𝑛▒〖𝑥= 〗 (𝑛×(𝑛+1))/2
The summation of a constant is represented by:
∑1_(𝑥=1)^𝑛▒〖𝑐= 〗 𝑛×𝑐
Thus,
=∑1_(𝑗=1)^(𝑖−1)▒〖1/2×𝑟×〖∆𝑇〗^2×(𝑗−1/2) 〗
= 1/2×𝑟×〖∆𝑇〗^2×(((𝒊−𝟏)×((𝒊−𝟏)+1))/2−((𝒊−𝟏))/2)
= 1/2×𝑟×〖∆𝑇〗^2×(((𝒊−𝟏)×(𝑖))/2−((𝒊−𝟏))/2)
= 1/2×𝑟×〖∆𝑇〗^2×((𝑖^2−2×𝑖+1)/2)
= 1/2×𝑟×〖∆𝑇〗^2×((𝑖−1)^2/2)
If the system has undergone a complete survey and this is the next round of surveying, ‘N’ parts have been surveyed before, and all will contribute to this element of leakage. After one survey, and the backlog of leakage is reduced, this element of leakage is the only one that constitutes the overall leakage for the distribution system:
=1/2×𝑟×〖∆𝑇〗^2×𝑁^2
Water loss occurring without intervention:
Without any intervention, the real loss for the system increases from the initial real loss (three-year average of real loss reported by supplier) increases with time at the natural rate of rise of leakage.
Without any intervention, it is assumed that suppliers would maintain the current or baseline real loss for the system (three-year average of real loss reported by supplier). Leakage without intervention for each part would be:
Without any intervention, it is assumed that suppliers would maintain the current or baseline real loss for the system (three-year average of real loss reported by supplier). Leakage without intervention for each part would be:
=𝑙_𝑜×∆𝑇
(Net benefit)/((1+Average annual rise in price of water×(month of implementation−1)×time step) )
+(7 gallons )/(burst∙minute)×(1 acrefeet)/(325,851 gallons)×(0.75 leaks)/(1000 service connections∙year)×(Total number of service connections)/1000×(60 minutes)/hour×(24 hours)/day×(8 days)/year
The leakage occurring in each time step is the area under the curve traced by the leakage level and time. The area under the leakage curve for each time step, marked by the dashed area in the schematic, is as follows:
During the first survey, while the ‘i’th part is being surveyed, (i-1) parts would have been surveyed. Hence, out of ‘N’ parts, (N - i +1) parts would remain to be surveyed and would have been leaking due to the naturally rising leakage.
The total leakage due to this component is:
After the entire system is surveyed once, this component becomes zero.
The leakage occurring in each time step is the area under the curve traced by the leakage level and time. The area under the leakage curve for each time step, marked by the dashed area in the schematic, is as follows:
1/2×(𝑟×(𝑖−1)×∆𝑇+𝑟×𝑖×∆𝑇)×∆𝑇=(𝑟×∆𝑇×(𝑖−0.5))×∆𝑇=𝑟×〖∆𝑇〗^2×(𝑖−0.5)
During the first survey, while the ‘i’th part is being surveyed, (i-1) parts would have been surveyed. Hence, out of ‘N’ parts, (N - i +1) parts would remain to be surveyed and would have been leaking due to the naturally rising leakage.
The total leakage due to this component is: (𝑁−𝑖+1)×(𝑟×〖∆𝑇〗^2×(𝑖−0.5))
After the entire system is surveyed once, this component becomes zero.
Water lost only due to natural rise in leakage in parts of the system surveyed previously:
Each part of the system starts leaking after a survey as the leakage rises naturally in the distribution system after being surveyed. The leakage occurring in each time step is the rise in leakage that occurs over that time step for all parts in the system. Since this component of leakage occurs in previously surveyed parts, all parts are surveyed at different times.
The following schematic shows how leakage occurs in different parts of the system that have been surveyed before, in a time step, due to this component.

## CollectedData_References
Water Loss Economic Model - References and Data
References for default inputs in model :
1. Water loss audit reports, 2020, Department of Water Resources: https://wuedata.water.ca.gov/, Accessed: July 2020
2. American Water Works Association, 2016, Water Audits and Loss Control Programs (M36 Manual), Fourth Edition
3. Water Research Foundation, 2015, Water Audits and Real Loss Component Analysis, Report 4372a
4. A.O. Lambert, 1999, International Report: Water losses management and techniques, Water Science and Technology: Water Supply Vol 2 No 4 pp 1–20
5. European Union, 2015, EU Reference document Good Practices on Leakage Management: Main Report
6. American Water Works Association Water Loss Control Committee, 2003, Committee Report: Applying worldwide BMPs in water loss control, Volume 95, Issue 8, Pages 65-79
7. California Rural Water Association, 2015, Water System Leak Identification and Control Field Evaluation, Emerging Technologies Report:ET13PGE1451, Pacific Gas and Electric Company
8. Pacific Institute, 2016, The Cost of Alternative Water Supply and Efficiency Options in California
9. Natural Resources Defense Council, 2016, Issue Brief: Proceed with Caution II: California's Droughts and Desalination in Context
Value of Water
Rise in price of water, based on historical rates for Tier 1 Treated Water rates for water sold by the Metropolitan Water District
Consumer price index for 2019 |  | 270.35
Prices are converted to one year (2019) to obtain real prices and then compared. (Consumer Price Index: West Region (All prices): Bureau of Labor Statistics, https://www.bls.gov/cpi/data.htm
Year | Price (Tier 1, treated) | Consumer price indices (all prices) | Real price as 2019$ | Percent increase | Source: Metropolitan Water district, Historical Water rates
2008 | 508 | 219.646 | 625.2688
2009 | 579 | 218.822 | 715.3424 | 14.41%
2010 | 701 | 221.203 | 856.7486 | 19.77%
2011 | 744 | 227.485 | 884.1919 | 3.203%
2012 | 794 | 232.376 | 923.7525 | 4.474%
2013 | 847 | 235.824 | 971.0057 | 5.115%
2014 | 890 | 240.215 | 1001.6506 | 3.156%
2015 | 923 | 243.015 | 1026.8216 | 2.513%
2016 | 942 | 247.705 | 1028.1169 | 0.1261%
2017 | 979 | 254.738 | 1038.9995 | 1.058%
2018 | 1015 | 263.263 | 1042.3236 | 0.3199%
2019 | 1050 | 270.35 | 1050 | 0.7365%
2020 | 1078 | 275.057 | 1059.5524 | 0.9098%
Average annual price increase (2008-2018): |  | 4.649%
Avoided Cost of Water
Alternative water supplies |  | Cost (2015 dollars) | Costs (2019 dollars) | Cost (2020 dollars) | Consumer price index for 2015 | Consumer price index for 2019 | Consumer price index for 2020
Stormwater |  | 590 | 656.3648 | 667.7926 | 243.015 | 270.35 | 275.057
Indirect potable reuse |  | 1800 | 2002.469 | 2037.3335
Brackish water desalination |  | 1100 | 1223.731 | 1245.0371
Imported water (Metropolitan Water District,2019): $ 1015 per acre-feet |  | 1015 | 1129.17 | 1148.8297
| Average avoided cost ($): | 1274.7483
Lambert (2009) Table 1: Reported and Unreported Leakage
Collected Data
Typical number of miles surveyed per day
Services provided by Municipal Water District of Orange County: 10 miles a week ~ 2 miles a day ~ 40 miles per month
Services provided by M.E. Simpson: 5 miles a day ~ 100 miles per month
Irvine Ranch Water District: 3.5 miles per day ~ 70 miles per month
Services used by Water Systems Optimization in Nashville, TN: 6 miles per day ~ 120 miles per month
East Bay Municipal Utility District: 74 miles of manual surveying; 61 miles of automated acoustic surveying; 1236 miles of satellite surveying throughout the year ~ 114.25 miles per month
The following surveying schedule has been planned for member agencies of the Municipal Water District of Orange county
Agency | Total length of mains (Miles) | Target Miles (Annual) | % of system planned to be surveyed annually
Seal Beach | 75 | 75 | 100%
TCWD | 66 | 66.5 | 100.8%
La Habra | 165 | 83 | 50.3%
Tustin | 172 | 102 | 59.3%
EOCWD | 23.7 | 48 | 202.5%
Huntington Beach | 607.2 | 18 | 2.964%
Mesa | 328.4 | 32 | 9.744%
Orange | 462 | 30 | 6.494%
San Clemente | 212.6 | 30 | 14.11%
YLWD | 367.1 | 110 | 29.96%
Systems above 6000 miles of distribution pipeline:
Los Angeles Department of Water and Power is the only system with distribution system pipeline greater than 6000 miles. As per conversations, LADWP is currently planning its active leak detection program. To address the size of the system, and estimate a reasonable leak detection survey rate, staff compared its total operating cost with that of East Bay Municipal Utility District. LADWP has an operating budget of $1,194,818,812 per year, and EBMUD has an operating budget of $345,821,000 per year, and surveys 114 miles per month. LADWP has about 3.5 the operating budget of EBMUD, hence staff estimated a leak detection survey rate of about 15 additional miles per month, rounded up to 130 miles per month.
Leak detection costs - Summary (Scroll down for cost estimates)
Equipment type | Lifecycle | Efficiency range | Average efficiency
Leak Survey | 4 - 7 years | 98 - 99%a | 98.5
Leak Pinpoint | 9 - 10 years | 50 - 92%b | 71
|  |  | 69.93% | Product of efficiencies for surveying and pinpointing
a. Highly trained and experienced staff.
b. Expected Efficiency of a new program (variable).
c/d. Costs are total costs per mile, including labor and equipment cost. Variances in costs are also due to size of survey, type of pipe material and logistical issues withing the water system.
Unit cost per mile (survey and pinpointing)
$177 - $595
Provided by Kunkel Water Efficiency Consulting
Leak detection cost estimates (including surveying and pinpointing)
Location of contractor | Type of piping | Unit cost per mile
Cleveland, Ohio | Metallic | 177
National | Metallic | $185 (local) - $275 (non-local)
| Plastic | $395 (local) - $495 (non-local)
Regional (small water utilities) | Metallic | 300
| Plastic | 400
Provided by Water Systems Optimization
Unit cost per mile | Additional details
$250 - $400 | Includes surveying and pinpointing
Provided by M.E. Simpson
Pipe material | Unit cost per mile
Metallic | 295
Plastic | 595
Life cycle
Listening devices | 7 years
Correlators | 9 - 10 years
Provided by the Municipal Water District of Orange County per their Shared Services Agreement (Fiscal Year 2019-20)
Unit cost | Additional detail
$278 per mile (Under 50 miles) $350 per mile (50 - 100 miles) $300 per mile (Over 100 miles) | Deliverables include: Distribution System Leak Detection Plan and Weekly progress reporting and leak verification (All indications of leaks found during initial survey will be verified a second time, after which the leak will be pinpointed with a computer-based leak sound correlator whenever possible.)
$347 per leak | Includes: Suspected leak consultation, Field leak investigation, Written report and pinpointed leak location
Average cost per mile including correlation | 353.5255 | Calculated based on 0.75 leaks per 1000 service connections and 0.01 main leaks per mile. The median number of connections per mile of main was 74.
From the Los Angeles Water Action Plan (2015)
Total capital costs | 3000
(equipment, one-time)
Present value of annuity factor | 8.3166
Annualized cost over lifecycle | 360.7241
Total Operations and Maintenance (per year) | 183000
Miles to be surveyed | 720
Unit cost per mile ($) | 254.6677
Other cost estimates from vendors
Vendor - Subsurface
Type | Equipment | Part # | Items Incld. | Unit Cost | Upfront Cost
Acoustic Leak Detection | Listening Rod + Ground Microphones | LD-12a | 1 | 3695 | Included in unit cost
|  | w/ optional 6ft sensor cable |  | 35
|  | LD-15b | 1 | 3750
|  | 40 in. extension rod |  | 75
|  | 60 in. extension rod |  | 95
|  | Sensor w/ steel base & adapter |  | 30
|  | LD-18b | 1 | 5995
|  | Sensor w/ magnet & 9.8 ft cable |  | 750
|  | 40 in. extension rod |  | 105
|  | 60 in. extension rod |  | 125
Correlator | Leak Noise Correlators | ZCorr3c | 3 | 8495
|  | ZCorr8d | 8 | 15995
|  | LC-5000 | 4 | 32000
a. LD-12 Series includes apmlifier, meter display unit, ground microphone, headphones, 10mm nutfriver, aluminum sensor base and 39" contact rod.
b. LD-15/18 Series includes apmlifier w/meter display unit, 9.75 ft long cable, base plate, and headphones.
c. ZCorr3 includes 3 digital correlating loggers, 1 docking station (supports up to 8 loggers) and basic software.
d. ZCorr8 includes 8 digital correlating loggers, 1 docking station (supports up to 8 loggers) and PRO software.
e. LC-5000 includes 4 wireless/GPS correlator (real time and programmable), 5 charging cables and headphones.
* Pricing does not include applicable taxes or shipping costs.
http://www.subsurfaceleak.com/waterleakdetec.html
Vendor - Sewerin
Type | Equipment | Part # | Items Incld. | Unit Cost
Acoustic & Special Leak dectetion | Stethophon 04 Kita | EA15-10002B | Single Unit | 1415
|  | EA15-10002S |  | 1885
|  | EA15-10002C |  | 1969
| Stethophon 04 SDR Kita | EA15-10102B |  | 1766
|  | EA15-10102S |  | 2236
|  | EA15-10102C |  | 2320
| Aqua Test T-10 Kitb | EA16-10002B |  | 2352
|  | EA16-10002C |  | 2634
|  | EA16-10002P |  | 3049
| Aqua Test T-10 SDR Kitb | EA16-10102B |  | 2885
|  | EA16-10102C |  | 3167
|  | EA16-10102P |  | 3581
| Aquaphon A50 Kit "Entry Level Pro." | EA50-10002BP |  | 3225
|  | EA50-10002C |  | 3969
|  | EA50-10002P |  | 4996
| Aquaphon A50 SDR Kit | EA50-10011B |  | 3708
|  | EA50-10011C |  | 4478
|  | EA50-10011P |  | 5506
| Aquaphon A100 Pro Kit "Stnd Pro kit" | EA14-10222B |  | 5552
|  | EA14-10222P |  | 7082
|  | EA14-10222C |  | 8250
| Aquaphon A200 Pro Kit "Pro. Kit" | EA20-10022B |  | 5952
|  | EA20-10022PB |  | 7908
|  | EA20-10022P |  | 9085
|  | EA20-10022C |  | 10132
| Combiphon Striker Kitc | SA01-10002K |  | 4207
| Combiphon Stopper Kit | SA01-10002S |  | 4930
| Combiphon Complete Kit | SA01-10002C |  | 6459
| Variotec VT 460 Tracergas Kit | VT10-10502B |  | 7659
Logger/Correlator | SeCorr C200 Kit | KR20-10202B | 2 | 10495
| SeCorrPhon AC200 Kit | KR08-22202B | 2 | 14866
|  | KR20-20202P | 2 | 16249
| SeCorr 300 Digital Correlator Pro Kit | KR30-S0004P | 2 | 20214
| SePem 01 Starter Kit | SF01-10002S | 10 | 9455
|  | SePem 155 Logger | 1 | 685
Vendor - FCS
Type | Equipment | Part # | Items Incld. | Unit Cost | Upfront Cost
Acoustic Leak Detection | DXMic System | DXMICSYS | 1 | 4950 | Included in unit cost
| DXMic Pro System | DXPROSYS | 1 | 5380
| Bmic System | BMICSYS | 1 | 4950
| TMic - FCS Portable Electronic Listening Stick | TMICFCS | 1 | 995
| L-Mic System | LMICSYS | 1 | 1950
| L-Mic System Deluxe | LMICSYSDEL | 1 | 3950
Correlator / Logger | S-30 System | S30SYS | 1 | 4500
| TriCorr Touch Pro | TCTOUCH |  | 25000
| Hydrophone Kit | HYDKITMCTUSA | 1 | 9144
| Additional Correlating Pods | RDL 5014L/4 | 1 | 1700
| 3 Pod with 8 Pod Case | - | 3 | 11885
| 4 Pod with 8 Pod Case | - | 4 | 13202
| 6 Pod with 8 Pod Case | - | 6 | 15428
| 8 Pod with 8 Pod Case | - | 8 | 17950
Permalog+
| 1-25 Permalogs | PR4US | 1 | 700
| 26-50 Permalogs | PR4US | 1 | 650
| 51-100 Permalogs | PR4US | 1 | 600
| 101-200 Permalogs | PR4US | 1 | 550
| 201-300 Permalogs | PR4US | 1 | 500
| 301-500 Permalogs | PR4US | 1 | 450
| 501-750 Permalogs | PR4US | 1 | 400
| 751 + Permalogs | PR4US | 1 | 350
Pcorr+
| 1-25 Pcorr+ | PR5US | 1 | 800
| 26-50 Pcorr+ | PR5US | 1 | 750
| 51-100 Pcorr+ | PR5US | 1 | 700
| 101-200 Pcorr+ | PR5US | 1 | 650
| 201-300 Pcorr+ | PR5US | 1 | 600
| 301-500 Pcorr+ | PR5US | 1 | 550
| 501-750 Pcorr+ | PR5US | 1 | 500
| 751 + Pcorr+ | PR5US | 1 | 450
* Pricing does not include applicable taxes or shipping costs.
http://www.subsurfaceleak.com/waterleakdetec.html
Vendor - SEBA
Type | Equipment | Part # | Items Incld. | Unit Cost | Upfront Cost
Acoustic Leak Detection | HL-7000 Electro-Acoustic Leak Detector | seba-HL7000-US-PRO | 1 | 5595 | Included in unit cost
| HL50 Bluetooth Municipal Digital Leak Locator | SEBA-HL50BT-kit | 1 | 2150
| Listining Rod add on | PAM T-3-1 | 1
Correlator/Logger | N3-C10: 1 Commander 3a | SEBA-WP12389 | 1 | 14500
| N3-M logger add on | SEBA-WP12391 | 31 | 21700
| Correlux C-3 Seba Pro Correlatorb | SEBA-WP12399 | 1 | 22000
a. Includes 10 Loggers
b. Includes 3 Correlators
* Pricing does not include applicable taxes or freight.
Vendor - Gutermann
Type | Labor | External Vendor | DI | PVC | AC | Median | Average
Acoustic Leak Detection | 50 < miles $278 / mi 50 > 100 mile $350 / mi 100 > miles $300 / mi | $295 / mile for metal pipes $595 / mile for non-metallic pipe | 93.7% | 82.3% | 66.6% | 82.3% | 80.87%
Correlator / Logger
Repair costs
From Irvine Ranch Water district
Repair costs for leaks found in area surveyed ($) | Average Cost/Foot | Leak Repair Rangea |  | Reported Water Saved | 2" & 3" PVC | 4" PVC | 6" PVC | 6" ACP | 8" C-900 / ACP | 8" DIP | 10" ACP | 12" CML/ACP | 16" CML&C
234000 | 207 | $3500 - $30000 |  | 263 AF | $3000 - 5,000 | $3000 - 6,000 | $4000 - 6,000 | $3000 - 12,000 | $3000 - 9,000 | 6000 | $4000 - 6,000 | $6000 - 15,000 | $4000 - 31,650 | 2018
[5 empty] | $2000 - 6,000 | $4000 - 9,000 | $4000 - 9,000 | $4000 - 5,000 | $4000 - 6,000 | 12000 | 7000 | 15000 | $6000 - 12,000 | 2017
Average
[5 empty] | Averages: | 4000 | 5500 | 5750 | 6000 | 5500 | 9000 | 5666.6667 | 12000 | 13412.5 | 7425.463
From Pacific Gas and Electric's Report ET13PGE1451: Water System Leak Identification and Control Field Evaluation (2015) | [8 empty] | Irvine ranch Water District (Transposed)
Repairs costs for the leaks detected: | [7 empty] | 2" & 3" PVC |  | $3000 - 5,000 |  | $2000 - 6,000 |  | Averages:
Tehama County Water system | Kings County Water System | Alpine County Water System | Madera County System |  | PG&E |  |  | 4" PVC |  | $3000 - 6,000 |  | $4000 - 9,000 |  | 4000
2745 | 2500 | 2500 | 1500 |  | Average cost: | 4466.25 |  | 6" PVC |  | $4000 - 6,000 |  | $4000 - 9,000 |  | 5500
|  | 6000 | 1500 |  |  |  |  | 6" ACP |  | $3000 - 12,000 |  | $4000 - 5,000 |  | 5750
|  | 7900 | [5 empty] | 8" C-900 / ACP |  | $3000 - 9,000 |  | $4000 - 6,000 |  | 6000
|  | 4100 | [5 empty] | 8" DIP |  | 6000 |  | 12000 |  | 5500
|  | 8600 | [5 empty] | 10" ACP |  | $4000 - 6,000 |  | 7000 |  | 9000
|  | 7500 | [5 empty] | 12" CML/ACP |  | $6000 - 15,000 |  | 15000 |  | 5666.6667
|  | 6800 | [5 empty] | 16" CML&C |  | $4000 - 31,650 |  | $6000 - 12,000 |  | 12000
|  | 1950 | [7 empty] | 2018 |  | 2017 |  | 13412.5
Based on these data sets, the average repair cost is estimated to be: |  |  | 5945.8565
Repair costs for laterals and service line leaks
Provided by Kunkel Water Efficiency Consulting based on the Philadelphia Water Department leak detection program
Type of leak | Unit repair cost per leak
Service leaks | 108
Abandoned services | 1100
Hydrant leaks | 215
Valve leaks | 215
Average unit cost: | 409.5
(assuming equal probability for all types of leaks)
Provided by Water Systems Optimization Inc.
Typical costs per leak: | $3500 - $5000
Average cost per leak | 4250
(assuming equal probability for all types of leaks)
Average cost per leak using these estimates:
2329.75