## Background Information
Drought Infrastructure Cost Assessment
The State Water Board has conducted a targeted Drought Cost Assessment. The Drought Cost Assessment estimates the costs associated with drought infrastructure requirements for small community water systems (15 – 2,999 service connections) in accordance with Senate Bill 552’s addition of section 10609.62 to the California Water Code.
SB 552 Requirements
- No later than January 1, 2023, implement monitoring systems sufficient to detect production well groundwater levels.
- Beginning no later than January 1, 2023, maintain membership in the California Water/Wastewater Agency Response Network (CalWARN) or similar mutual aid organization.
- No later than January 1, 2024, to ensure continuous operations during power failures, provide adequate backup electrical supply.
- No later than January 1, 2027, have at least one backup source of water supply, or a water system intertie, that meets current water quality requirements and is sufficient to meet average daily demand.
- No later than January 1, 2032, meter each service connection and monitor for water loss due to leakages.
- No later than January 1, 2032, have source system capacity, treatment system capacity if necessary, and distribution system capacity to meet fire flow requirements (excluded from the Cost Assessment).
Cost Assessment Assumptions per Requirement:
- Static Well Level Monitoring: A system is not meeting this requirement if their response to the 2020 EAR question regarding this requirement is any of (No, Null, Blank, NA)
~Sounder Cost ($1700)
~ No well modifications are assumed to be needed.
~Total Cost = Sounder Cost + Regional Multiplier + 4.7% Total Cost Inflation
- Backup Electrical Supply: A system is not meeting this requirement if their response to the 2020 EAR question regarding this requirement is any of (None, Some, Blank ,Null)
~Cost is based on Maximum Day Demand (MDD)= Average Day Demand (150 gpd)* population served * Peak factor (2.25).
~Account for 5% permitting multiplier.
~Total Cost Estimate ($) = $30,134 + ($341 x MDD) + Regional Multiplier + 5% Total Cost Permitting + 4.7% Total Cost Inflation.
- Backup Source: New Well or Intertie: A system is not meeting their requirement if they only have a single source and no backup source.
New Well: Systems are costed out a new well if their only source is a well and an intertie is not feasible.
~Well drilling 1,000 ft depth at $1,200,000
~Well production= (MDD)= ADD (150 gpd)* population served * Peak factor (2.25)
~CEQA $85,000
~ SCADA $100,000
~ Apply 25% of total cost estimate for planning costs
~Well development Cost = ($145.01 x Well Production (MDD)) + $32,268
~Well Pump and Motor Cost = ($136.73 x Well Production (MDD)) + $116,448
~ Total Cost ($) = Well drilling + CEQA+SCADA + Well Development+ Well Pump and Motor + 25% Total Cost Planning and Construction + Regional Multiplier + 4.7% Total Cost Inflation
Intertie: Systems are costed out an intertie if they don't already have one, and locationally intersecting a larger system.
~ Buffer for intersects (added pipeline) = 1,000 ft
~Pipeline Cost per ft = $155
~Service line (system connection) =$5,000
~Connection fee ($/connection) = $6,600
~Admin/Legal $200,000
~Apply a 20% contingency = 20% of total cost estimate
~Apply 25% of total cost estimate for planning costs
~Total Cost Estimate = Pipeline cost + Service line cost + Connection fees + Admin/legal fees + 20% Total Cost Contingency + 25% Total Cost Planning + Regional Multiplier + 4.7% Total Cost inflation
- Meter All Service Connections: A system is not meeting this requirement if the count of unmetered service connection > 0
~ Meter Cost $1200
~ Equipment and Software Cost $29,000
~Total Cost = Meter Cost + Software + Regional Multiplier + 4.7% Total Cost Inflation

## Cost Per County
County | Total Point Estimate | Max Range | Min Range
Monterey | 195725981.4391 | 391451962.8782 | 97862990.7196
Sonoma | 168526054.0703 | 337052108.1406 | 84263027.0352
San Joaquin | 132780552.0484 | 265561104.0968 | 66390276.0242
Los Angeles | 126744825.875 | 253489651.75 | 63372412.9375
Kern | 125790377.4948 | 251580754.9896 | 62895188.7474
Tulare | 116400526.4288 | 232801052.8577 | 58200263.2144
Fresno | 116317425.9946 | 232634851.9891 | 58158712.9973
Tehama | 87227155.295 | 174454310.59 | 43613577.6475
Sacramento | 77343121.2396 | 154686242.4791 | 38671560.6198
Riverside | 76972199.1989 | 153944398.3977 | 38486099.5994
Madera | 73993021.6369 | 147986043.2738 | 36996510.8185
Stanislaus | 69414995.7909 | 138829991.5819 | 34707497.8955
Nevada | 62461542.599 | 124923085.1979 | 31230771.2995
Contra Costa | 62374446.8714 | 124748893.7428 | 31187223.4357
Butte | 62181483.4426 | 124362966.8851 | 31090741.7213
San Bernardino | 57205281.9401 | 114410563.8801 | 28602640.97
Santa Clara | 55600576.8501 | 111201153.7003 | 27800288.4251
Santa Cruz | 48379019.42 | 96758038.84 | 24189509.71
Santa Barbara | 46761054.2176 | 93522108.4353 | 23380527.1088
San Benito | 43355998.4529 | 86711996.9057 | 21677999.2264
Mendocino | 41682667.7251 | 83365335.4502 | 20841333.8626
San Diego | 40409788.7894 | 80819577.5788 | 20204894.3947
San Luis Obispo | 35632683.9664 | 71265367.9327 | 17816341.9832
Ventura | 34070143.3219 | 68140286.6438 | 17035071.6609
Yuba | 33530755.5596 | 67061511.1191 | 16765377.7798
Tuolumne | 32847172.0241 | 65694344.0483 | 16423586.0121
Merced | 32292416.4167 | 64584832.8335 | 16146208.2084
Lake | 29240607.0976 | 58481214.1953 | 14620303.5488
Inyo | 27904360.4868 | 55808720.9736 | 13952180.2434
Plumas | 23146634.6039 | 46293269.2078 | 11573317.302
Siskiyou | 20718851.5895 | 41437703.179 | 10359425.7948
Sutter | 20199546.5511 | 40399093.1021 | 10099773.2755
Kings | 15747148.689 | 31494297.378 | 7873574.3445
Napa | 15682968.2169 | 31365936.4338 | 7841484.1084
Yolo | 14743911.187 | 29487822.374 | 7371955.5935
Mono | 10716374.7832 | 21432749.5665 | 5358187.3916
Imperial | 10537664.9161 | 21075329.8322 | 5268832.4581
Marin | 6684675.0172 | 13369350.0344 | 3342337.5086
San Mateo | 5978995.7905 | 11957991.581 | 2989497.8953
Calaveras | 3843227.5371 | 7686455.0742 | 1921613.7686
Colusa | 3409745.0536 | 6819490.1072 | 1704872.5268

## Summary
PWSID | WATER SYSTEM NAME - FROM SDWIS | POPULATION | TOTAL SERVICE CONNECTIONS | Regulating Agency | State Type | Service Area | Meet SB 552 "Detect Well Groundwater Levels" Requirement (Yes/No/N/A) | Sounder Cost ($) | Meet SB 552 "Continuous Operation During Power Failures" Requirement (Yes/No/N/A) | Generator Cost ($) | Meet SB 552 "Back up source" Requirement (Yes/No/N/A) | Well Cost ($) | Intertie Cost ($) | Meet SB 552 "Meter All Service Connections" (Yes/No/N/A) | Meter Cost ($) | Total Point Estimate ($) | Min Value ($) | Max Value ($) | SAFER Status | DAC Status
CA1910108 | CITY OF BELL GARDENS | 11292 | 1652 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | SDAC
CA1710008 | NICE MUTUAL WATER COMPANY | 2731 | 1069 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA0400051 | DINGERVILLE USA PARK | 447 | 80 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 130875 | 132654.9 | 66327.45 | 265309.8 | Not At-Risk | SDAC
CA1910012 | BELLFLOWER HOME GARDEN WATER COMPANY | 1129 | 342 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | N/A | 0 | No | 172651.4954 | N/A | 0 | 0 | No | 595659.24 | 768310.7354 | 384155.3677 | 1536621.4708 | Not At-Risk | DAC
CA1502315 | CAMP OWEN WATER SYSTEM | 225 | 23 | DISTRICT 19 - TEHACHAPI | C | NT - INSTITUTION | Yes | 0 | No | 52896.7884 | Yes | 0 | 0 | No | 59260.2 | 112156.9884 | 56078.4942 | 224313.9768 | Not At-Risk | Non-DAC
CA1500447 | SIERRA BREEZE MUTUAL WATER COMPANY | 150 | 60 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 46307.1299 | Yes | 0 | 0 | No | 105747 | 153834.0299 | 76917.0149 | 307668.0598 | Potentially At-Risk | Missing
CA1500333 | CWS - FREMONT VALLEY | 116 | 80 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA3200114 | EVERGREEN MOTEL & MHP | 28 | 40 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2009670.5874 | 0 | No | 80619 | 2090289.5874 | 1045144.7937 | 4180579.1748 | Potentially At-Risk | DAC
CA2810012 | PACIFIC UNION COLLEGE | 2360 | 313 | DISTRICT 03 - MENDOCINO | C | NT - SCHOOL | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 362869.26 | 362869.26 | 181434.63 | 725738.52 | Not At-Risk | Non-DAC
CA5510503 | YOSEMITE NPS-HODGDON MEADOW | 51 | 51 | DISTRICT 11 - MERCED | C | T - RECREATION AREA | No | 1779.9 | Yes | 0 | No | 2011658.2576 | 0 | Yes | 0 | 2013438.1576 | 1006719.0788 | 4026876.3152 | Not At-Risk | Missing
CA1310013 | SEELEY CWD | 2010 | 377 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA4510003 | BURNEY WATER DISTRICT | 3154 | 1413 | DISTRICT 02 - LASSEN | C | O - OTHER AREA | Yes | 0 | No | 310244.9182 | Yes | 0 | 0 | Yes | 0 | 310244.9182 | 155122.4591 | 620489.8364 | Not At-Risk | SDAC
CA5510005 | TWAIN HARTE COMMUNITY SERVICES DISTRICT | 2226 | 1582 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 228708.8771 | Yes | 0 | 0 | Yes | 0 | 228708.8771 | 114354.4385 | 457417.7541 | Not At-Risk | DAC
CA3110023 | NORTH TAHOE PUD - CARNELIAN WOODS | 524 | 269 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 0 | 3370900.26 | Yes | 0 | 3370900.26 | 1685450.13 | 6741800.52 | Not At-Risk | Non-DAC
CA4100533 | SKYLONDA MUTUAL | 420 | 154 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 91372.3463 | Yes | 0 | 0 | Yes | 0 | 93721.8143 | 46860.9072 | 187443.6287 | Not At-Risk | Non-DAC
CA5610022 | VENTURA RIVER WATER DISTRICT | 5700 | 2166 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1009051 | CANTUA CREEK VINEYARDS, IV, LLC. | 50 | 16 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | No | 37520.9186 | No | 2011571.8372 | 0 | No | 50465.4 | 2101338.0557 | 1050669.0279 | 4202676.1115 | HR2W | SDAC
CA1910022 | CALIF STATE POLYTECHNICAL UNIV - POMONA | 35586 | 148 | DISTRICT 22 - ANGELES | C | NT - SCHOOL | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 190997.928 | 190997.928 | 95498.964 | 381995.856 | Not At-Risk | Non-DAC
CA1000039 | FCSA #10/CUMORAH KNOLLS | 132 | 47 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 44725.6119 | Yes | 0 | 0 | Yes | 0 | 44725.6119 | 22362.8059 | 89451.2237 | Not At-Risk | Non-DAC
CA2400053 | EL NIDO MOBILE HOME PARK | 137 | 50 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK | Yes | 0 | No | 45164.9224 | Yes | 0 | 0 | No | 93183 | 138347.9224 | 69173.9612 | 276695.8448 | Potentially At-Risk | DAC
CA2010013 | CAL AM - COARSEGOLD | 83 | 25 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 40420.3683 | Yes | 0 | 0 | Yes | 0 | 40420.3683 | 20210.1842 | 80840.7366 | Not At-Risk | DAC
CA2300502 | ALBION MUTUAL WATER COMPANY | 40 | 27 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36642.2974 | Yes | 0 | 0 | Yes | 0 | 38422.1974 | 19211.0987 | 76844.3949 | Not At-Risk | SDAC
CA5200504 | CITY OF TEHAMA | 445 | 195 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 72226.4533 | Yes | 0 | 0 | Yes | 0 | 74006.3533 | 37003.1767 | 148012.7066 | Not At-Risk | SDAC
CA4810012 | SID - QUAIL CANYON | 287 | 40 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2519746.318 | 0 | Yes | 0 | 2519746.318 | 1259873.159 | 5039492.636 | At-Risk | Non-DAC
CA1500448 | HILLVIEW ACRES MUTUAL WATER COMPANY | 36 | 47 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36290.849 | No | 2010361.951 | 0 | Yes | 0 | 2048432.6999 | 1024216.35 | 4096865.3999 | Not At-Risk | Missing
CA4200578 | PAINTED CAVE | 172 | 91 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2507422.7628 | 0 | Yes | 0 | 2507422.7628 | 1253711.3814 | 5014845.5255 | Not At-Risk | Non-DAC
CA3600383 | MWD OF SO CAL GENE PLANT | 109 | 61 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 54906.1499 | N/A | 0 | 0 | No | 139104.42 | 194010.5699 | 97005.2849 | 388021.1398 | Not At-Risk | SDAC
CA4300978 | BRUSH AND OLD WELL MUTUAL WATER COMPANY | 70 | 27 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 51248.6479 | N/A | 0 | 0 | Yes | 0 | 51248.6479 | 25624.324 | 102497.2959 | Not At-Risk | Non-DAC
CA5000048 | LAZY B MOBILEHOME PARK | 125 | 49 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 44110.5771 | Yes | 0 | 0 | No | 91926.6 | 137817.0771 | 68908.5385 | 275634.1541 | Not At-Risk | SDAC
CA4910701 | U.S. COAST GUARD TRAINING CENTER | 1422 | 217 | DISTRICT 18 - SONOMA | C | NT - INSTITUTION | N/A | 0 | No | 203229.9488 | N/A | 0 | 0 | No | 83571.54 | 286801.4888 | 143400.7444 | 573602.9777 | Not At-Risk | Non-DAC
CA1200701 | ORICK C.S.D. | 450 | 141 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 72665.7639 | Yes | 0 | 0 | Yes | 0 | 74445.6639 | 37222.8319 | 148891.3278 | Not At-Risk | SDAC
CA2700678 | PARADISE RD WS #05 | 42 | 15 | LPA57 - MONTEREY COUNTY | C | O - OTHER AREA | No | 2313.87 | No | 47337.4564 | No | 2493491.7873 | 0 | No | 63971.7 | 2607114.8137 | 1303557.4069 | 5214229.6274 | At-Risk | Non-DAC
CA2701647 | GREEN ACRES WA | 50 | 20 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48241.181 | No | 2494349.0781 | 0 | No | 72138.3 | 2617042.4291 | 1308521.2145 | 5234084.8582 | At-Risk | SDAC
CA4000203 | IRISH HILLS MUTUAL WATER CO | 135 | 58 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 57843.2548 | Yes | 0 | 0 | Yes | 0 | 57843.2548 | 28921.6274 | 115686.5096 | Not At-Risk | Non-DAC
CA4100582 | COUNTY SERVICE AREA 11 | 450 | 102 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 94811.5205 | Yes | 0 | 0 | Yes | 0 | 94811.5205 | 47405.7602 | 189623.041 | Not At-Risk | Non-DAC
CA4000750 | RIM ROCK WATER COMPANY | 55 | 25 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | HR2W | Non-DAC
CA4000202 | EDNA VALLEY RANCH EAST | 148 | 40 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 59311.8073 | Yes | 0 | 0 | Yes | 0 | 59311.8073 | 29655.9036 | 118623.6146 | Not At-Risk | Non-DAC
CA1310007 | HEBER PUBLIC UTILITY DISTRICT | 6979 | 1632 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA5500124 | MONO VISTA RANCH MHP | 105 | 30 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK | Yes | 0 | No | 42353.3348 | No | 2016324.9616 | 0 | Yes | 0 | 2058678.2963 | 1029339.1482 | 4117356.5927 | Potentially At-Risk | DAC
CA0400021 | ROBINSON'S CORNER MHP | 20 | 22 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 34885.0552 | No | 2008979.2239 | 0 | No | 58003.8 | 2103647.979 | 1051823.9895 | 4207295.9581 | Potentially At-Risk | SDAC
CA5500071 | RAWHIDE INVESTMENT COMPANY | 269 | 100 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 56762.7214 | Yes | 0 | 0 | No | 156003 | 212765.7214 | 106382.8607 | 425531.4427 | Not At-Risk | SDAC
CA5510015 | TUD - CEDAR RIDGE WATER SYSTEM | 1645 | 676 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 177660.9892 | Yes | 0 | 0 | Yes | 0 | 177660.9892 | 88830.4946 | 355321.9785 | Not At-Risk | DAC
CA3900568 | CARIBOU MOBILE PARK PWS | 180 | 72 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 48942.9933 | Yes | 0 | 0 | No | 120823.8 | 169766.7933 | 84883.3966 | 339533.5866 | Potentially At-Risk | SDAC
CA3400331 | WESTERNER MOBILE HOME PARK | 65 | 49 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 50675.4522 | No | 2528162.3886 | 0 | No | 121343.112 | 2700180.9529 | 1350090.4764 | 5400361.9058 | Not At-Risk | SDAC
CA1000546 | FCSA #49/ FIVE POINTS | 445 | 46 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 72226.4533 | N/A | 0 | 0 | Yes | 0 | 72226.4533 | 36113.2267 | 144452.9066 | HR2W | SDAC
CA3400130 | THE COURTLAND GROUP | 40 | 34 | LPA64 - SACRAMENTO COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 47809.4738 | No | 2525448.7867 | 0 | No | 96466.392 | 2672074.1205 | 1336037.0603 | 5344148.241 | HR2W | SDAC
CA1010055 | FCSA #47/QUAIL LAKE ESTATES | 1982 | 710 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1300018 | GATEWAY | 1800 | 48 | LPA43 - IMPERIAL COUNTY | C | T - SECONDARY RESIDENCES | N/A | 0 | No | 191279.6168 | N/A | 0 | 0 | Yes | 0 | 191279.6168 | 95639.8084 | 382559.2336 | Potentially At-Risk | SDAC
CA4400595 | VILLA DEL MONTE MWC | 419 | 127 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 89925.4779 | Yes | 0 | 0 | Yes | 0 | 89925.4779 | 44962.7389 | 179850.9558 | At-Risk | Non-DAC
CA3600345 | WEST END MWC | 63 | 31 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 49709.7335 | Yes | 0 | 0 | Yes | 0 | 49709.7335 | 24854.8667 | 99419.467 | Potentially At-Risk | SDAC
CA3901074 | TWIN OAKS MOBILE PARK | 255 | 85 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | At-Risk | DAC
CA4500210 | LASSEN PINES MUTUAL WATER CO INC | 600 | 198 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 279130.2 | 280910.1 | 140455.05 | 561820.2 | Not At-Risk | SDAC
CA2700838 | SPRING CANYON WA | 99 | 33 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 53776.4941 | Yes | 0 | 0 | Yes | 0 | 56090.3641 | 28045.1821 | 112180.7283 | Potentially At-Risk | Non-DAC
CA2710702 | FORT HUNTER LIGGETT | 5000 | 160 | DISTRICT 05 - MONTEREY | C | O - OTHER AREA | No | 2313.87 | No | 607420.7734 | Yes | 0 | 0 | No | 300803.1 | 910537.7434 | 455268.8717 | 1821075.4868 | Not At-Risk | DAC
CA3600184 | NORTH SHORE MWC | 25 | 32 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 45417.0417 | Yes | 0 | 0 | No | 91738.14 | 139469.0517 | 69734.5258 | 278938.1033 | At-Risk | DAC
CA4300638 | SAN MARTIN FOOTHILLS WATER COMPANY | 145 | 44 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 2349.468 | 1174.734 | 4698.936 | Not At-Risk | Non-DAC
CA1502690 | DUNE 3 MUTUAL WATER COMPANY, LLC | 119 | 36 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 43583.4044 | Yes | 0 | 0 | Yes | 0 | 45363.3044 | 22681.6522 | 90726.6088 | Not At-Risk | DAC
CA3500511 | CASA DE FRUTA ORCHARDS | 53 | 20 | DISTRICT 05 - MONTEREY | C | NT - INDUSTRIAL/AGRICULTURAL | No | 2313.87 | No | 48580.0777 | No | 2494670.5621 | 0 | No | 72138.3 | 2617702.8099 | 1308851.4049 | 5235405.6197 | Not At-Risk | Non-DAC
CA1400020 | ABERDEEN WATER SYSTEM | 23 | 75 | DISTRICT 13 - SAN BERNARDINO | C | R - MOBILE HOME PARK | No | 1779.9 | No | 35148.6415 | No | 2009238.4852 | 0 | No | 124593 | 2170760.0267 | 1085380.0134 | 4341520.0534 | Potentially At-Risk | SDAC
CA3410022 | OLYMPIA MOBILODGE | 450 | 200 | DISTRICT 09 - SACRAMENTO | C | R - MOBILE HOME PARK | Yes | 0 | No | 94811.5205 | Yes | 0 | 0 | No | 371768.76 | 466580.2805 | 233290.1402 | 933160.561 | Not At-Risk | SDAC
CA1000023 | FCSA #14/BELMONT MANOR | 115 | 41 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | No | 2017189.166 | 0 | No | 81875.4 | 2099064.566 | 1049532.283 | 4198129.132 | HR2W | Non-DAC
CA1000041 | FCWWD #38/SKY HARBOUR | 165 | 64 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2021510.1882 | 0 | Yes | 0 | 2021510.1882 | 1010755.0941 | 4043020.3763 | At-Risk | Non-DAC
CA4310021 | PURISSIMA HILLS WATER DISTRICT | 6190 | 2132 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 752840.1742 | Yes | 0 | 0 | Yes | 0 | 752840.1742 | 376420.0871 | 1505680.3484 | Not At-Risk | Non-DAC
CA5010029 | CITY OF MODESTO - DEL RIO | 1274 | 401 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | No | 145064.1452 | Yes | 0 | 0 | No | 31619.4 | 176683.5452 | 88341.7726 | 353367.0904 | Not At-Risk | Non-DAC
CA4900578 | CARMET BY THE SEA WATER COMPANY | 280 | 64 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 74223.2631 | Yes | 0 | 0 | Yes | 0 | 74223.2631 | 37111.6315 | 148446.5262 | Not At-Risk | DAC
CA3301630 | BLYTHE - HIDDEN BEACHES | 383 | 116 | DISTRICT 20 - RIVERSIDE | C | R - MOBILE HOME PARK | No | 2349.468 | No | 87130.6982 | No | 2562679.4051 | 0 | Yes | 0 | 2652159.5713 | 1326079.7856 | 5304319.1426 | Potentially At-Risk | SDAC
CA5610021 | WARRING WATER SERVICE INC | 2100 | 578 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA4900796 | SANTA ROSA MOBILE ESTATES | 420 | 141 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 269770.02 | 272083.89 | 136041.945 | 544167.78 | Potentially At-Risk | SDAC
CA1000299 | THREE PALMS MOBILEHOME PARK | 300 | 105 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK | Yes | 0 | No | 59486.4469 | No | 0 | 1727654.7 | No | 162285 | 1949426.1469 | 974713.0734 | 3898852.2938 | HR2W | SDAC
CA3710044 | RINCON DEL DIABLO MWD (ID-A) | 3330 | 1057 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA5200534 | PASKENTA COMM. SERVICES DIST. | 244 | 74 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 54566.1685 | N/A | 0 | 0 | Yes | 0 | 54566.1685 | 27283.0843 | 109132.3371 | HR2W | SDAC
CA3700900 | LAKE HENSHAW RESORT INC. | 300 | 101 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 77615.6497 | Yes | 0 | 0 | Yes | 0 | 79965.1177 | 39982.5589 | 159930.2355 | HR2W | SDAC
CA3301180 | ANZA MUTUAL WATER COMPANY | 224 | 85 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA2010012 | CAL AM - RAYMOND | 317 | 96 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 60980.1028 | Yes | 0 | 0 | Yes | 0 | 60980.1028 | 30490.0514 | 121960.2056 | At-Risk | SDAC
CA1800534 | SPAULDING EAGLE LAKE MWC | 300 | 82 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 133387.8 | 133387.8 | 66693.9 | 266775.6 | Not At-Risk | SDAC
CA1500550 | WEST VALLEY MUTUAL WATER COMPANY | 70 | 41 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39278.1608 | Yes | 0 | 0 | Yes | 0 | 41058.0608 | 20529.0304 | 82116.1217 | Not At-Risk | Missing
CA1710001 | CLEARLAKE OAKS COUNTY WATER DISTRICT | 2359 | 2110 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | SDAC
CA1900636 | EL RANCHO MOBILE HOME PARK | 215 | 76 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 67871.323 | No | 0 | 1754229.654 | No | 166121.208 | 1990571.653 | 995285.8265 | 3981143.306 | Potentially At-Risk | SDAC
CA5200010 | WOODSON BRIDGE RV PARK | 45 | 46 | LPA82 - TEHAMA COUNTY | C | T - OTHER TRANSIENT AREA | No | 1779.9 | No | 37081.608 | Yes | 0 | 0 | No | 88157.4 | 127018.908 | 63509.454 | 254037.816 | Not At-Risk | DAC
CA3701837 | WYNOLA WATER DISTRICT | 120 | 73 | LPA67 - SAN DIEGO COUNTY | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 56980.6049 | Yes | 0 | 0 | Yes | 0 | 56980.6049 | 28490.3024 | 113961.2097 | Not At-Risk | SDAC
CA2010014 | CAL AM - GOLDSIDE | 1020 | 309 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 122747.1684 | Yes | 0 | 0 | Yes | 0 | 122747.1684 | 61373.5842 | 245494.3369 | HR2W | DAC
CA4810010 | SID - GIBSON CANYON | 452 | 162 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA3810702 | TREASURE ISLAND | 2400 | 172 | DISTRICT 04 - SAN FRANCISCO | C | NT - INSTITUTION | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 142902.936 | 142902.936 | 71451.468 | 285805.872 | Potentially At-Risk | DAC
CA1500436 | HUNGRY GULCH MWC | 74 | 36 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39629.6093 | Yes | 0 | 0 | Yes | 0 | 41409.5093 | 20704.7546 | 82819.0186 | HR2W | SDAC
CA1510049 | CWS - LAKELAND | 271 | 209 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | SDAC
CA4000670 | WALNUT HILLS MUTUAL WATER CO | 486 | 26 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 97494.1714 | Yes | 0 | 0 | Yes | 0 | 97494.1714 | 48747.0857 | 194988.3427 | Not At-Risk | Non-DAC
CA2000832 | SKP PARK OF THE SIERRAS INC | 450 | 261 | DISTRICT 11 - MERCED | C | T - RECREATION AREA | Yes | 0 | No | 72665.7639 | Yes | 0 | 0 | No | 358283.4 | 430949.1639 | 215474.5819 | 861898.3278 | Not At-Risk | DAC
CA1300513 | OCOTILLO MUTUAL WATER CO | 150 | 113 | LPA43 - IMPERIAL COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Missing
CA5610056 | VINEYARD AVE ESTATES MWC | 1200 | 342 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 180790.8742 | Yes | 0 | 0 | Yes | 0 | 183140.3422 | 91570.1711 | 366280.6844 | Potentially At-Risk | DAC
CA2702388 | ROYAL OAK PLACE WS | 60 | 20 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49370.8368 | Yes | 0 | 0 | Yes | 0 | 51684.7068 | 25842.3534 | 103369.4135 | At-Risk | Non-DAC
CA4300792 | ABORN HEIGHTS WATER MUTUAL ASSOCIATION | 45 | 19 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 48382.6695 | No | 2525991.5071 | 0 | No | 43396.056 | 2620119.7006 | 1310059.8503 | 5240239.4012 | Not At-Risk | Non-DAC
CA2000592 | TWO TWENTY FOUR MOBILE HOME PK | 35 | 15 | LPA50 - MADERA COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 36202.9869 | No | 2010275.5305 | 0 | Yes | 0 | 2046478.5174 | 1023239.2587 | 4092957.0348 | HR2W | SDAC
CA1910002 | AMARILLO MUTUAL WATER COMPANY | 3134 | 627 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | DAC
CA1500475 | KRISTA MUTUAL WATER COMPANY | 501 | 179 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 77146.7317 | No | 2050547.4571 | 0 | No | 255258.6 | 2382952.7888 | 1191476.3944 | 4765905.5776 | HR2W | SDAC
CA5800863 | FELLOWSHIP OF FRIENDS | 325 | 30 | LPA88 - YUBA COUNTY | C | T - SECONDARY RESIDENCES | No | 1779.9 | No | 61682.9997 | Yes | 0 | 0 | No | 68055 | 131517.8997 | 65758.9499 | 263035.7994 | Not At-Risk | Non-DAC
CA5310002 | TRINITY CO. W.W. DIST #1 | 2138 | 648 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA4300521 | KENNON WATER COMPANY | 142 | 43 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1300575 | DATE GARDENS MOBILE HOME PARK | 101 | 72 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK | N/A | 0 | No | 42001.8863 | N/A | 0 | 0 | Yes | 0 | 42001.8863 | 21000.9432 | 84003.7727 | Potentially At-Risk | SDAC
CA3100023 | AUBURN MOBILE HOME VILLAGE | 59 | 23 | LPA61 - PLACER COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 38311.6776 | No | 2012349.6212 | 0 | No | 59260.2 | 2111701.3987 | 1055850.6994 | 4223402.7975 | Not At-Risk | Non-DAC
CA3810001 | SAN FRANCISCO REGIONAL WATER SYSTEM | 600 | 257 | DISTRICT 04 - SAN FRANCISCO | C | O - WHOLESALER (SELLS WATER) | Yes | 0 | No | 112007.3912 | Yes | 0 | 0 | Yes | 0 | 112007.3912 | 56003.6956 | 224014.7825 | Not At-Risk | Missing
CA1500340 | WEST TEHACHAPI MUTUAL | 150 | 36 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 46307.1299 | No | 0 | 1036289.19 | Yes | 0 | 1084376.2199 | 542188.1099 | 2168752.4398 | Not At-Risk | DAC
CA1210010 | SCOTIA CSD | 850 | 304 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA | N/A | 0 | No | 107810.6092 | N/A | 0 | 0 | No | 221335.8 | 329146.4092 | 164573.2046 | 658292.8184 | Potentially At-Risk | SDAC
CA1910203 | LOS ANGELES CWWD 40, R 24,27,33-PEARBLSM | 10854 | 2862 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1287517.1152 | Yes | 0 | 0 | Yes | 0 | 1287517.1152 | 643758.5576 | 2575034.2303 | Not At-Risk | DAC
CA1500575 | SAN JOAQUIN ESTATES MUTUAL WATER COMPANY | 165 | 61 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 47625.0616 | No | 2021510.1882 | 0 | No | 107003.4 | 2177918.5497 | 1088959.2749 | 4355837.0995 | HR2W | SDAC
CA5410048 | PORTERVILLE-JONES CORNER | 339 | 118 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA3900755 | SHADY REST TRAILER COURT | 120 | 49 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 43671.2665 | No | 2017621.2682 | 0 | Yes | 0 | 2063072.4347 | 1031536.2173 | 4126144.8694 | At-Risk | SDAC
CA4400692 | ALLAN LANE WATER ASSOCIATION | 68 | 17 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | No | 0 | 1020929.7 | Yes | 0 | 1023243.57 | 511621.785 | 2046487.14 | Potentially At-Risk | Non-DAC
CA5410014 | TIPTON COMMUNITY SERVICES DIST | 1998 | 608 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 208676.3152 | Yes | 0 | 0 | No | 781690.2 | 990366.5152 | 495183.2576 | 1980733.0305 | HR2W | SDAC
CA3900719 | MOKELUMNE MOBILE SENIOR PARK | 55 | 25 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 37960.2291 | No | 2012003.9394 | 0 | No | 61773 | 2113517.0685 | 1056758.5343 | 4227034.137 | Potentially At-Risk | Non-DAC
CA1500507 | ST. CLAIR RANCHOS MUTUAL WATER CO. | 105 | 32 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 42353.3348 | No | 2016324.9616 | 0 | No | 70567.8 | 2131025.9963 | 1065512.9982 | 4262051.9927 | At-Risk | Non-DAC
CA2702198 | FOOTHILL ESTATES WS | 183 | 41 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 63265.6024 | Yes | 0 | 0 | Yes | 0 | 63265.6024 | 31632.8012 | 126531.2048 | Not At-Risk | Non-DAC
CA0105008 | CASTLEWOOD DOMESTIC WATER SYSTEM | 524 | 206 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 101786.8632 | N/A | 0 | 0 | Yes | 0 | 101786.8632 | 50893.4316 | 203573.7264 | Not At-Risk | Non-DAC
CA4000214 | BARON CANYON MUTUAL WATER CO. | 81 | 25 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 51743.1138 | Yes | 0 | 0 | Yes | 0 | 54056.9838 | 27028.4919 | 108113.9676 | Not At-Risk | Non-DAC
CA4000648 | KEN MAR GARDENS | 84 | 45 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 52082.0105 | No | 0 | 1359529.5 | No | 112971.3 | 1526896.6805 | 763448.3403 | 3053793.3611 | HR2W | Non-DAC
CA5610081 | CAL AMERICAN WC - LAS POSAS ESTATES | 2049 | 621 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA5700554 | CAMPERS INN - RV & GOLF COURSE | 120 | 68 | LPA87 - YOLO COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 43671.2665 | No | 2017621.2682 | 0 | No | 115798.2 | 2178870.6347 | 1089435.3173 | 4357741.2694 | At-Risk | DAC
CA2000534 | LEISURE ACRES MUTUAL WATER COMPANY | 45 | 24 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37081.608 | Yes | 0 | 0 | Yes | 0 | 38861.508 | 19430.754 | 77723.016 | At-Risk | Non-DAC
CA0300019 | FIDDLETOWN COMMUNITY SERVICE | 100 | 66 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 41914.0242 | No | 2015892.8593 | 0 | No | 31619.4 | 2091206.1836 | 1045603.0918 | 4182412.3671 | Not At-Risk | DAC
CA0310006 | RIVER PINES PUD | 510 | 215 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | No | 77937.4907 | Yes | 0 | 0 | Yes | 0 | 77937.4907 | 38968.7453 | 155874.9813 | Not At-Risk | DAC
CA2701935 | MOUNT TORO RANCHOS MWA | 45 | 19 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 47676.3531 | Yes | 0 | 0 | Yes | 0 | 49990.2231 | 24995.1116 | 99980.4463 | Not At-Risk | Non-DAC
CA1710014 | MT. KONOCTI MUTUAL WATER COMPANY | 4360 | 1595 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | Non-DAC
CA5500125 | MOTHER LODE MOBILE ESTATES | 210 | 75 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK | No | 1779.9 | No | 51578.8567 | Yes | 0 | 0 | No | 124593 | 177951.7567 | 88975.8783 | 355903.5134 | Not At-Risk | SDAC
CA3103310 | EMIGRANT GAP MUTUAL WATER CO. | 125 | 43 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 44110.5771 | Yes | 0 | 0 | No | 84388.2 | 130278.6771 | 65139.3385 | 260557.3541 | Not At-Risk | Non-DAC
CA3301803 | CASTRO TRAILER PARK | 180 | 44 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK | N/A | 0 | No | 63858.9532 | N/A | 0 | 0 | No | 113050.872 | 176909.8252 | 88454.9126 | 353819.6503 | Not At-Risk | SDAC
CA3610002 | ALPINE WATER USERS ASSOCIATION | 2534 | 931 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 328847.6674 | Yes | 0 | 0 | Yes | 0 | 328847.6674 | 164423.8337 | 657695.3347 | HR2W | DAC
CA2701742 | CALIFORNIA ORCHARD WS | 150 | 50 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 2313.87 | No | 59537.7384 | Yes | 0 | 0 | Yes | 0 | 61851.6084 | 30925.8042 | 123703.2169 | Not At-Risk | Non-DAC
CA3301114 | CHERRY VALLEY WATER COMPANY | 210 | 75 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA2710005 | CASTROVILLE COMMUNITY SERVICES DISTRICT | 6897 | 1884 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 821716.4677 | Yes | 0 | 0 | No | 406968.9 | 1228685.3677 | 614342.6838 | 2457370.7354 | Not At-Risk | DAC
CA1400111 | MEADOWCREEK MUTUAL WATER COMPANY | 764 | 284 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 100254.4674 | Yes | 0 | 0 | No | 373360.2 | 473614.6674 | 236807.3337 | 947229.3349 | Not At-Risk | Non-DAC
CA4900605 | MARK WEST ACRES MWC | 61 | 22 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | N/A | 0 | No | 2495527.8529 | 0 | Yes | 0 | 2497841.7229 | 1248920.8615 | 4995683.4459 | At-Risk | Non-DAC
CA4500219 | CREEKSIDE MOBILEHOME PARK | 85 | 41 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 81875.4 | 83655.3 | 41827.65 | 167310.6 | Not At-Risk | SDAC
CA4900548 | HOLLAND HEIGHTS MUTUAL WATER COMPANY | 300 | 117 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 230570.34 | 230570.34 | 115285.17 | 461140.68 | Not At-Risk | Non-DAC
CA5610005 | MEINERS OAKS CWD | 4200 | 1279 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 524708.289 | Yes | 0 | 0 | Yes | 0 | 524708.289 | 262354.1445 | 1049416.5781 | Not At-Risk | Non-DAC
CA2910002 | CITY OF NEVADA CITY | 3001 | 1252 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | No | 0 | 13220353.83 | Yes | 0 | 13220353.83 | 6610176.915 | 26440707.66 | At-Risk | SDAC
CA4200721 | NAPLES | 67 | 23 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 50161.5958 | N/A | 0 | 0 | Yes | 0 | 50161.5958 | 25080.7979 | 100323.1915 | Potentially At-Risk | SDAC
CA0510001 | UNION PUBLIC UTILITY DISTRICT | 4620 | 1679 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA2710300 | CSP-PFEIFFER BIG SUR | 580 | 129 | DISTRICT 05 - MONTEREY | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 250170.18 | 250170.18 | 125085.09 | 500340.36 | Not At-Risk | DAC
CA1710010 | LOWER LAKE COUNTY WATER DISTRICT | 1355 | 794 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES | Yes | 0 | No | 152180.9764 | Yes | 0 | 0 | Yes | 0 | 152180.9764 | 76090.4882 | 304361.9528 | Not At-Risk | SDAC
CA3701747 | NORTH PEAK MUTUAL WATER COMPANY | 25 | 89 | LPA67 - SAN DIEGO COUNTY | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 46089.8867 | Yes | 0 | 0 | Yes | 0 | 46089.8867 | 23044.9434 | 92179.7734 | Not At-Risk | SDAC
CA4210002 | LOS ALAMOS COMMUNITY SERVICES DISTRICT | 1800 | 613 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 245930.9359 | Yes | 0 | 0 | Yes | 0 | 245930.9359 | 122965.4679 | 491861.8718 | Not At-Risk | Non-DAC
CA4900728 | EVERGREEN MOBILE ESTATES | 70 | 23 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | No | 2313.87 | No | 50500.4925 | No | 0 | 1093486.8 | No | 77038.26 | 1223339.4225 | 611669.7112 | 2446678.845 | Potentially At-Risk | Non-DAC
CA1710021 | LAKE COUNTY CSA 21 - NORTH LAKEPORT | 3104 | 1257 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA5710004 | KNIGHTS LANDING SVC. DIST. | 1300 | 287 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 147348.5602 | Yes | 0 | 0 | No | 390949.8 | 538298.3602 | 269149.1801 | 1076596.7203 | At-Risk | SDAC
CA2701897 | BERRY DR WS #02 | 50 | 19 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48241.181 | No | 2494349.0781 | 0 | No | 70504.98 | 2615409.1091 | 1307704.5545 | 5230818.2182 | Potentially At-Risk | Non-DAC
CA4200800 | EAST VALLEY FARMS MUTUAL WATER COMPANY | 132 | 41 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 57504.3581 | Yes | 0 | 0 | Yes | 0 | 57504.3581 | 28752.179 | 115008.7162 | At-Risk | Non-DAC
CA1500211 | STOCKDALE ANNEX MUTUAL WATER | 433 | 143 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 71172.108 | Yes | 0 | 0 | No | 210028.2 | 281200.308 | 140600.154 | 562400.6159 | At-Risk | Non-DAC
CA3110006 | PLACER CWA - COLFAX | 2987 | 942 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA5700712 | CAL AM - DUNNIGAN | 400 | 150 | LPA87 - YOLO COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 68272.6582 | Yes | 0 | 0 | Yes | 0 | 68272.6582 | 34136.3291 | 136545.3164 | Not At-Risk | SDAC
CA0110012 | TOWN OF SUNOL - SFPUC | 352 | 126 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1900817 | CLEAR SKIES MOBILE HOME PARK | 131 | 47 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 58241.6354 | No | 0 | 1399529.088 | No | 118026.216 | 1578146.4074 | 789073.2037 | 3156292.8147 | At-Risk | SDAC
CA3310800 | CALIFORNIA REHABILITATION CENTER - NORCO | 3800 | 1357 | DISTRICT 20 - RIVERSIDE | C | NT - INSTITUTION | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 2287276.2 | 2287276.2 | 1143638.1 | 4574552.4 | Not At-Risk | Non-DAC
CA4210003 | GUADALUPE WATER DEPARTMENT | 8123 | 2366 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA5610039 | CHANNEL ISLANDS BEACH CSD | 5180 | 1866 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA4900533 | MORTON'S WARM SPRINGS / SONOMA SPRINGS | 59 | 21 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | No | 2495313.5302 | 0 | Yes | 0 | 2497627.4002 | 1248813.7001 | 4995254.8005 | Not At-Risk | Non-DAC
CA4310019 | CITY OF SAN JOSE - NSJ/ALVISO | 15300 | 2200 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1797202.724 | Yes | 0 | 0 | Yes | 0 | 1797202.724 | 898601.362 | 3594405.4479 | Not At-Risk | Non-DAC
CA4900588 | LAWNDALE MUTUAL WATER COMPANY | 218 | 66 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA2702608 | THIMIO MWC | 60 | 21 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49370.8368 | Yes | 0 | 0 | No | 73771.62 | 125456.3268 | 62728.1634 | 250912.6535 | Potentially At-Risk | Non-DAC
CA4300550 | VISTA GRANDE WATER USERS ASSOCIATION | 60 | 24 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA4910024 | CALIFORNIA-AMERICAN GEYSERVILLE (PUC) | 1014 | 306 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 157139.9946 | Yes | 0 | 0 | Yes | 0 | 157139.9946 | 78569.9973 | 314279.9891 | Not At-Risk | Non-DAC
CA3610031 | MUSCOY MWC NO. 1 | 13000 | 1407 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1511145.3671 | Yes | 0 | 0 | No | 49271.82 | 1560417.1871 | 780208.5936 | 3120834.3743 | Not At-Risk | SDAC
CA1500327 | RANCHO SECO INC. WATER SYSTEM | 55 | 23 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2012003.9394 | 0 | Yes | 0 | 2012003.9394 | 1006001.9697 | 4024007.8788 | At-Risk | SDAC
CA2600501 | BIRCHIM COMMUNITY SERVICE DISTRICT | 150 | 76 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 46307.1299 | Yes | 0 | 0 | No | 125849.4 | 172156.5299 | 86078.2649 | 344313.0598 | Not At-Risk | Non-DAC
CA0800548 | KLAMATH C.S.D. | 100 | 59 | DISTRICT 01 - KLAMATH | C | T - SECONDARY RESIDENCES | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 50465.4 | 52245.3 | 26122.65 | 104490.6 | Not At-Risk | SDAC
CA1502564 | SIERRA MEADOWS | 68 | 51 | DISTRICT 19 - TEHACHAPI | C | R - MOBILE HOME PARK | No | 1779.9 | No | 39102.4366 | No | 2013127.4051 | 0 | No | 93183 | 2147192.7418 | 1073596.3709 | 4294385.4835 | Not At-Risk | Missing
CA1510033 | CWS - KERNVILLE | 2520 | 1903 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 254540.3384 | Yes | 0 | 0 | Yes | 0 | 254540.3384 | 127270.1692 | 509080.6767 | Potentially At-Risk | Non-DAC
CA4010003 | SAN MIGUELITO MWC | 1758 | 693 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 241186.3818 | Yes | 0 | 0 | Yes | 0 | 241186.3818 | 120593.1909 | 482372.7636 | Not At-Risk | Non-DAC
CA4410002 | SLVWD - FELTON WATER SYSTEM | 4340 | 1355 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1510016 | RAND COMMUNITIES WATER DISTRICT | 303 | 284 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 59750.0332 | Yes | 0 | 0 | Yes | 0 | 59750.0332 | 29875.0166 | 119500.0664 | HR2W | Missing
CA5500042 | BELLEVIEW OAKS MUTUAL WATER CO | 468 | 168 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 74247.2819 | Yes | 0 | 0 | Yes | 0 | 74247.2819 | 37123.641 | 148494.5638 | Not At-Risk | Non-DAC
CA5602101 | ESTERINA PROPERTIES | 50 | 16 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 48955.8652 | Yes | 0 | 0 | Yes | 0 | 51305.3332 | 25652.6666 | 102610.6663 | HR2W | DAC
CA5601137 | RINCON WATER & ROAD WORKS | 25 | 27 | DISTRICT 06 - SANTA BARBARA | C | NT - INDUSTRIAL/AGRICULTURAL | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | DAC
CA4000200 | BASSI RANCH MUTUAL WATER CO. | 85 | 24 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 52194.9761 | Yes | 0 | 0 | Yes | 0 | 54508.8461 | 27254.4231 | 109017.6922 | Not At-Risk | Non-DAC
CA0400027 | FOOTHILL SOLAR COMPANY | 180 | 127 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2022806.4948 | 0 | No | 189925.8 | 2214512.1948 | 1107256.0974 | 4429024.3896 | Not At-Risk | Missing
CA4700513 | HORNBROOK C.S.D. | 280 | 147 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | No | 57729.2046 | Yes | 0 | 0 | Yes | 0 | 57729.2046 | 28864.6023 | 115458.4092 | At-Risk | SDAC
CA1900102 | WESTSIDE PARK MUTUAL WATER | 485 | 166 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1200587 | BRICELAND C.S.D. | 75 | 26 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | No | 39717.4714 | N/A | 0 | 0 | Yes | 0 | 39717.4714 | 19858.7357 | 79434.9428 | Not At-Risk | DAC
CA3900813 | HAVEN ACRES RIVER CLUB INC | 100 | 51 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 41914.0242 | No | 2015892.8593 | 0 | No | 94439.4 | 2152246.2836 | 1076123.1418 | 4304492.5671 | Not At-Risk | Non-DAC
CA3701995 | WILLOWSIDE TERRACE WATER ASSOCIATION | 100 | 32 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 54687.8221 | Yes | 0 | 0 | Yes | 0 | 54687.8221 | 27343.911 | 109375.6442 | HR2W | Non-DAC
CA2900529 | GOLD COUNTRY HOME PARK - WATER SYSTEM | 60 | 27 | LPA59 - NEVADA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 38399.5397 | Yes | 0 | 0 | No | 64285.8 | 104465.2397 | 52232.6198 | 208930.4794 | Not At-Risk | DAC
CA1900804 | EVERGREEN MUTUAL WATER COMPANY | 95 | 46 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 54114.6264 | No | 0 | 1387298.034 | Yes | 0 | 1443762.1284 | 721881.0642 | 2887524.2568 | Not At-Risk | DAC
CA4300997 | NASA AMES RESEARCH CENTER | 5300 | 300 | DISTRICT 17 - SANTA CLARA | C | NT - INSTITUTION | N/A | 0 | N/A | 0 | Yes | 0 | 0 | No | 429814.44 | 429814.44 | 214907.22 | 859628.88 | Not At-Risk | Non-DAC
CA5500120 | 49ER TRAILER RANCH | 121 | 80 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 90670.2 | 92450.1 | 46225.05 | 184900.2 | Not At-Risk | SDAC
CA4900587 | BRAND WATER COMPANY | 112 | 34 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 55245.0466 | No | 0 | 1226508.15 | No | 95004.78 | 1379071.8466 | 689535.9233 | 2758143.6932 | Potentially At-Risk | DAC
CA2700541 | DEL MONTE FARMS RD WS #03 | 55 | 16 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | N/A | 0 | No | 2494884.8848 | 0 | No | 65605.02 | 2562803.7748 | 1281401.8874 | 5125607.5497 | At-Risk | DAC
CA1910020 | CAL-AM WATER COMPANY - EAST PASADENA | 9887 | 2996 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1176661.0684 | Yes | 0 | 0 | Yes | 0 | 1176661.0684 | 588330.5342 | 2353322.1369 | At-Risk | Non-DAC
CA2700638 | MAHER RD WS #05 | 65 | 17 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 49935.6646 | No | 2495956.4983 | 0 | No | 67238.34 | 2613130.503 | 1306565.2515 | 5226261.0059 | At-Risk | Non-DAC
CA2700665 | OAK HEIGHTS W & R CO INC | 105 | 35 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 54454.2876 | Yes | 0 | 0 | No | 96638.1 | 153406.2576 | 76703.1288 | 306812.5152 | HR2W | Non-DAC
CA4900549 | SONOMA COUNTY CSA 41-FREESTONE | 90 | 26 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA3301115 | CHIRIACO SUMMIT WATER DIST. | 534 | 37 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 104441.2081 | N/A | 0 | 0 | Yes | 0 | 104441.2081 | 52220.6041 | 208882.4162 | Potentially At-Risk | SDAC
CA4710010 | TULELAKE, CITY OF | 1000 | 471 | DISTRICT 01 - KLAMATH | C | T - RECREATION AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 50465.4 | 52245.3 | 26122.65 | 104490.6 | Not At-Risk | SDAC
CA1009232 | SUMNER PECK RANCH | 85 | 19 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | No | 40596.0925 | N/A | 0 | 0 | No | 54234.6 | 94830.6925 | 47415.3463 | 189661.3851 | Not At-Risk | Missing
CA0400014 | LAKE MADRONE WATER DISTRICT | 297 | 123 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 31619.4 | 33399.3 | 16699.65 | 66798.6 | Not At-Risk | SDAC
CA4900901 | SOBRE VISTA WATER COMPANY | 80 | 26 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 51630.1482 | No | 0 | 1129765.35 | Yes | 0 | 1183709.3682 | 591854.6841 | 2367418.7365 | At-Risk | Non-DAC
CA0800555 | GASQUET C.S.D. | 775 | 239 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA1000078 | FCWWD #42/ALLUVIAL & FANCHER | 291 | 104 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 58695.6879 | Yes | 0 | 0 | Yes | 0 | 58695.6879 | 29347.8439 | 117391.3757 | Not At-Risk | Non-DAC
CA5010006 | CITY OF WATERFORD | 8788 | 2065 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | DAC
CA1900563 | SUNDALE MUTUAL WATER COMPANY A, B | 1100 | 330 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA0510011 | SNOWSHOE SPRINGS ASSN. | 596 | 301 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA2400201 | VOLTA COMMUNITY SD | 156 | 44 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 46834.3026 | No | 2020732.4042 | 0 | No | 85644.6 | 2153211.3067 | 1076605.6534 | 4306422.6135 | At-Risk | SDAC
CA4700523 | GRENADA SANITARY DISTRICT | 280 | 103 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 57729.2046 | Yes | 0 | 0 | Yes | 0 | 59509.1046 | 29754.5523 | 119018.2092 | Potentially At-Risk | DAC
CA1300620 | RIO BEND RV GOLF RESORT & STORM CROSSING | 500 | 68 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK | N/A | 0 | No | 77058.8695 | N/A | 0 | 0 | Yes | 0 | 77058.8695 | 38529.4348 | 154117.7391 | Not At-Risk | DAC
CA1910061 | LAS FLORES WATER CO. | 4844 | 1479 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | Yes | 0 | No | 598535.8941 | Yes | 0 | 0 | Yes | 0 | 598535.8941 | 299267.947 | 1197071.7882 | Potentially At-Risk | Non-DAC
CA3600114 | CSA 70 W-3 HACIENDA | 695 | 165 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | SDAC
CA2700522 | CABANA HOLIDAY WS | 400 | 146 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 87779.132 | No | 2531855.5505 | 0 | No | 277936.62 | 2899885.1725 | 1449942.5862 | 5799770.345 | Not At-Risk | DAC
CA1610002 | AVENAL, CITY OF | 13218 | 2019 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA2710021 | CAL AM WATER COMPANY - TORO | 1065 | 418 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | Non-DAC
CA2710022 | CAL AM WATER COMPANY - HIDDEN HILLS | 1106 | 451 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA2710009 | CWSC KING CITY | 14441 | 2749 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1673928.7596 | Yes | 0 | 0 | Yes | 0 | 1673928.7596 | 836964.3798 | 3347857.5192 | Not At-Risk | SDAC
CA3900733 | COUNTRY CLUB VISTA MUTUAL WATER CO | 75 | 31 | LPA69 - SAN JOAQUIN COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | No | 39717.4714 | No | 2013732.3483 | 0 | No | 69311.4 | 2124541.1196 | 1062270.5598 | 4249082.2393 | Not At-Risk | Non-DAC
CA3310078 | WEST PALM SPRINGS VILLAGE | 532 | 260 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | SDAC
CA4900736 | CLEAR CREEK WATER COMPANY | 40 | 19 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 47111.5253 | No | 2493277.4646 | 0 | Yes | 0 | 2540388.9899 | 1270194.4949 | 5080777.9797 | Not At-Risk | Non-DAC
CA2000544 | MADERA CO MD1-HIDDEN LAKE ESTATES | 162 | 49 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | N/A | 0 | No | 47361.4753 | N/A | 0 | 0 | Yes | 0 | 47361.4753 | 23680.7376 | 94722.9505 | HR2W | Non-DAC
CA1910103 | PALM RANCH IRRIGATION DIST. | 5564 | 1702 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 681076.0737 | Yes | 0 | 0 | Yes | 0 | 683425.5417 | 341712.7708 | 1366851.0833 | Not At-Risk | Non-DAC
CA2010016 | RIVERSTONE/ROOTCREEK WATER DISTRICT | 2270 | 742 | DISTRICT 11 - MERCED | C | R - SUBDIVISION | Yes | 0 | No | 232574.81 | Yes | 0 | 0 | Yes | 0 | 232574.81 | 116287.405 | 465149.6201 | Not At-Risk | Non-DAC
CA5301103 | COVINGTON MILL - A | 60 | 42 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2012436.0416 | 0 | No | 83131.8 | 2097347.7416 | 1048673.8708 | 4194695.4832 | Not At-Risk | DAC
CA2000501 | BASS LAKE ANNEX 3 | 42 | 28 | LPA50 - MADERA COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 65542.2 | 67322.1 | 33661.05 | 134644.2 | At-Risk | DAC
CA4900660 | YULUPA MUTUAL WATER COMPANY | 200 | 59 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 65186.0171 | Yes | 0 | 0 | No | 135837.78 | 201023.7971 | 100511.8986 | 402047.5943 | Not At-Risk | Non-DAC
CA5010034 | CITY OF MODESTO - NORTH TURLOCK | 145 | 52 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | No | 45867.8193 | No | 0 | 1196605.83 | Yes | 0 | 1242473.6493 | 621236.8247 | 2484947.2987 | Potentially At-Risk | DAC
CA3710047 | CAMPO HILLS-COUNTY PUBLIC WORKS WASTEWTR | 500 | 216 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA1510014 | MOJAVE PUD | 4200 | 1200 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 402148.6887 | Yes | 0 | 0 | Yes | 0 | 402148.6887 | 201074.3443 | 804297.3774 | Potentially At-Risk | SDAC
CA3110028 | NORTHSTAR C.S.D. | 300 | 933 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 59486.4469 | Yes | 0 | 0 | Yes | 0 | 59486.4469 | 29743.2234 | 118972.8938 | Not At-Risk | Non-DAC
CA1410007 | HIGHLAND MOBILE HOME PARK | 1400 | 500 | DISTRICT 13 - SAN BERNARDINO | C | R - MOBILE HOME PARK | Yes | 0 | No | 156134.7715 | Yes | 0 | 0 | No | 658563 | 814697.7715 | 407348.8857 | 1629395.543 | Not At-Risk | SDAC
CA1510038 | BEAR VALLEY CSD | 8170 | 2851 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 750961.2784 | Yes | 0 | 0 | Yes | 0 | 750961.2784 | 375480.6392 | 1501922.5568 | Not At-Risk | Non-DAC
CA4500303 | TUCKER OAKS EAST WATER DISTRICT | 95 | 34 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2015460.7571 | 0 | Yes | 0 | 2017240.6571 | 1008620.3286 | 4034481.3142 | Not At-Risk | DAC
CA4900630 | AUSTIN CREEK MUTUAL (SPRINGHILL) | 150 | 63 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA3700937 | LAZY H MUTUAL WATER COMPANY | 70 | 43 | LPA67 - SAN DIEGO COUNTY | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 51248.6479 | Yes | 0 | 0 | Yes | 0 | 51248.6479 | 25624.324 | 102497.2959 | Not At-Risk | Non-DAC
CA1110001 | CITY OF ORLAND | 8323 | 2671 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA3110041 | MIDWAY HEIGHTS C. W. D. | 1080 | 443 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA0310012 | AWA BUCKHORN PLANT | 8809 | 2743 | DISTRICT 10 - STOCKTON | C | O - WHOLESALER (SELLS WATER) | N/A | 0 | No | 807105.1688 | N/A | 0 | 0 | Yes | 0 | 807105.1688 | 403552.5844 | 1614210.3376 | Not At-Risk | Non-DAC
CA5010033 | CITY OF MODESTO - GRAYSON | 871 | 277 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | No | 109655.7136 | Yes | 0 | 0 | Yes | 0 | 109655.7136 | 54827.8568 | 219311.4271 | At-Risk | DAC
CA5601125 | COMMUNITY MUTUAL WATER CO | 53 | 36 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 49299.7826 | Yes | 0 | 0 | Yes | 0 | 51649.2506 | 25824.6253 | 103298.5012 | Not At-Risk | Non-DAC
CA2701257 | CAL AM WATER COMPANY - GARRAPATA | 30 | 47 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 45981.8695 | Yes | 0 | 0 | Yes | 0 | 45981.8695 | 22990.9348 | 91963.7391 | Not At-Risk | DAC
CA0510012 | CAMANCHE SOUTH SHORE-EBMUD | 1079 | 448 | DISTRICT 10 - STOCKTON | C | T - RECREATION AREA | N/A | 0 | Yes | 0 | Yes | 0 | 0 | No | 593230.2 | 593230.2 | 296615.1 | 1186460.4 | Not At-Risk | Non-DAC
CA5500077 | SLIDE INN SNOWBOWL WATER CO | 417 | 153 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 69766.3141 | Yes | 0 | 0 | No | 186156.6 | 255922.9141 | 127961.4571 | 511845.8283 | Not At-Risk | Non-DAC
CA3610850 | CALIFORNIA INSTITUTION FOR MEN | 10667 | 1912 | DISTRICT 13 - SAN BERNARDINO | C | NT - INSTITUTION | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | Non-DAC
CA5210002 | GERBER LAS FLORES CSD | 1200 | 399 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 138562.3488 | Yes | 0 | 0 | Yes | 0 | 138562.3488 | 69281.1744 | 277124.6977 | Not At-Risk | SDAC
CA4810026 | SID - PEABODY | 66 | 17 | DISTRICT 04 - SAN FRANCISCO | C | T - SECONDARY RESIDENCES | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1500561 | ROUND MOUNTAIN WATER COMPANY | 50 | 18 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37520.9186 | Yes | 0 | 0 | No | 52978.2 | 92279.0186 | 46139.5093 | 184558.0371 | HR2W | DAC
CA1500251 | RIVERKERN MUTUAL WATER COMPANY | 336 | 145 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Missing
CA1510026 | CWS - UPPER BODFISH WATER SYSTEM | 419 | 221 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | SDAC
CA5610003 | VENTURA CWWD NO. 17 - BELL CANYON | 2049 | 710 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 278119.5026 | N/A | 0 | 0 | Yes | 0 | 278119.5026 | 139059.7513 | 556239.0052 | Not At-Risk | Non-DAC
CA4900599 | RANDAL'S RANCHETTE MUTUAL WATER COMPANY | 100 | 29 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 53889.4597 | Yes | 0 | 0 | No | 86838.18 | 143041.5097 | 71520.7549 | 286083.0194 | Not At-Risk | Non-DAC
CA3600215 | GILBERT STREET COMPLEX | 1000 | 1 | LPA66 - SAN BERNARDINO COUNTY | C | MEDICAL FACILITY | Yes | 0 | N/A | 0 | No | 0 | 827444.1 | Yes | 0 | 827444.1 | 413722.05 | 1654888.2 | Not At-Risk | Missing
CA4300526 | OAKMONT WATER SYSTEM | 63 | 25 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 50446.174 | N/A | 0 | 0 | Yes | 0 | 50446.174 | 25223.087 | 100892.3479 | Not At-Risk | Non-DAC
CA5301104 | COVINGTON MILL MWC-DIVISION B | 59 | 99 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 38311.6776 | Yes | 0 | 0 | No | 154746.6 | 194838.1776 | 97419.0888 | 389676.3552 | Not At-Risk | SDAC
CA4010028 | SLO CSA NO. 16 - SHANDON | 1347 | 340 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 194757.5308 | Yes | 0 | 0 | Yes | 0 | 194757.5308 | 97378.7654 | 389515.0615 | Potentially At-Risk | DAC
CA2310009 | BROOKTRAILS TOWNSHIP CSD | 3800 | 1554 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 367003.8434 | N/A | 0 | 0 | Yes | 0 | 367003.8434 | 183501.9217 | 734007.6867 | At-Risk | SDAC
CA5610010 | CAL AMERICAN WC - RIO PLAZA | 1716 | 518 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | Non-DAC
CA5301010 | BUD FINE MWC | 43 | 40 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | No | 36905.8838 | N/A | 0 | 0 | No | 80619 | 117524.8838 | 58762.4419 | 235049.7675 | Not At-Risk | SDAC
CA1710009 | UPPER LAKE COUNTY WATER DISTRICT | 989 | 401 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES | Yes | 0 | No | 120023.4429 | Yes | 0 | 0 | Yes | 0 | 120023.4429 | 60011.7215 | 240046.8859 | Not At-Risk | DAC
CA3600166 | MILL CREEK MSC | 315 | 72 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 157070.94 | 159384.81 | 79692.405 | 318769.62 | Not At-Risk | DAC
CA3310026 | NUEVO WATER COMPANY | 7033 | 1882 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 849480.9678 | Yes | 0 | 0 | Yes | 0 | 849480.9678 | 424740.4839 | 1698961.9356 | Not At-Risk | DAC
CA2300731 | CITY OF 10,000 BUDDHAS | 200 | 50 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2024534.9037 | 0 | No | 93183 | 2117717.9037 | 1058858.9518 | 4235435.8073 | At-Risk | SDAC
CA4300716 | LUPIN LODGE | 300 | 22 | DISTRICT 17 - SANTA CLARA | C | T - RECREATION AREA | N/A | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | Non-DAC
CA3200509 | CLIO PUBLIC UTILITY DISTRICT | 79 | 53 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 96952.2 | 96952.2 | 48476.1 | 193904.4 | Not At-Risk | DAC
CA4810013 | RURAL NORTH VACAVILLE WATER DISTRICT | 1130 | 398 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | Non-DAC
CA4400558 | SAN ANDREAS MUTUAL WATER CO | 350 | 135 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 82130.8533 | Yes | 0 | 0 | Yes | 0 | 82130.8533 | 41065.4266 | 164261.7066 | At-Risk | Non-DAC
CA5010021 | DENAIR COMMUNITY SERVICES DISTRICT | 5189 | 1674 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | No | 489044.3187 | Yes | 0 | 0 | Yes | 0 | 489044.3187 | 244522.1594 | 978088.6374 | Not At-Risk | Non-DAC
CA1502659 | OWENS PEAK SOUTH | 40 | 17 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36642.2974 | No | 2010707.6327 | 0 | Yes | 0 | 2049129.8302 | 1024564.9151 | 4098259.6603 | At-Risk | Non-DAC
CA1510056 | CWS - LOWER BODFISH WATER SYSTEM | 348 | 528 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | SDAC
CA0510002 | CALAVERAS PUD | 6286 | 1906 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | No | 585429.057 | N/A | 0 | 0 | Yes | 0 | 585429.057 | 292714.5285 | 1170858.114 | Not At-Risk | DAC
CA4200848 | VISTA HILLS MUTUAL WATER COMPANY | 75 | 21 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | Non-DAC
CA1200588 | SEAWOOD ESTATES MUTUAL WATER COMPANY | 60 | 23 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | No | 38399.5397 | Yes | 0 | 0 | No | 35388.6 | 73788.1397 | 36894.0698 | 147576.2794 | Potentially At-Risk | SDAC
CA5200570 | SURREY VILLAGE WATER CO. INC. | 145 | 75 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 45867.8193 | Yes | 0 | 0 | No | 124593 | 172240.7193 | 86120.3597 | 344481.4387 | Not At-Risk | SDAC
CA4900585 | BENNETT RIDGE MUTUAL WATER COMPANY | 446 | 135 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 92975.5484 | Yes | 0 | 0 | Yes | 0 | 92975.5484 | 46487.7742 | 185951.0968 | Not At-Risk | Non-DAC
CA0410018 | DEL ORO WATER CO.-STIRLING BLUFFS | 514 | 156 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA5200584 | LITTLE AVENUE WATER SYSTEM | 53 | 16 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37784.5049 | No | 0 | 835893.39 | No | 50465.4 | 925923.1949 | 462961.5975 | 1851846.3898 | Not At-Risk | SDAC
CA4500204 | WHITE OAK MUTUAL WATER COMPANY | 415 | 126 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 69590.5899 | Yes | 0 | 0 | Yes | 0 | 69590.5899 | 34795.295 | 139181.1798 | Not At-Risk | Non-DAC
CA3700924 | LAKE MORENA VIEWS MWC | 360 | 123 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 84493.998 | Yes | 0 | 0 | Yes | 0 | 86843.466 | 43421.733 | 173686.9321 | HR2W | SDAC
CA1210022 | RESORT IMPROVEMENT DISTRICT #1 | 1500 | 656 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Missing
CA1500349 | STOCKDALE MUTUAL WATER CO. | 200 | 81 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 50700.2356 | Yes | 0 | 0 | No | 132131.4 | 184611.5356 | 92305.7678 | 369223.0711 | Not At-Risk | Non-DAC
CA0400019 | OROVILLE MOBILE HOME PARK | 74 | 35 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 39629.6093 | No | 2013645.9278 | 0 | No | 74337 | 2129392.4371 | 1064696.2185 | 4258784.8742 | Potentially At-Risk | SDAC
CA3210010 | HAMILTON BRANCH CSD | 1624 | 503 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | No | 1779.9 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | Missing
CA1200643 | BEACH CREEK MOBILE HOME PARK | 67 | 24 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK | N/A | 0 | No | 39014.5745 | N/A | 0 | 0 | No | 60516.6 | 99531.1745 | 49765.5872 | 199062.349 | Not At-Risk | SDAC
CA1410001 | BISHOP, CITY OF | 3879 | 1158 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 1485274.2 | 1485274.2 | 742637.1 | 2970548.4 | Not At-Risk | DAC
CA3600022 | BAKER COMMUNITY SERVICES DISTRICT | 1000 | 109 | LPA66 - SAN BERNARDINO COUNTY | C | T - SECONDARY RESIDENCES | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA4900584 | TIMBER COVE COUNTY WATER DISTRICT | 271 | 189 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 73206.5729 | Yes | 0 | 0 | Yes | 0 | 75520.4429 | 37760.2215 | 151040.8858 | Not At-Risk | Non-DAC
CA2000551 | MD 07 MARINA VIEW HEIGHTS | 200 | 83 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 50700.2356 | Yes | 0 | 0 | Yes | 0 | 50700.2356 | 25350.1178 | 101400.4711 | HR2W | Non-DAC
CA4500018 | SALT CREEK SUMMER HOMES | 151 | 47 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 46394.992 | No | 2020300.3019 | 0 | No | 89413.8 | 2157888.994 | 1078944.497 | 4315777.9879 | Not At-Risk | SDAC
CA3400149 | RANCHO MARINA | 250 | 77 | LPA64 - SACRAMENTO COUNTY | C | T - RECREATION AREA | Yes | 0 | No | 71883.6928 | No | 2548243.0429 | 0 | Yes | 0 | 2620126.7357 | 1310063.3678 | 5240253.4714 | At-Risk | SDAC
CA4900543 | SONOMA COUNTY CSA 41-SALMON CREEK | 427 | 99 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 90829.2025 | Yes | 0 | 0 | Yes | 0 | 93143.0725 | 46571.5362 | 186286.145 | Not At-Risk | DAC
CA3010097 | MIDWAY CITY MUTUAL WC | 1285 | 198 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 362869.26 | 362869.26 | 181434.63 | 725738.52 | Not At-Risk | SDAC
CA1910054 | LA CANADA IRRIGATION DIST. | 9300 | 2946 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1109367.8943 | Yes | 0 | 0 | Yes | 0 | 1109367.8943 | 554683.9471 | 2218735.7886 | Not At-Risk | Non-DAC
CA3910003 | ESCALON, CITY OF | 7478 | 2510 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 34132.2 | 34132.2 | 17066.1 | 68264.4 | Not At-Risk | Non-DAC
CA2610003 | BRIDGEPORT PUD | 851 | 258 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 354514.2 | 354514.2 | 177257.1 | 709028.4 | HR2W | Non-DAC
CA2701731 | BRANDON CREEK MWS | 41 | 26 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 47224.4908 | Yes | 0 | 0 | No | 50905.14 | 100443.5008 | 50221.7504 | 200887.0017 | Not At-Risk | DAC
CA1000040 | FCWWD #37/MILE HIGH | 128 | 46 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | DAC
CA4210019 | MISSION HILLS CSD | 3600 | 1271 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 449268.9695 | Yes | 0 | 0 | Yes | 0 | 449268.9695 | 224634.4847 | 898537.939 | Not At-Risk | Non-DAC
CA4900551 | MELITA HEIGHTS MUTUAL WATER COMPANY | 64 | 25 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49822.6991 | No | 0 | 1117672.5 | Yes | 0 | 1169809.0691 | 584904.5345 | 2339618.1381 | At-Risk | DAC
CA5810700 | BEALE AIR FORCE BASE | 7252 | 841 | DISTRICT 21 - VALLEY | C | NT - INSTITUTION | Yes | 0 | No | 670303.8584 | Yes | 0 | 0 | No | 1068149.4 | 1738453.2584 | 869226.6292 | 3476906.5168 | Not At-Risk | Non-DAC
CA2000727 | MD 36 EASTIN ARCOLA | 80 | 16 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 40156.782 | Yes | 0 | 0 | Yes | 0 | 40156.782 | 20078.391 | 80313.5639 | At-Risk | DAC
CA5601110 | MIDDLE ROAD MUTUAL WATER CO | 134 | 48 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA4900560 | KELLY MUTUAL WATER COMPANY | 135 | 41 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 57843.2548 | Yes | 0 | 0 | Yes | 0 | 57843.2548 | 28921.6274 | 115686.5096 | Not At-Risk | DAC
CA2000293 | MD 46 AHWAHNEE RESORTS | 300 | 90 | LPA50 - MADERA COUNTY | C | T - RECREATION AREA | Yes | 0 | No | 59486.4469 | Yes | 0 | 0 | Yes | 0 | 59486.4469 | 29743.2234 | 118972.8938 | At-Risk | SDAC
CA1700579 | VILLA BLUE ESTATES WATER DISTRICT | 60 | 21 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2012436.0416 | 0 | No | 56747.4 | 2070963.3416 | 1035481.6708 | 4141926.6832 | Potentially At-Risk | DAC
CA1009179 | BRITZ/FIVE POINT SYSTEM | 76 | 23 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | No | 39805.3335 | N/A | 0 | 0 | No | 59260.2 | 99065.5335 | 49532.7668 | 198131.067 | Not At-Risk | SDAC
CA3301355 | ANZA RV RESORT | 120 | 101 | LPA63 - RIVERSIDE COUNTY | C | T - OTHER TRANSIENT AREA | No | 2349.468 | No | 56980.6049 | Yes | 0 | 0 | No | 207582.408 | 266912.4809 | 133456.2404 | 533824.9617 | Not At-Risk | Missing
CA3500505 | THOUSAND TRAILS SAN BENITO PRESERVE | 1025 | 365 | DISTRICT 05 - MONTEREY | C | T - RECREATION AREA | No | 2313.87 | No | 158382.6159 | Yes | 0 | 0 | No | 635633.7 | 796330.1859 | 398165.0929 | 1592660.3717 | Not At-Risk | Non-DAC
CA1800523 | PINEVIEW MOBILE HOME PARK | 113 | 52 | DISTRICT 02 - LASSEN | C | R - MOBILE HOME PARK | No | 1779.9 | No | 43056.2317 | No | 0 | 1196605.83 | No | 95695.8 | 1337137.7617 | 668568.8809 | 2674275.5234 | Potentially At-Risk | Non-DAC
CA3600270 | GOLDEN STATE WATER MORONGO DELNORTE | 870 | 165 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 140872.9519 | Yes | 0 | 0 | Yes | 0 | 140872.9519 | 70436.4759 | 281745.9037 | Not At-Risk | SDAC
CA2000552 | MD 24 TEAFORD MEADOW LAKES | 150 | 66 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 46307.1299 | Yes | 0 | 0 | Yes | 0 | 46307.1299 | 23153.5649 | 92614.2598 | HR2W | DAC
CA3700936 | RANCHO ESTATES MUTUAL WATER CO. | 200 | 89 | LPA67 - SAN DIEGO COUNTY | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 66151.7359 | Yes | 0 | 0 | Yes | 0 | 66151.7359 | 33075.868 | 132303.4718 | Not At-Risk | SDAC
CA1500209 | ALTA SIERRA MUTUAL WATER CO. | 143 | 225 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 45692.0951 | Yes | 0 | 0 | No | 310540.2 | 358012.1951 | 179006.0975 | 716024.3902 | Not At-Risk | Missing
CA4500063 | CEDAR CREEK MOBILEHOME PARK | 40 | 20 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 55491 | 55491 | 27745.5 | 110982 | Not At-Risk | SDAC
CA2701367 | TIERRA MEADOWS HOA WS | 63 | 21 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49709.7335 | Yes | 0 | 0 | No | 73771.62 | 125795.2235 | 62897.6117 | 251590.447 | Not At-Risk | Non-DAC
CA4710006 | MCCLOUD C.S.D. | 1300 | 730 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | No | 147348.5602 | Yes | 0 | 0 | No | 947535 | 1094883.5602 | 547441.7801 | 2189767.1203 | At-Risk | SDAC
CA0910006 | GRIZZLY FLATS COMMUNITY SERVIC | 1300 | 621 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | DAC
CA2000524 | SKY ACRES MUTUAL WATER CORP | 175 | 64 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 48503.6827 | Yes | 0 | 0 | No | 110772.6 | 161056.1827 | 80528.0914 | 322112.3654 | At-Risk | SDAC
CA3301682 | TRAILS END MUTUAL WATER COMPANY | 52 | 34 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 49185.1435 | No | 2526751.3156 | 0 | No | 96466.392 | 2674752.3191 | 1337376.1595 | 5349504.6382 | Not At-Risk | DAC
CA2800625 | ADVENTIST HEALTH - ST. HELENA HOSPITAL | 860 | 227 | DISTRICT 03 - MENDOCINO | C | NT - MEDICAL FACILITY | Yes | 0 | No | 139743.2961 | Yes | 0 | 0 | Yes | 0 | 139743.2961 | 69871.6481 | 279486.5923 | Not At-Risk | Non-DAC
CA4810024 | SID - BLUE RIDGE OAKS | 53 | 19 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | Non-DAC
CA4810025 | SID - PLEASANT HILLS RANCH | 73 | 27 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 50839.3892 | Yes | 0 | 0 | Yes | 0 | 50839.3892 | 25419.6946 | 101678.7784 | Potentially At-Risk | Non-DAC
CA1502569 | FIRST MUTUAL WATER SYSTEM | 35 | 13 | DISTRICT 19 - TEHACHAPI | C | RESIDENTIAL AREA | N/A | 0 | N/A | 0 | No | 0 | 805834.02 | Yes | 0 | 805834.02 | 402917.01 | 1611668.04 | HR2W | Non-DAC
CA5402036 | R-RANCH IN THE SEQUOIAS | 330 | 115 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 62122.3103 | Yes | 0 | 0 | No | 174849 | 238751.2103 | 119375.6051 | 477502.4206 | At-Risk | SDAC
CA4900558 | BELMONT TERRACE MUTUAL WATER COMPANY | 244 | 87 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 181570.74 | 181570.74 | 90785.37 | 363141.48 | Not At-Risk | Non-DAC
CA3600087 | DEER LODGE WATER SYSTEM | 745 | 193 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 126752.2551 | Yes | 0 | 0 | Yes | 0 | 126752.2551 | 63376.1275 | 253504.5102 | Not At-Risk | Non-DAC
CA1910025 | LOS ANGELES CWWD 40, REG. 39-ROCK CREEK | 1326 | 350 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | Yes | 0 | No | 195235.4056 | Yes | 0 | 0 | Yes | 0 | 195235.4056 | 97617.7028 | 390470.8112 | Not At-Risk | SDAC
CA4900532 | SONOMA COUNTY CSA 41-JENNER | 406 | 123 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 88456.9254 | N/A | 0 | 0 | Yes | 0 | 88456.9254 | 44228.4627 | 176913.8509 | HR2W | SDAC
CA3900637 | BIG WHEEL MOBILE HOME PARK | 120 | 63 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 43671.2665 | Yes | 0 | 0 | No | 109516.2 | 154967.3665 | 77483.6832 | 309934.733 | At-Risk | SDAC
CA4900562 | DIAMOND A MUTUAL WATER COMPANY | 420 | 190 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 90038.4435 | Yes | 0 | 0 | Yes | 0 | 90038.4435 | 45019.2217 | 180076.8869 | Not At-Risk | Non-DAC
CA3710011 | JACUMBA COMMUNITY SD | 561 | 248 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 107536.4648 | Yes | 0 | 0 | Yes | 0 | 107536.4648 | 53768.2324 | 215072.9297 | Potentially At-Risk | SDAC
CA4300992 | GOLDEN HEIGHTS MUTUAL WATER COMPANY | 66 | 21 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 50790.0914 | Yes | 0 | 0 | No | 69931.224 | 120721.3154 | 60360.6577 | 241442.6308 | Not At-Risk | Non-DAC
CA4000631 | ALMIRA WATER ASSOCIATION | 40 | 20 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 47111.5253 | No | 0 | 1057208.25 | Yes | 0 | 1106633.6453 | 553316.8226 | 2213267.2905 | HR2W | Non-DAC
CA2701570 | LOS CARNEROS MWA | 105 | 24 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 54454.2876 | No | 2500242.9523 | 0 | No | 78671.58 | 2635682.6899 | 1317841.345 | 5271365.3798 | At-Risk | Non-DAC
CA5810006 | NORTH YUBA WATER DISTRICT | 2772 | 785 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 31619.4 | 31619.4 | 15809.7 | 63238.8 | Not At-Risk | DAC
CA3610011 | CEDARPINES PARK MWC | 2511 | 739 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA4000653 | RANCHO COLINA MOBILE HOME PARK | 250 | 127 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 135837.78 | 138151.65 | 69075.825 | 276303.3 | Potentially At-Risk | Non-DAC
CA3810003 | HHW&P MOCCASIN COMPOUND-SFPUC | 150 | 81 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 94807.944 | 94807.944 | 47403.972 | 189615.888 | Not At-Risk | Non-DAC
CA1500579 | LIFE WATER CO-OP | 27 | 18 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 35500.09 | Yes | 0 | 0 | Yes | 0 | 37279.99 | 18639.995 | 74559.9799 | Potentially At-Risk | Non-DAC
CA5602104 | DEL NORTE MUTUAL WATER CO. | 211 | 84 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 67412.7664 | Yes | 0 | 0 | Yes | 0 | 67412.7664 | 33706.3832 | 134825.5329 | Not At-Risk | Missing
CA1300514 | COYOTE VALLEY MUTUAL WATER CO | 125 | 124 | LPA43 - IMPERIAL COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA0510009 | BLUE LAKE SPRINGS MUT WTR | 4600 | 1714 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA4800561 | SNUG HARBOR RESORT | 125 | 110 | DISTRICT 04 - SAN FRANCISCO | C | T - RECREATION AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 215870.46 | 218184.33 | 109092.165 | 436368.66 | Potentially At-Risk | DAC
CA5000389 | MONTEREY PARK TRACT CSD | 186 | 51 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | SDAC
CA1900794 | ANTELOPE PARK MUTUAL WATER COMPANY | 445 | 145 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 94238.3248 | Yes | 0 | 0 | No | 280554.12 | 374792.4448 | 187396.2224 | 749584.8896 | Potentially At-Risk | SDAC
CA1710011 | BUCKINGHAM PARK WATER DISTRICT | 1501 | 457 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA0400041 | FOREST RANCH MOBILE PARK | 25 | 16 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2009411.3261 | 0 | No | 50465.4 | 2061656.6261 | 1030828.313 | 4123313.2522 | Not At-Risk | Missing
CA5610069 | VENTURA CWWD NO. 38 - LAKE SHERWOOD | 1527 | 777 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 218277.8724 | N/A | 0 | 0 | Yes | 0 | 218277.8724 | 109138.9362 | 436555.7448 | Not At-Risk | Non-DAC
CA1810002 | WESTWOOD C.S.D. | 1662 | 949 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 31619.4 | 31619.4 | 15809.7 | 63238.8 | Potentially At-Risk | SDAC
CA5010009 | KEYES COMMUNITY SERVICES DIST. | 5999 | 1370 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | No | 560212.6305 | Yes | 0 | 0 | Yes | 0 | 560212.6305 | 280106.3152 | 1120425.2609 | HR2W | DAC
CA3600196 | CSA 70 W-4 PIONEERTOWN | 400 | 120 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA2700702 | PRUNEDALE MWC | 277 | 84 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 73884.3664 | Yes | 0 | 0 | No | 152170.98 | 228369.2164 | 114184.6082 | 456738.4327 | Not At-Risk | Non-DAC
CA2700772 | STRUVE RD WS #02 | 166 | 105 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 61345.1876 | No | 2506779.7947 | 0 | No | 210970.5 | 2781409.3523 | 1390704.6761 | 5562818.7046 | HR2W | DAC
CA4900673 | ATHENA TERRACE MUTUAL WATER COMPANY | 74 | 23 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 50952.3548 | Yes | 0 | 0 | No | 73771.62 | 127037.8448 | 63518.9224 | 254075.6896 | Not At-Risk | Non-DAC
CA3110036 | NORTH TAHOE PUD - DOLLAR COVE | 800 | 273 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA2701882 | CAL AM WATER COMPANY - BISHOP | 704 | 390 | DISTRICT 05 - MONTEREY | C | RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA0400026 | MEADOWBROOK OAKS | 50 | 26 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 37520.9186 | No | 2011571.8372 | 0 | No | 63029.4 | 2113902.0557 | 1056951.0279 | 4227804.1115 | Potentially At-Risk | Missing
CA0310008 | CAMANCHE NORTH SHORE INC. | 1184 | 211 | DISTRICT 10 - STOCKTON | C | T - RECREATION AREA | Yes | 0 | No | 137156.555 | Yes | 0 | 0 | No | 295463.4 | 432619.955 | 216309.9775 | 865239.91 | Not At-Risk | DAC
CA5510028 | TUD-APPLE VALLEY ESTATES | 507 | 245 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 77673.9043 | Yes | 0 | 0 | Yes | 0 | 77673.9043 | 38836.9522 | 155347.8087 | Not At-Risk | Non-DAC
CA5500104 | CASCADE ESTATES | 316 | 113 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK | Yes | 0 | No | 60892.2407 | Yes | 0 | 0 | Yes | 0 | 60892.2407 | 30446.1203 | 121784.4814 | Not At-Risk | SDAC
CA1900529 | CAMP WILLIAMS-RESORT WATER | 80 | 69 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | Yes | 0 | Yes | 0 | 0 | No | 59980.536 | 62330.004 | 31165.002 | 124660.008 | Not At-Risk | Missing
CA4500247 | WEST COTTONWOOD APARTMENTS | 35 | 17 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36202.9869 | No | 2010275.5305 | 0 | No | 51721.8 | 2099980.2174 | 1049990.1087 | 4199960.4348 | Not At-Risk | Non-DAC
CA0400004 | FOREST RANCH MUTUAL WATER SYSTEM | 92 | 42 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2015201.4958 | 0 | Yes | 0 | 2015201.4958 | 1007600.7479 | 4030402.9916 | Potentially At-Risk | Missing
CA4110005 | GUADALUPE VALLEY MID | 1401 | 752 | DISTRICT 17 - SANTA CLARA | C | NT - INDUSTRIAL/AGRICULTURAL | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA5000090 | RIVERVIEW MOBILE HOME ESTATES | 250 | 175 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 55093.3412 | Yes | 0 | 0 | No | 250233 | 305326.3412 | 152663.1706 | 610652.6824 | HR2W | SDAC
CA1010028 | RIVERDALE PUBLIC UTILITY DISTRICT | 3145 | 928 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 309454.1592 | Yes | 0 | 0 | Yes | 0 | 309454.1592 | 154727.0796 | 618908.3183 | At-Risk | SDAC
CA5010023 | CITY OF MODESTO - SOUTH TURLOCK | 1079 | 332 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | No | 127931.0331 | Yes | 0 | 0 | No | 32875.8 | 160806.8331 | 80403.4166 | 321613.6663 | At-Risk | SDAC
CA4200924 | EL RANCHO TAJIGUAS | 40 | 20 | LPA72 - SANTA BARBARA COUNTY | C | NT - INDUSTRIAL/AGRICULTURAL | Yes | 0 | No | 47111.5253 | Yes | 0 | 0 | No | 72138.3 | 119249.8253 | 59624.9126 | 238499.6505 | Not At-Risk | SDAC
CA1500398 | FRONTIER TRAILS HOMEOWNERS ASSOC INC. | 32 | 32 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 35939.4005 | Yes | 0 | 0 | Yes | 0 | 35939.4005 | 17969.7003 | 71878.801 | Not At-Risk | Missing
CA5200531 | RIVER POINTE LANDING MHP | 104 | 40 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 42265.4727 | No | 2016238.5411 | 0 | Yes | 0 | 2060283.9138 | 1030141.9569 | 4120567.8276 | Not At-Risk | SDAC
CA1510045 | GOLDEN HILLS CSD | 9640 | 2921 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 880118.5849 | Yes | 0 | 0 | Yes | 0 | 880118.5849 | 440059.2925 | 1760237.1699 | Not At-Risk | Non-DAC
CA1500393 | RAINBIRD VALLEY MUTUAL WATER COMPANY | 238 | 85 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 54038.9959 | Yes | 0 | 0 | Yes | 0 | 55818.8959 | 27909.4479 | 111637.7917 | HR2W | SDAC
CA0300011 | SUTTER PINES MHP | 40 | 19 | DISTRICT 10 - STOCKTON | C | R - MOBILE HOME PARK | No | 1779.9 | No | 36642.2974 | No | 2010707.6327 | 0 | No | 54234.6 | 2103364.4302 | 1051682.2151 | 4206728.8603 | Potentially At-Risk | Non-DAC
CA3310080 | LAKE HEMET MWD-CAMP GROUND | 600 | 287 | DISTRICT 20 - RIVERSIDE | C | R - MOBILE HOME PARK | Yes | 0 | Yes | 0 | No | 2586233.4698 | 0 | No | 516053.736 | 3102287.2058 | 1551143.6029 | 6204574.4115 | Not At-Risk | DAC
CA0410009 | DEL ORO WATER CO.-MAGALIA | 297 | 90 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA3500006 | CSA NO. 31 STONEGATE WS | 252 | 77 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 71060.227 | Yes | 0 | 0 | Yes | 0 | 71060.227 | 35530.1135 | 142120.454 | Potentially At-Risk | Non-DAC
CA4900846 | ROLLING OAKS ROAD ASSOCIATION | 25 | 16 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 45417.0417 | Yes | 0 | 0 | Yes | 0 | 47730.9117 | 23865.4558 | 95461.8233 | Potentially At-Risk | Non-DAC
CA5500243 | RAMBLING HILLS ESTATES | 78 | 38 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK | Yes | 0 | No | 39981.0577 | Yes | 0 | 0 | Yes | 0 | 39981.0577 | 19990.5289 | 79962.1155 | Not At-Risk | SDAC
CA3000585 | PAGE AVENUE MUTUAL WATER COMPANY | 115 | 36 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 55583.9433 | Yes | 0 | 0 | Yes | 0 | 55583.9433 | 27791.9717 | 111167.8867 | Potentially At-Risk | SDAC
CA4400764 | MOUNT MADONNA CENTER | 165 | 31 | LPA74 - SANTA CRUZ COUNTY | C | T - SUMMER CAMP | Yes | 0 | No | 61232.222 | Yes | 0 | 0 | Yes | 0 | 61232.222 | 30616.111 | 122464.4441 | Not At-Risk | Non-DAC
CA5700571 | MADISON SERVICE DIST | 876 | 149 | LPA87 - YOLO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 217566.6 | 217566.6 | 108783.3 | 435133.2 | At-Risk | SDAC
CA1400078 | SCE BISHOP CREEK PLANT 4 | 38 | 15 | DISTRICT 13 - SAN BERNARDINO | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | No | 36466.5732 | No | 2010534.7918 | 0 | No | 49209 | 2097990.2651 | 1048995.1325 | 4195980.5301 | At-Risk | Non-DAC
CA5610035 | RIO MANOR MUTUAL WATER CO | 983 | 295 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 155914.1812 | Yes | 0 | 0 | Yes | 0 | 158263.6492 | 79131.8246 | 316527.2984 | Potentially At-Risk | Non-DAC
CA3310051 | MYOMA DUNES MUTUAL WATER COMPANY | 8948 | 2551 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 1069014.9176 | Yes | 0 | 0 | Yes | 0 | 1069014.9176 | 534507.4588 | 2138029.8352 | Not At-Risk | Non-DAC
CA2700594 | HIDDEN VALLEY WA | 164 | 32 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 61119.2565 | Yes | 0 | 0 | No | 91738.14 | 155171.2665 | 77585.6332 | 310342.5329 | Potentially At-Risk | Non-DAC
CA4900561 | WILLOWSIDE MUTUAL WATER COMPANY | 350 | 160 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 238736.94 | 241050.81 | 120525.405 | 482101.62 | Not At-Risk | Non-DAC
CA2810001 | HOWELL MOUNTAIN MUTUAL WATER COMPANY | 2070 | 391 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | Non-DAC
CA3900831 | ARBOR MOBILE HOME PARK WS | 340 | 173 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 63000.9314 | No | 2036633.7657 | 0 | Yes | 0 | 2101414.5972 | 1050707.2986 | 4202829.1943 | Potentially At-Risk | Non-DAC
CA1910029 | CITY OF INDUSTRY WATERWORKS SYSTEMS | 6151 | 1864 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA | Yes | 0 | No | 748369.2478 | Yes | 0 | 0 | Yes | 0 | 748369.2478 | 374184.6239 | 1496738.4957 | Not At-Risk | Non-DAC
CA1510800 | CCI - TEHACHAPI | 4482 | 1806 | DISTRICT 19 - TEHACHAPI | C | NT - INSTITUTION | Yes | 0 | No | 426925.8046 | Yes | 0 | 0 | No | 2299421.4 | 2726347.2046 | 1363173.6023 | 5452694.4093 | Not At-Risk | Non-DAC
CA4010024 | SLO CWWD NO. 23 - SANTA MARGARITA | 1259 | 503 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 184816.5602 | Yes | 0 | 0 | Yes | 0 | 184816.5602 | 92408.2801 | 369633.1205 | Not At-Risk | DAC
CA1100445 | ORLAND MOBILE H.P. | 178 | 54 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 48767.2691 | No | 2022633.6539 | 0 | No | 50465.4 | 2123646.223 | 1061823.1115 | 4247292.446 | Not At-Risk | SDAC
CA1500458 | R.S. MUTUAL WATER COMPANY | 67 | 24 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39014.5745 | No | 2013040.9847 | 0 | No | 60516.6 | 2114352.0592 | 1057176.0296 | 4228704.1184 | HR2W | Missing
CA1500466 | A.F.P. MUTUAL WATER COMPANY | 710 | 216 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 95509.9133 | Yes | 0 | 0 | Yes | 0 | 95509.9133 | 47754.9567 | 191019.8267 | Not At-Risk | Non-DAC
CA5100107 | SUTTER CO. WWD#1 (ROBBINS) | 339 | 94 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 62913.0693 | Yes | 0 | 0 | Yes | 0 | 64692.9693 | 32346.4847 | 129385.9386 | HR2W | SDAC
CA4400621 | RIVER GROVE MUTUAL WATER ASSN | 54 | 25 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | No | 0 | 1117672.5 | Yes | 0 | 1117672.5 | 558836.25 | 2235345 | At-Risk | Non-DAC
CA5110001 | CITY OF LIVE OAK | 8912 | 2407 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 816154.9665 | Yes | 0 | 0 | Yes | 0 | 817934.8665 | 408967.4332 | 1635869.7329 | At-Risk | DAC
CA3600226 | CSA 70-F MORONGO | 450 | 84 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | SDAC
CA2700731 | Z RANCH MWC | 62 | 27 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49596.7679 | Yes | 0 | 0 | Yes | 0 | 51910.6379 | 25955.319 | 103821.2758 | Not At-Risk | Non-DAC
CA4300517 | CHEMEKETA PARK MUTUAL WATER COMPANY | 346 | 153 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | No | 293821.704 | 293821.704 | 146910.852 | 587643.408 | Not At-Risk | Non-DAC
CA4300979 | QUAIL CREEK ESTATES MUTUAL WATER COMPANY | 55 | 39 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 2349.468 | 1174.734 | 4698.936 | At-Risk | Non-DAC
CA4500014 | LAKESHORE HEIGHTS MUTUAL WATER | 264 | 66 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | No | 56323.4108 | N/A | 0 | 0 | Yes | 0 | 56323.4108 | 28161.7054 | 112646.8216 | At-Risk | SDAC
CA0610002 | CITY OF COLUSA | 6175 | 2205 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 575676.3624 | Yes | 0 | 0 | Yes | 0 | 575676.3624 | 287838.1812 | 1151352.7248 | HR2W | DAC
CA4000789 | SPANISH LAKES MUTUAL WATER CO | 125 | 45 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 56713.5991 | Yes | 0 | 0 | Yes | 0 | 56713.5991 | 28356.7995 | 113427.1982 | Not At-Risk | Non-DAC
CA4510004 | SHASTA CSA - JONES VALLEY, #6 | 1119 | 479 | DISTRICT 02 - LASSEN | C | O - OTHER AREA | N/A | 0 | No | 131445.5177 | N/A | 0 | 0 | Yes | 0 | 131445.5177 | 65722.7588 | 262891.0353 | At-Risk | DAC
CA1000042 | FCWWD #40 / SHAVER SPRINGS | 193 | 70 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | DAC
CA5610058 | CRESTVIEW MUTUAL WATER CO | 2040 | 620 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 277087.7504 | Yes | 0 | 0 | Yes | 0 | 277087.7504 | 138543.8752 | 554175.5007 | Not At-Risk | Non-DAC
CA4010019 | TEMPLETON CSD | 9322 | 2957 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1095657.9852 | Yes | 0 | 0 | Yes | 0 | 1095657.9852 | 547828.9926 | 2191315.9703 | Not At-Risk | Non-DAC
CA3200104 | GRIZZLY LAKE CSD-DELLEKER | 657 | 350 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 90853.2213 | Yes | 0 | 0 | Yes | 0 | 90853.2213 | 45426.6107 | 181706.4427 | HR2W | DAC
CA4900721 | COLONIAL PARK | 342 | 194 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 356335.98 | 358649.85 | 179324.925 | 717299.7 | Not At-Risk | Missing
CA3200107 | GRIZZLY LAKE CSD-CROCKER/WELCH | 215 | 70 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 52018.1673 | Yes | 0 | 0 | Yes | 0 | 52018.1673 | 26009.0836 | 104036.3345 | Not At-Risk | DAC
CA1502750 | RIVERVIEW HOMEOWNERS ASSOCIATION | 40 | 20 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36642.2974 | No | 2010707.6327 | 0 | Yes | 0 | 2049129.8302 | 1024564.9151 | 4098259.6603 | Potentially At-Risk | DAC
CA1510802 | KERN VALLEY STATE PRISON | 5000 | 2249 | DISTRICT 12 - VISALIA | C | NT - INSTITUTION | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 2856006.6 | 2856006.6 | 1428003.3 | 5712013.2 | At-Risk | DAC
CA1910075 | LOS ANGELES CWWD 21-KAGEL CANYON | 559 | 250 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | N/A | 0 | No | 107307.1866 | N/A | 0 | 0 | Yes | 0 | 107307.1866 | 53653.5933 | 214614.3731 | Not At-Risk | Non-DAC
CA2801080 | MILTON ROAD WATER COMPANY | 55 | 24 | LPA58 - NAPA COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 2313.87 | No | 48806.0089 | No | 0 | 1105579.65 | Yes | 0 | 1156699.5289 | 578349.7644 | 2313399.0578 | At-Risk | Non-DAC
CA2000527 | YOSEMITE FORKS EST MUTUAL | 110 | 99 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 42792.6454 | Yes | 0 | 0 | No | 154746.6 | 199319.1454 | 99659.5727 | 398638.2907 | HR2W | SDAC
CA3010008 | EASTSIDE WATER ASSOCIATION | 2000 | 333 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 268524.0507 | Yes | 0 | 0 | No | 583367.46 | 851891.5107 | 425945.7554 | 1703783.0215 | Not At-Risk | DAC
CA4901071 | BOULEVARD HEIGHTS MUTUAL WATER | 60 | 18 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49370.8368 | Yes | 0 | 0 | Yes | 0 | 51684.7068 | 25842.3534 | 103369.4135 | Not At-Risk | Non-DAC
CA2110006 | NORTH MARIN WD - PT. REYES | 1700 | 764 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA2702004 | CAL AM WATER COMPANY - RALPH LANE | 96 | 27 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | No | 2499278.5002 | 0 | Yes | 0 | 2499278.5002 | 1249639.2501 | 4998557.0004 | Potentially At-Risk | Missing
CA1810004 | LEAVITT LAKE CSD | 950 | 259 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 31619.4 | 31619.4 | 15809.7 | 63238.8 | Not At-Risk | DAC
CA2300730 | WESTPORT COUNTY WATER DISTRICT | 369 | 73 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 65548.9327 | Yes | 0 | 0 | Yes | 0 | 67328.8327 | 33664.4164 | 134657.6654 | Not At-Risk | SDAC
CA3710750 | NAS NORTH ISLAND & NAB CORONADO | 6000 | 1663 | DISTRICT 14 - SAN DIEGO | C | O - OTHER AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | No | 1363520.664 | 1363520.664 | 681760.332 | 2727041.328 | Not At-Risk | Non-DAC
CA3610108 | GOLDEN STATE WATER CO - LUCERNE | 751 | 317 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 127430.0485 | Yes | 0 | 0 | Yes | 0 | 127430.0485 | 63715.0243 | 254860.0971 | Not At-Risk | SDAC
CA1710003 | HIGHLANDS MUTUAL WATER COMPANY | 9494 | 2878 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES | N/A | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | SDAC
CA3110011 | TAHOE CITY PUD - MCKINNEY/QUAIL | 844 | 559 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA3600209 | ROCKY COMFORT MUTUAL WATER CO | 160 | 33 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA4500246 | EL RIO ESTATES | 434 | 155 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 71259.9701 | Yes | 0 | 0 | No | 225105 | 298144.8701 | 149072.435 | 596289.7401 | Not At-Risk | DAC
CA2700536 | CORRAL DE TIERRA ESTATES WC | 45 | 16 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 47676.3531 | Yes | 0 | 0 | No | 65605.02 | 115595.2431 | 57797.6216 | 231190.4863 | HR2W | Non-DAC
CA1910064 | LITTLEROCK CREEK IRRIGATION DIST. | 3488 | 1352 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA | Yes | 0 | No | 443085.2226 | Yes | 0 | 0 | Yes | 0 | 443085.2226 | 221542.6113 | 886170.4452 | Not At-Risk | DAC
CA2000737 | MD 42 STILL MEADOW | 100 | 34 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 41914.0242 | Yes | 0 | 0 | Yes | 0 | 41914.0242 | 20957.0121 | 83828.0485 | HR2W | SDAC
CA5000099 | DEL RIO EAST HOA WATER SYSTEM | 110 | 55 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 42792.6454 | Yes | 0 | 0 | Yes | 0 | 44572.5454 | 22286.2727 | 89145.0907 | Not At-Risk | Non-DAC
CA3310029 | PERRIS, CITY OF | 7854 | 2596 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA0800825 | JED SMITH HOMEOWNERS ASSN. | 58 | 27 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 38223.8155 | Yes | 0 | 0 | Yes | 0 | 40003.7155 | 20001.8577 | 80007.4309 | HR2W | DAC
CA3900732 | V & P TRAILER COURT WATER SYSTEM | 35 | 15 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 36202.9869 | No | 0 | 825873.6 | Yes | 0 | 863856.4869 | 431928.2434 | 1727712.9737 | At-Risk | DAC
CA1400010 | ROLLING GREEN UTILITIES, INC. | 1225 | 285 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | DAC
CA0400091 | DEL ORO WATER COMPANY - BUZZTAIL DIST. | 99 | 30 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 41826.1621 | No | 2015806.4389 | 0 | Yes | 0 | 2057632.601 | 1028816.3005 | 4115265.202 | Not At-Risk | Non-DAC
CA5210001 | CITY OF CORNING | 7663 | 2378 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 706415.187 | Yes | 0 | 0 | No | 42927 | 749342.187 | 374671.0935 | 1498684.3739 | Not At-Risk | DAC
CA4000650 | MESA DUNES MOBILE HOME ESTATES | 600 | 313 | DISTRICT 06 - SANTA BARBARA | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 47638.5 | 47638.5 | 23819.25 | 95277 | Not At-Risk | Non-DAC
CA4410008 | MT. HERMON ASSOCIATION, INC. | 2850 | 494 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 364544.7888 | Yes | 0 | 0 | Yes | 0 | 364544.7888 | 182272.3944 | 729089.5776 | Not At-Risk | Non-DAC
CA5510002 | TUD - PONDEROSA | 1647 | 640 | DISTRICT 11 - MERCED | C | O - WHOLESALER (SELLS WATER) | N/A | 0 | No | 177836.7135 | N/A | 0 | 0 | Yes | 0 | 177836.7135 | 88918.3567 | 355673.4269 | Not At-Risk | Non-DAC
CA5200545 | MODERN VILLAGE MWC | 85 | 19 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 40596.0925 | No | 0 | 865952.76 | No | 54234.6 | 962563.3525 | 481281.6763 | 1925126.7051 | Not At-Risk | SDAC
CA1500540 | PINON VALLEY WATER COMPANY | 109 | 39 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2016670.6433 | 0 | Yes | 0 | 2016670.6433 | 1008335.3217 | 4033341.2867 | At-Risk | SDAC
CA3600010 | LIBERTY UTILITIES APPLE VALLEY | 170 | 50 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 61797.0499 | Yes | 0 | 0 | Yes | 0 | 61797.0499 | 30898.525 | 123594.0998 | Not At-Risk | SDAC
CA4510008 | FALL RIVER VALLEY CSD | 1535 | 482 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 167996.1568 | Yes | 0 | 0 | Yes | 0 | 167996.1568 | 83998.0784 | 335992.3136 | Not At-Risk | SDAC
CA3610063 | GOLDEN STATE WATER CO - MORONGO DEL SUR | 1748 | 818 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 240056.726 | Yes | 0 | 0 | No | 44371.86 | 284428.586 | 142214.293 | 568857.1721 | Potentially At-Risk | DAC
CA0400012 | FARM LABOR HOUSING | 460 | 135 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2047004.2189 | 0 | Yes | 0 | 2048784.1189 | 1024392.0595 | 4097568.2379 | At-Risk | Non-DAC
CA5400505 | HARTLAND CHRISTIAN CAMP | 250 | 54 | DISTRICT 24 - TULARE | C | T - RECREATION AREA | Yes | 0 | No | 55093.3412 | No | 2028855.9258 | 0 | No | 98208.6 | 2182157.8671 | 1091078.9335 | 4364315.7341 | Potentially At-Risk | DAC
CA4810021 | CITY OF VALLEJO-LAKES SYSTEM | 2800 | 854 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 358896.5101 | Yes | 0 | 0 | Yes | 0 | 358896.5101 | 179448.2551 | 717793.0202 | Not At-Risk | Non-DAC
CA4500203 | RAPID RIVER MOBILEHOME PARK | 92 | 44 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 41211.1273 | No | 2015201.4958 | 0 | No | 85644.6 | 2143837.1231 | 1071918.5616 | 4287674.2462 | Not At-Risk | SDAC
CA3110033 | CASTLE CITY MHP | 280 | 201 | District 2_Lassen | NP/C | MOBILE HOME PARK | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 282899.4 | 282899.4 | 141449.7 | 565798.8 | Not At-Risk | Non-DAC
CA4900723 | SHAMROCK MOBILE HOME PARK | 188 | 127 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | No | 2313.87 | No | 63830.4303 | No | 0 | 2351143.2 | No | 246903.54 | 2664191.0403 | 1332095.5201 | 5328382.0805 | At-Risk | DAC
CA4000802 | SANTA YSABEL RANCH MWC | 238 | 151 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 69478.709 | Yes | 0 | 0 | No | 111337.98 | 183130.559 | 91565.2795 | 366261.1179 | Not At-Risk | Non-DAC
CA2800530 | MEYERS WATER CO. | 250 | 92 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 0 | 1927893.45 | No | 189737.34 | 2117630.79 | 1058815.395 | 4235261.58 | HR2W | Non-DAC
CA3301380 | SAINT ANTHONY TRAILER PARK | 340 | 68 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 82201.2153 | No | 0 | 1656381.222 | No | 152853.624 | 1893785.5293 | 946892.7646 | 3787571.0586 | HR2W | SDAC
CA4900798 | MOUNTAIN VIEW MOBILE ESTATES, LLC | 250 | 111 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | DAC
CA4900553 | PARK ROYAL MUTUAL WATER COMPANY | 75 | 27 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 51065.3204 | Yes | 0 | 0 | Yes | 0 | 51065.3204 | 25532.6602 | 102130.6407 | HR2W | Non-DAC
CA2900541 | CHRISTIAN ENCOUNTER MINISTRIES | 35 | 16 | LPA59 - NEVADA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36202.9869 | No | 2010275.5305 | 0 | Yes | 0 | 2048258.4174 | 1024129.2087 | 4096516.8348 | Potentially At-Risk | Non-DAC
CA3301491 | ALPINE VILLAGE | 198 | 60 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 65922.4576 | Yes | 0 | 0 | Yes | 0 | 68271.9256 | 34135.9628 | 136543.8513 | HR2W | SDAC
CA3301676 | THOMAS MOUNTAIN WATER COMPANY | 162 | 57 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 61795.4487 | No | 2538691.1641 | 0 | Yes | 0 | 2600486.6128 | 1300243.3064 | 5200973.2255 | Not At-Risk | DAC
CA4300522 | LAKE CANYON MUTUAL WATER COMPANY | 156 | 56 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 61107.6138 | Yes | 0 | 0 | Yes | 0 | 61107.6138 | 30553.8069 | 122215.2277 | Not At-Risk | Non-DAC
CA1100452 | SHADY OAKS TRAILER PARK | 57 | 43 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2012176.7803 | 0 | No | 84388.2 | 2098344.8803 | 1049172.4401 | 4196689.7605 | Not At-Risk | SDAC
CA2000690 | MD 73 QUARTZ MOUNTAIN | 375 | 127 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 66076.1054 | Yes | 0 | 0 | Yes | 0 | 66076.1054 | 33038.0527 | 132152.2108 | HR2W | DAC
CA2600714 | WHEELER CREST CSD | 86 | 43 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 40683.9546 | Yes | 0 | 0 | Yes | 0 | 40683.9546 | 20341.9773 | 81367.9093 | Not At-Risk | Non-DAC
CA2210001 | MARIPOSA PUBLIC UTILITY DIST | 2000 | 677 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 208852.0395 | Yes | 0 | 0 | Yes | 0 | 208852.0395 | 104426.0197 | 417704.0789 | Not At-Risk | SDAC
CA0707623 | WILCOX STATION RANCH | 90 | 15 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | No | 0 | 996744 | No | 63971.7 | 1063029.57 | 531514.785 | 2126059.14 | Potentially At-Risk | Non-DAC
CA5000313 | BUEHNER WATER SYSTEM | 150 | 50 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 46307.1299 | Yes | 0 | 0 | No | 93183 | 141270.0299 | 70635.0149 | 282540.0598 | Not At-Risk | Non-DAC
CA1900146 | SUNNYSIDE FARMS MUTUAL WATER COMPANY | 326 | 158 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 80596.2673 | Yes | 0 | 0 | Yes | 0 | 82945.7353 | 41472.8677 | 165891.4707 | Not At-Risk | Non-DAC
CA1000213 | HARRIS FARMS/HORSE BARN | 100 | 20 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | No | 41914.0242 | N/A | 0 | 0 | No | 55491 | 97405.0242 | 48702.5121 | 194810.0485 | Potentially At-Risk | SDAC
CA5400537 | LINDYS LANDING | 49 | 177 | DISTRICT 24 - TULARE | C | T - RECREATION AREA | No | 1779.9 | No | 37433.0565 | No | 2011485.4167 | 0 | No | 252745.8 | 2303444.1732 | 1151722.0866 | 4606888.3464 | Potentially At-Risk | Missing
CA3610046 | VALLEY VIEW PARK MWC | 499 | 218 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 98962.7238 | Yes | 0 | 0 | Yes | 0 | 101276.5938 | 50638.2969 | 202553.1877 | Not At-Risk | Missing
CA3301280 | GOLDEN ERA PRODUCTIONS | 500 | 30 | LPA63 - RIVERSIDE COUNTY | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 89832.6 | 89832.6 | 44916.3 | 179665.2 | Not At-Risk | SDAC
CA3110003 | FORESTHILL PUBLIC UTILITY DIST | 6000 | 2032 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | Non-DAC
CA1500459 | LAKE OF THE WOODS MOBILE VILLAGE | 82 | 86 | DISTRICT 19 - TEHACHAPI | C | R - MOBILE HOME PARK | Yes | 0 | No | 40332.5062 | No | 2014337.2914 | 0 | No | 138413.4 | 2193083.1975 | 1096541.5988 | 4386166.3951 | At-Risk | SDAC
CA3310048 | COACHELLA VWD: I.D. NO. 8 | 4300 | 1603 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 536172.2029 | Yes | 0 | 0 | Yes | 0 | 536172.2029 | 268086.1014 | 1072344.4057 | Not At-Risk | SDAC
CA3301226 | MWD - EAGLE MOUNTAIN | 16 | 25 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 45058.1345 | N/A | 0 | 0 | No | 81540.36 | 126598.4945 | 63299.2472 | 253196.9889 | Not At-Risk | SDAC
CA4900563 | MISSION HIGHLANDS MUTUAL WATER CO. | 150 | 69 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | Non-DAC
CA3710036 | BORREGO WD | 3429 | 2033 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 436321.5134 | Yes | 0 | 0 | Yes | 0 | 436321.5134 | 218160.7567 | 872643.0269 | Not At-Risk | Non-DAC
CA5500040 | BLUEBELL VALLEY MWC | 282 | 91 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 57904.9288 | Yes | 0 | 0 | Yes | 0 | 57904.9288 | 28952.4644 | 115809.8577 | Potentially At-Risk | Non-DAC
CA4500015 | SHASTA CSA - CASTELLA, #3 | 252 | 101 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | No | 55269.0654 | N/A | 0 | 0 | Yes | 0 | 55269.0654 | 27634.5327 | 110538.1309 | Potentially At-Risk | SDAC
CA0910017 | EL DORADO ID - STRAWBERRY | 400 | 149 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Missing
CA2701046 | CAMPHORA APARTMENTS | 126 | 42 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 2313.87 | No | 56826.5647 | No | 2502493.3407 | 0 | No | 108071.34 | 2669705.1153 | 1334852.5577 | 5339410.2306 | Not At-Risk | SDAC
CA1510801 | WASCO ST. PRISON RECEPTION CTR | 6068 | 1768 | DISTRICT 12 - VISALIA | C | NT - INSTITUTION | No | 1779.9 | No | 566275.1163 | Yes | 0 | 0 | No | 2247909 | 2815964.0163 | 1407982.0081 | 5631928.0326 | HR2W | Missing
CA4000554 | GREEN RIVER MUTUAL WATER CO. | 350 | 124 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 82130.8533 | Yes | 0 | 0 | Yes | 0 | 82130.8533 | 41065.4266 | 164261.7066 | Not At-Risk | Non-DAC
CA5602130 | SOLANO VERDE MUTUAL WATER CO | 100 | 34 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA0210002 | KIRKWOOD MEADOWS PUBLIC UTILITY DISTRICT | 7851 | 863 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 34132.2 | 34132.2 | 17066.1 | 68264.4 | Not At-Risk | DAC
CA5301017 | RUSH CREEK MUTUAL WATER SYSTEM | 104 | 37 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA4200702 | VIEJA MUTUAL WATER COMPANY | 60 | 26 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 49370.8368 | Yes | 0 | 0 | No | 80304.9 | 129675.7368 | 64837.8684 | 259351.4735 | Not At-Risk | Non-DAC
CA2410008 | CAL AM - MEADOWBROOK | 5650 | 1713 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 529548.7529 | Yes | 0 | 0 | Yes | 0 | 529548.7529 | 264774.3765 | 1059097.5059 | Not At-Risk | DAC
CA5010039 | WESTERN HILLS WATER DISTRICT/DIABLO GRAN | 2000 | 596 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | DAC
CA1500380 | DE RANCHO Y MOBILE VILLA WATER | 200 | 90 | DISTRICT 12 - VISALIA | C | R - MOBILE HOME PARK | No | 1779.9 | No | 50700.2356 | N/A | 0 | 0 | No | 143439 | 195919.1356 | 97959.5678 | 391838.2711 | Potentially At-Risk | DAC
CA4410018 | CENTRAL WATER DISTRICT | 2715 | 817 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 349294.4363 | Yes | 0 | 0 | Yes | 0 | 349294.4363 | 174647.2182 | 698588.8726 | Potentially At-Risk | Non-DAC
CA3700968 | SAN PASQUAL ACADEMY | 350 | 64 | LPA67 - SAN DIEGO COUNTY | C | T - SECONDARY RESIDENCES | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 139586.04 | 139586.04 | 69793.02 | 279172.08 | Not At-Risk | Non-DAC
CA1910050 | COMMERCE-CITY, WATER DEPT. | 4203 | 991 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA | Yes | 0 | No | 525052.2065 | Yes | 0 | 0 | Yes | 0 | 525052.2065 | 262526.1032 | 1050104.4129 | Potentially At-Risk | SDAC
CA1510042 | MOUNTAIN MESA WC | 777 | 375 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 101396.6749 | Yes | 0 | 0 | Yes | 0 | 101396.6749 | 50698.3375 | 202793.3498 | Potentially At-Risk | SDAC
CA3600009 | APPLE VALLEY HEIGHTS CWD | 986 | 296 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 153976.9585 | Yes | 0 | 0 | Yes | 0 | 156290.8285 | 78145.4142 | 312581.657 | Not At-Risk | SDAC
CA3710700 | CAMP PENDLETON (NORTH) | 26355 | 1605 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 3064538.3977 | Yes | 0 | 0 | Yes | 0 | 3064538.3977 | 1532269.1988 | 6129076.7953 | Potentially At-Risk | DAC
CA0910018 | EL DORADO ID - OUTINGDALE | 538 | 193 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | DAC
CA4300577 | RANCHO ROBLES MUTUAL WATER COMPANY | 103 | 37 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 55031.7395 | Yes | 0 | 0 | Yes | 0 | 57381.2075 | 28690.6038 | 114762.415 | Not At-Risk | Non-DAC
CA3500509 | TRES PINOS CWD | 350 | 121 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 82130.8533 | No | 2526497.483 | 0 | No | 215870.46 | 2826812.6663 | 1413406.3331 | 5653625.3326 | Not At-Risk | Non-DAC
CA3702354 | WARNER SPRINGS ESTATES | 443 | 307 | DISTRICT 14 - SAN DIEGO | C | R - MOBILE HOME PARK | Yes | 0 | No | 94009.0465 | Yes | 0 | 0 | No | 540930.456 | 634939.5025 | 317469.7513 | 1269879.005 | Not At-Risk | SDAC
CA1000445 | LINDA VISTA FARMS | 63 | 17 | DISTRICT 23 - FRESNO | NP/C | OTHER RESIDENTIAL AREA | Yes | 0 | No | 38663.126 | No | 2012695.3029 | 0 | No | 51721.8 | 2103080.229 | 1051540.1145 | 4206160.4579 | At-Risk | SDAC
CA2800525 | LA TIERRA HEIGHTS MUTUAL | 67 | 19 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | Not At-Risk | DAC
CA5200508 | RIO VISTA MOBILE HOME PARK | 543 | 195 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 80836.9404 | No | 2054177.1157 | 0 | No | 31619.4 | 2168413.3562 | 1084206.6781 | 4336826.7123 | Not At-Risk | SDAC
CA4500173 | CASSEL PARK MUTUAL WATER CO | 131 | 71 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 44637.7497 | Yes | 0 | 0 | Yes | 0 | 44637.7497 | 22318.8749 | 89275.4995 | Not At-Risk | DAC
CA4000805 | CALLENDER GROVE MUTUAL WATER | 30 | 37 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 45981.8695 | Yes | 0 | 0 | Yes | 0 | 48295.7395 | 24147.8698 | 96591.4791 | Not At-Risk | Non-DAC
CA1910249 | WHITE FENCE FARMS MWC NO. 1 | 1362 | 454 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA | Yes | 0 | No | 199362.4146 | Yes | 0 | 0 | Yes | 0 | 199362.4146 | 99681.2073 | 398724.8292 | HR2W | Non-DAC
CA3110150 | CALAM - WEST PLACER | 4561 | 1386 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA0610004 | CITY OF WILLIAMS | 5255 | 1481 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA5410025 | WOODVILLE PUBLIC UTILITY DIST | 1673 | 467 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 180121.1284 | Yes | 0 | 0 | Yes | 0 | 180121.1284 | 90060.5642 | 360242.2568 | HR2W | SDAC
CA3310018 | HOME GARDENS COUNTY WD | 3095 | 874 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA1500096 | OLD RIVER MUTUAL WATER COMPANY | 128 | 14 | DISTRICT 12 - VISALIA | C | RESIDENTIAL AREA | N/A | 0 | N/A | 0 | No | 0 | 815853.81 | N/A | 0 | 815853.81 | 407926.905 | 1631707.62 | HR2W | Non-DAC
CA4900644 | BRIDGEHAVEN PARK | 70 | 31 | DISTRICT 18 - SONOMA | C | T - OTHER TRANSIENT AREA | N/A | 0 | No | 50500.4925 | Yes | 0 | 0 | No | 72138.3 | 122638.7925 | 61319.3962 | 245277.585 | Potentially At-Risk | DAC
CA4910016 | COTATI, CITY OF | 7653 | 2669 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 907118.4418 | Yes | 0 | 0 | Yes | 0 | 907118.4418 | 453559.2209 | 1814236.8836 | Not At-Risk | Non-DAC
CA4200684 | LINCOLNWOOD MUTUAL WATER COMPANY | 206 | 62 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 0 | 1565107.95 | Yes | 0 | 1565107.95 | 782553.975 | 3130215.9 | Not At-Risk | Non-DAC
CA1010035 | DEL REY COMMUNITY SERV DIST | 1500 | 312 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 164920.9828 | Yes | 0 | 0 | No | 422359.8 | 587280.7828 | 293640.3914 | 1174561.5656 | HR2W | SDAC
CA0600008 | COLUSA CO. WWD #1 - GRIMES | 305 | 123 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 59925.7575 | Yes | 0 | 0 | No | 184900.2 | 246605.8575 | 123302.9287 | 493211.7149 | HR2W | SDAC
CA4900641 | SUNRISE MOUNTAIN MUTUAL WATER COMPANY | 100 | 51 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 122771.22 | 125085.09 | 62542.545 | 250170.18 | Not At-Risk | SDAC
CA2700523 | CALERA CANYON HEIGHTS HOA | 74 | 17 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 50952.3548 | Yes | 0 | 0 | Yes | 0 | 53266.2248 | 26633.1124 | 106532.4496 | Not At-Risk | Non-DAC
CA5400666 | DEL ORO GRANDVIEW GARDENS DISTRICT | 327 | 98 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 61858.7239 | No | 2035510.3 | 0 | Yes | 0 | 2097369.0239 | 1048684.512 | 4194738.0478 | HR2W | DAC
CA0410012 | SFWP-BANGOR | 73 | 22 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA5601201 | LIMONEIRA RANCH #1 | 832 | 232 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 138603.6713 | N/A | 0 | 0 | No | 424839.096 | 563442.7673 | 281721.3837 | 1126885.5346 | Not At-Risk | Non-DAC
CA2701926 | MORO RD WS #09 | 210 | 65 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 66315.6729 | Yes | 0 | 0 | Yes | 0 | 68629.5429 | 34314.7714 | 137259.0858 | HR2W | Non-DAC
CA2000728 | MD 37 LA VINA | 350 | 100 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 63879.5525 | Yes | 0 | 0 | Yes | 0 | 63879.5525 | 31939.7763 | 127759.1051 | Potentially At-Risk | Missing
CA5000055 | OLIVE LANE MOBILEHOME PARK | 153 | 51 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 46570.7162 | Yes | 0 | 0 | Yes | 0 | 48350.6162 | 24175.3081 | 96701.2325 | At-Risk | SDAC
CA0707573 | DELTA MUTUAL WATER COMPANY | 225 | 119 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 68010.1565 | Yes | 0 | 0 | No | 233836.98 | 304161.0065 | 152080.5032 | 608322.013 | HR2W | Non-DAC
CA4000563 | HIGUERA APARTMENTS | 30 | 24 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 45981.8695 | No | 2492205.8511 | 0 | Yes | 0 | 2540501.5906 | 1270250.7953 | 5081003.1812 | HR2W | DAC
CA1500591 | SWEET WATER CO-OP | 47 | 15 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37257.3322 | No | 2011312.5758 | 0 | Yes | 0 | 2050349.8081 | 1025174.904 | 4100699.6161 | Not At-Risk | Missing
CA1910053 | HEMLOCK MUTUAL WATER CO. | 686 | 208 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA | Yes | 0 | No | 121866.3571 | Yes | 0 | 0 | Yes | 0 | 121866.3571 | 60933.1786 | 243732.7142 | At-Risk | DAC
CA1910247 | SANTA CLARITA VALLEY W.A.-CASTAIC DIV. | 9820 | 1910 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1168980.2462 | Yes | 0 | 0 | Yes | 0 | 1168980.2462 | 584490.1231 | 2337960.4924 | Not At-Risk | Non-DAC
CA1910250 | SANTA CLARITA VALLEY W.A.-PINETREE DIV. | 15219 | 2821 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1787916.9538 | Yes | 0 | 0 | Yes | 0 | 1787916.9538 | 893958.4769 | 3575833.9075 | Not At-Risk | Non-DAC
CA3310028 | RIVERSIDE CSA #122-MESA VERDE | 1000 | 311 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA2000865 | MD 58 SIERRA HIGHLANDS | 75 | 25 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 39717.4714 | No | 2013732.3483 | 0 | Yes | 0 | 2053449.8196 | 1026724.9098 | 4106899.6393 | HR2W | SDAC
CA3301512 | PINYON PINES COUNTY WATER DIST | 160 | 82 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | No | 0 | 1827615.978 | Yes | 0 | 1827615.978 | 913807.989 | 3655231.956 | At-Risk | SDAC
CA5304502 | SALYER HEIGHTS W.S., INC | 135 | 42 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 31619.4 | 31619.4 | 15809.7 | 63238.8 | Not At-Risk | SDAC
CA4510011 | CENTERVILLE C.S.D. | 4211 | 1257 | DISTRICT 02 - LASSEN | C | T - RECREATION AREA | N/A | 0 | No | 403115.1719 | N/A | 0 | 0 | Yes | 0 | 403115.1719 | 201557.586 | 806230.3439 | Not At-Risk | Non-DAC
CA3600283 | DEPARTMENT OF WATER AND POWER | 388 | 125 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA1000057 | DEL ORO WATER CO - METROPOLITAN DISTRICT | 96 | 29 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 41562.5758 | No | 2015547.1776 | 0 | Yes | 0 | 2057109.7533 | 1028554.8767 | 4114219.5067 | HR2W | SDAC
CA3205001 | WALKER RANCH CSD | 50 | 1107 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2011571.8372 | 0 | No | 1206353.4 | 3219705.1372 | 1609852.5686 | 6439410.2743 | Potentially At-Risk | DAC
CA2300644 | WOODSIDE RV PARK | 280 | 58 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK | No | 1779.9 | No | 57729.2046 | Yes | 0 | 0 | No | 103234.2 | 162743.3046 | 81371.6523 | 325486.6092 | At-Risk | SDAC
CA3700277 | SUNRISE ESTATES MUTUAL WATER COMPANY | 150 | 46 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1410800 | CDF - OWENS VALLEY CONSERVATION CAMP | 127 | 37 | DISTRICT 13 - SAN BERNARDINO | C | NT - INSTITUTION | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 76849.8 | 76849.8 | 38424.9 | 153699.6 | Not At-Risk | Non-DAC
CA4901445 | JAMES COURT WATER SYSTEM | 205 | 40 | DISTRICT 18 - SONOMA | C | R - SUBDIVISION | No | 2313.87 | No | 65750.845 | Yes | 0 | 0 | No | 104804.7 | 172869.415 | 86434.7075 | 345738.83 | HR2W | Non-DAC
CA2000688 | ECCO | 100 | 15 | LPA50 - MADERA COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | No | 41914.0242 | Yes | 0 | 0 | No | 49209 | 92902.9242 | 46451.4621 | 185805.8485 | HR2W | SDAC
CA2701403 | PINE ST WS #01 | 36 | 17 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 46659.663 | No | 0 | 1020929.7 | No | 67238.34 | 1137141.573 | 568570.7865 | 2274283.1459 | Not At-Risk | Non-DAC
CA4700551 | COPCO LAKE MWC | 181 | 61 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | No | 49030.8554 | Yes | 0 | 0 | No | 107003.4 | 156034.2554 | 78017.1277 | 312068.5108 | Not At-Risk | SDAC
CA2900530 | ROUGH & READY MOBILEHOME VILLAGE | 268 | 56 | LPA59 - NEVADA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 56674.8593 | Yes | 0 | 0 | No | 100721.4 | 159176.1593 | 79588.0796 | 318352.3185 | Not At-Risk | SDAC
CA5510851 | CDCR - SIERRA CONSERVATION CENTER | 3885 | 578 | DISTRICT 11 - MERCED | C | NT - INSTITUTION | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 756562.2 | 756562.2 | 378281.1 | 1513124.4 | Potentially At-Risk | DAC
CA4010040 | GOLDEN STATE WATER COMPANY-CYPRESS RIDGE | 2559 | 959 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 331671.8067 | Yes | 0 | 0 | Yes | 0 | 331671.8067 | 165835.9034 | 663343.6135 | Not At-Risk | Non-DAC
CA2410006 | DELHI CWD | 7784 | 2303 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 717046.5027 | Yes | 0 | 0 | No | 31619.4 | 748665.9027 | 374332.9513 | 1497331.8054 | Not At-Risk | SDAC
CA3303003 | GALINDO HOUSING FACILITY | 50 | 38 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 48955.8652 | No | 0 | 1289449.602 | No | 103100.184 | 1443855.1192 | 721927.5596 | 2887710.2383 | Potentially At-Risk | SDAC
CA1502449 | CYPRESS CANYON WATER SYSTEM | 44 | 16 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36993.7459 | Yes | 0 | 0 | No | 50465.4 | 89239.0459 | 44619.5229 | 178478.0918 | At-Risk | SDAC
CA4200851 | ROLLING HILLS MUTUAL WATER COMPANY | 66 | 21 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 50048.6302 | No | 2496063.6597 | 0 | Yes | 0 | 2546112.2899 | 1273056.1449 | 5092224.5798 | At-Risk | Non-DAC
CA5010042 | WATERFORD-RIVER POINTE | 1079 | 333 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA3700919 | LAKE WOHLFORD RESORT | 250 | 137 | DISTRICT 14 - SAN DIEGO | C | R - MOBILE HOME PARK | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 56663.64 | 56663.64 | 28331.82 | 113327.28 | HR2W | Non-DAC
CA2300596 | BIG RIVER VISTA MUTUAL WATER COMPANY | 36 | 19 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36290.849 | No | 2010361.951 | 0 | Yes | 0 | 2048432.6999 | 1024216.35 | 4096865.3999 | Potentially At-Risk | SDAC
CA5400968 | IMPROVEMENT DISTRICT NO. 1 | 200 | 80 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 50700.2356 | Yes | 0 | 0 | Yes | 0 | 50700.2356 | 25350.1178 | 101400.4711 | Not At-Risk | SDAC
CA0900404 | OAKLANE MOBILE VILLAGE, LLC. | 75 | 35 | LPA39 - EL DORADO COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | Yes | 0 | No | 2497028.1118 | 0 | No | 42738.54 | 2542080.5218 | 1271040.2609 | 5084161.0437 | Potentially At-Risk | SDAC
CA2300638 | WILDWOOD CAMPGROUND | 150 | 50 | DISTRICT 03 - MENDOCINO | C | T - RECREATION AREA | Yes | 0 | No | 46307.1299 | Yes | 0 | 0 | No | 93183 | 139490.1299 | 69745.0649 | 278980.2598 | HR2W | SDAC
CA1500543 | AGAPE MUTUAL WATER SYSTEM | 60 | 16 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 38399.5397 | N/A | 0 | 0 | No | 50465.4 | 90644.8397 | 45322.4198 | 181289.6794 | At-Risk | Non-DAC
CA3610109 | SHEEP CREEK WATER COMPANY | 3623 | 1191 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 451867.1777 | Yes | 0 | 0 | Yes | 0 | 451867.1777 | 225933.5888 | 903734.3554 | Not At-Risk | DAC
CA1910018 | BELLFLOWER MUNICIPAL WATER SYSTEM | 5967 | 1826 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | Yes | 0 | No | 727275.6464 | Yes | 0 | 0 | Yes | 0 | 727275.6464 | 363637.8232 | 1454551.2928 | Not At-Risk | Non-DAC
CA1500564 | HOMETOWN WATER ASSOCIATION | 25 | 12 | DISTRICT 19 - TEHACHAPI | C | RESIDENTIAL AREA | N/A | 0 | N/A | 0 | No | 0 | 795814.23 | Yes | 0 | 795814.23 | 397907.115 | 1591628.46 | At-Risk | Missing
CA4210024 | LA CUMBRE MUTUAL WATER CO | 4861 | 1470 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 591718.5586 | Yes | 0 | 0 | Yes | 0 | 591718.5586 | 295859.2793 | 1183437.1172 | Not At-Risk | Non-DAC
CA1910248 | LOS ANGELES CWWD 37-ACTON | 6600 | 1484 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | Yes | 0 | No | 799842.2209 | Yes | 0 | 0 | Yes | 0 | 799842.2209 | 399921.1105 | 1599684.4418 | Not At-Risk | Non-DAC
CA4900667 | COLLEGE PARK MUTUAL WATER COMPANY | 237 | 72 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 69365.7434 | Yes | 0 | 0 | Yes | 0 | 71679.6134 | 35839.8067 | 143359.2268 | Not At-Risk | Non-DAC
CA2801020 | ESPINOZA WATER SYSTEM | 30 | 11 | LPA58 - NAPA COUNTY | C | RESIDENTIAL AREA | N/A | 0 | Yes | 0 | No | 0 | 948372.6 | N/A | 0 | 948372.6 | 474186.3 | 1896745.2 | Potentially At-Risk | DAC
CA4800531 | VACA VILLA APARTMENTS | 60 | 40 | DISTRICT 04 - SAN FRANCISCO | C | R - OTHER RESIDENTIAL AREA | No | 2313.87 | No | 49370.8368 | No | 0 | 1299065.25 | No | 103171.38 | 1453921.3368 | 726960.6684 | 2907842.6735 | Not At-Risk | Non-DAC
CA3110040 | PLACER CWA - BIANCHI ESTATES | 122 | 38 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1200591 | BIG LAGOON PARK WATER CO. | 70 | 76 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 125849.4 | 127629.3 | 63814.65 | 255258.6 | Not At-Risk | SDAC
CA3600399 | PARADISE MOBILE ESTATES | 190 | 38 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 64056.3614 | No | 2509351.6671 | 0 | Yes | 0 | 2573408.0285 | 1286704.0142 | 5146816.0569 | Potentially At-Risk | Non-DAC
CA1500554 | EAST INYOKERN MUTUAL WATER | 87 | 28 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 40771.8168 | Yes | 0 | 0 | Yes | 0 | 42551.7168 | 21275.8584 | 85103.4335 | Not At-Risk | Non-DAC
CA4300770 | THREE SPRINGS RANCH MUTUAL WATER COMPANY | 110 | 33 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 55834.2135 | Yes | 0 | 0 | Yes | 0 | 55834.2135 | 27917.1067 | 111668.4269 | Not At-Risk | Non-DAC
CA5500363 | TUD-WARDS FERRY RANCHES | 63 | 23 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 38663.126 | Yes | 0 | 0 | Yes | 0 | 38663.126 | 19331.563 | 77326.2521 | Not At-Risk | Non-DAC
CA1800503 | SUSAN RIVER PARK WATER CO. | 140 | 50 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 45428.5088 | Yes | 0 | 0 | No | 93183 | 140391.4088 | 70195.7044 | 280782.8175 | Potentially At-Risk | DAC
CA4110019 | O'CONNOR TRACT CO-OPERATIVE WATER CO. | 3128 | 359 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 574099.416 | 574099.416 | 287049.708 | 1148198.832 | Not At-Risk | Non-DAC
CA1910056 | LAKE ELIZABETH MUTUAL WATER CO. | 1790 | 724 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA | No | 2349.468 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 2349.468 | 1174.734 | 4698.936 | Not At-Risk | Non-DAC
CA3110009 | MEADOW VISTA CWD | 4001 | 1496 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA3310082 | NORTH PERRIS WATER SYSTEM | 4500 | 1389 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 559100.0305 | Yes | 0 | 0 | Yes | 0 | 559100.0305 | 279550.0153 | 1118200.0611 | Not At-Risk | Non-DAC
CA4210700 | AMERICAN WATER O&M, LLC - VAFB | 14971 | 1161 | DISTRICT 06 - SANTA BARBARA | C | NT - INSTITUTION | Yes | 0 | No | 1733800.5139 | Yes | 0 | 0 | No | 1865523.66 | 3599324.1739 | 1799662.087 | 7198648.3479 | Not At-Risk | Non-DAC
CA2702003 | VIERRA MEADOWS MWC | 65 | 25 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49935.6646 | Yes | 0 | 0 | Yes | 0 | 52249.5346 | 26124.7673 | 104499.0692 | Potentially At-Risk | Non-DAC
CA4400613 | LAS COLINAS ROAD & WATER ASSN | 70 | 24 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 50500.4925 | No | 0 | 1105579.65 | Yes | 0 | 1158394.0125 | 579197.0062 | 2316788.025 | At-Risk | Non-DAC
CA3103836 | HIDDEN VALLEY COMMUNITY ASSOCIATION | 499 | 165 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA0400030 | GOLDEN FEATHER MHP | 275 | 101 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 57289.8941 | Yes | 0 | 0 | Yes | 0 | 59069.7941 | 29534.897 | 118139.5881 | Not At-Risk | SDAC
CA5000008 | KNIGHTS FERRY COMM. SVC. DIST. | 168 | 67 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 47888.6479 | N/A | 0 | 0 | Yes | 0 | 47888.6479 | 23944.324 | 95777.2959 | Not At-Risk | Non-DAC
CA3901217 | HAYNES BOARD & CARE HOME | 41 | 15 | LPA69 - SAN JOAQUIN COUNTY | C | NT - INSTITUTION | Yes | 0 | No | 36730.1595 | No | 2010794.0532 | 0 | No | 49209 | 2096733.2127 | 1048366.6064 | 4193466.4254 | Not At-Risk | Non-DAC
CA2700674 | PARADISE LAKE MUTUAL WATER CO. | 180 | 76 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 62926.7057 | Yes | 0 | 0 | No | 163604.22 | 228844.7957 | 114422.3978 | 457689.5913 | Potentially At-Risk | Non-DAC
CA4100529 | CAMP LOMA MAR | 186 | 21 | DISTRICT 17 - SANTA CLARA | C | T - SUMMER CAMP | N/A | 0 | No | 64546.788 | N/A | 0 | 0 | No | 48371.4 | 112918.188 | 56459.094 | 225836.376 | HR2W | Non-DAC
CA4010012 | HERITAGE RANCH CSD | 2981 | 1954 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | Non-DAC
CA3410012 | CALAM - ISLETON | 1581 | 480 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 224468.3859 | Yes | 0 | 0 | Yes | 0 | 224468.3859 | 112234.1929 | 448936.7718 | Potentially At-Risk | SDAC
CA4400642 | CATHEDRAL WOOD MUTUAL WATER COMPANY | 60 | 20 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49370.8368 | Yes | 0 | 0 | Yes | 0 | 51684.7068 | 25842.3534 | 103369.4135 | Not At-Risk | Non-DAC
CA4000716 | AVILA VALLEY MUTUAL WATER CO | 75 | 29 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 51065.3204 | Yes | 0 | 0 | No | 41105.22 | 92170.5404 | 46085.2702 | 184341.0807 | Not At-Risk | DAC
CA4300741 | MIREVAL IMPROVEMENT ASSOCIATION | 60 | 15 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1100413 | COUNTRY LEISURE MOBILE ESTATES | 40 | 33 | DISTRICT 21 - VALLEY | C | R - MOBILE HOME PARK | Yes | 0 | N/A | 0 | No | 2010707.6327 | 0 | No | 71824.2 | 2082531.8327 | 1041265.9164 | 4165063.6655 | Not At-Risk | DAC
CA1000484 | FCSA #34/ MILLERTON NEW TOWN | 1100 | 394 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 129776.1375 | Yes | 0 | 0 | Yes | 0 | 129776.1375 | 64888.0688 | 259552.275 | HR2W | Non-DAC
CA3610114 | CLAWA | 2320 | 1225 | DISTRICT 13 - SAN BERNARDINO | C | O - WHOLESALER (SELLS WATER) | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA0310001 | CITY OF JACKSON | 4686 | 2185 | DISTRICT 10 - STOCKTON | C | O - OTHER AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | DAC
CA3310801 | BAUTISTA CC NO. 36 | 84 | 1 | DISTRICT 20 - RIVERSIDE | C | INSTITUTION | N/A | 0 | Yes | 0 | No | 0 | 836900.604 | Yes | 0 | 836900.604 | 418450.302 | 1673801.208 | Not At-Risk | Non-DAC
CA4900653 | LONE PINE MUTUAL WATER COMPANY | 65 | 28 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 49935.6646 | No | 2495956.4983 | 0 | Yes | 0 | 2545892.163 | 1272946.0815 | 5091784.3259 | Not At-Risk | Non-DAC
CA4700541 | CHATEAU SHASTA MOBILE HOME & RV PARK | 55 | 63 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK | No | 1779.9 | No | 37960.2291 | Yes | 0 | 0 | No | 109516.2 | 149256.3291 | 74628.1646 | 298512.6583 | Not At-Risk | DAC
CA0600005 | COLUSA CO. SERVICE AREA #2-STONYFORD | 250 | 63 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 55093.3412 | Yes | 0 | 0 | Yes | 0 | 56873.2412 | 28436.6206 | 113746.4824 | At-Risk | SDAC
CA2300634 | OCEAN'S EDGE ESTATES | 250 | 71 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 119567.4 | 119567.4 | 59783.7 | 239134.8 | Not At-Risk | DAC
CA3601010 | CRYSTAL LAKE PROPERTY OWNERS | 213 | 59 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 66654.5696 | Yes | 0 | 0 | No | 135837.78 | 202492.3496 | 101246.1748 | 404984.6992 | Not At-Risk | SDAC
CA1500485 | ANTELOPE VALLEY MOBILE ESTATES | 60 | 28 | DISTRICT 19 - TEHACHAPI | C | R - MOBILE HOME PARK | No | 1779.9 | No | 38399.5397 | Yes | 0 | 0 | No | 65542.2 | 105721.6397 | 52860.8198 | 211443.2794 | Not At-Risk | Missing
CA1910242 | CALIFORNIA WATER SERVICE CO-LAKE HUGHES | 952 | 209 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA | Yes | 0 | No | 152360.3679 | Yes | 0 | 0 | Yes | 0 | 152360.3679 | 76180.184 | 304720.7358 | Not At-Risk | Non-DAC
CA0400040 | ALMOND GROVE MOBILE PARK | 250 | 175 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 55093.3412 | No | 0 | 2429040 | No | 250233 | 2736146.2412 | 1368073.1206 | 5472292.4824 | At-Risk | Non-DAC
CA0400023 | GOLDEN OAKS MOBILE ESTATES | 34 | 52 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 36115.1248 | No | 2010189.1101 | 0 | No | 95695.8 | 2143779.9348 | 1071889.9674 | 4287559.8697 | Not At-Risk | SDAC
CA5400616 | LEMON COVE WATER CO | 109 | 60 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 42704.7832 | No | 2016670.6433 | 0 | Yes | 0 | 2061155.3266 | 1030577.6633 | 4122310.6531 | HR2W | Non-DAC
CA5601401 | KROTONA INSTITUTE | 31 | 31 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 46777.7215 | Yes | 0 | 0 | No | 91491.048 | 138268.7695 | 69134.3848 | 276537.5391 | Not At-Risk | DAC
CA3310046 | FARM MUTUAL W.C. (THE) | 4026 | 1265 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 51688.296 | 51688.296 | 25844.148 | 103376.592 | Not At-Risk | DAC
CA4100509 | COUNTY SERVICE AREA 7 | 300 | 68 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 77615.6497 | N/A | 0 | 0 | Yes | 0 | 77615.6497 | 38807.8249 | 155231.2995 | HR2W | Non-DAC
CA4000637 | COUNTRY HILLS ESTATES | 60 | 20 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | At-Risk | Non-DAC
CA3310019 | IDYLLWILD WATER DISTRICT | 2500 | 1665 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 329821.754 | Yes | 0 | 0 | Yes | 0 | 329821.754 | 164910.877 | 659643.5079 | Not At-Risk | Non-DAC
CA4900843 | SONOMA RANCH MUTUAL WATER COMPANY | 178 | 54 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 62700.7745 | Yes | 0 | 0 | Yes | 0 | 65014.6445 | 32507.3223 | 130029.289 | Not At-Risk | Non-DAC
CA4300525 | MELODY WOODS WATER COMPANY | 168 | 51 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 62483.2835 | Yes | 0 | 0 | Yes | 0 | 64832.7515 | 32416.3757 | 129665.503 | Not At-Risk | Non-DAC
CA5200539 | FRIENDLY ACRES MHP | 75 | 51 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 39717.4714 | No | 2013732.3483 | 0 | No | 94439.4 | 2149669.1196 | 1074834.5598 | 4299338.2393 | At-Risk | SDAC
CA2010006 | MADERA CO SA3-PARKSDALE | 1789 | 542 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 190313.1336 | Yes | 0 | 0 | No | 711331.8 | 901644.9336 | 450822.4668 | 1803289.8671 | Potentially At-Risk | DAC
CA5305103 | MAD RIVER COMPOUND - USFS | 57 | 16 | DISTRICT 01 - KLAMATH | NTNC | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | No | 2012176.7803 | 0 | No | 50465.4 | 2062642.1803 | 1031321.0901 | 4125284.3605 | Not At-Risk | Missing
CA3110124 | PLACER CWA - MONTE VISTA | 56 | 17 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA1800512 | CLEAR CREEK CSD-WESTWOOD | 400 | 166 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 238925.4 | 238925.4 | 119462.7 | 477850.8 | Potentially At-Risk | SDAC
CA1910035 | KINNELOA IRRIGATION DIST. | 1940 | 588 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA | Yes | 0 | No | 265623.8365 | Yes | 0 | 0 | Yes | 0 | 265623.8365 | 132811.9183 | 531247.6731 | Not At-Risk | Non-DAC
CA1910244 | GREEN VALLEY CWD | 1190 | 499 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 179644.4828 | Yes | 0 | 0 | Yes | 0 | 179644.4828 | 89822.2414 | 359288.9656 | Not At-Risk | Non-DAC
CA3600152 | LOMA LINDA UNIVERSITY | 8500 | 95 | LPA66 - SAN BERNARDINO COUNTY | C | NT - MEDICAL FACILITY | Yes | 0 | No | 1002800.2832 | Yes | 0 | 0 | No | 55805.1 | 1058605.3832 | 529302.6916 | 2117210.7663 | Not At-Risk | SDAC
CA4210017 | VANDENBERG VILLAGE COMM. SERV. DIST. | 7442 | 2585 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA5800824 | COUNTRY VILLAGE MOBILE HOME PARK | 50 | 45 | LPA88 - YUBA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 37520.9186 | No | 2011571.8372 | 0 | Yes | 0 | 2050872.6557 | 1025436.3279 | 4101745.3115 | HR2W | Non-DAC
CA1100436 | ORLAND OAKS MHP | 186 | 83 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 49470.166 | No | 2023325.0175 | 0 | No | 134644.2 | 2209219.2834 | 1104609.6417 | 4418438.5669 | Not At-Risk | SDAC
CA5510011 | COLD SPRINGS WATER CO | 153 | 535 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 46570.7162 | Yes | 0 | 0 | Yes | 0 | 48350.6162 | 24175.3081 | 96701.2325 | Not At-Risk | SDAC
CA2701929 | COUNTRY MEADOWS MWC | 621 | 107 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 112744.5239 | Yes | 0 | 0 | Yes | 0 | 112744.5239 | 56372.2619 | 225489.0478 | Not At-Risk | Missing
CA4500006 | SHASTA CSA - SUGARLOAF, #2 | 160 | 61 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 47185.751 | Yes | 0 | 0 | Yes | 0 | 47185.751 | 23592.8755 | 94371.502 | HR2W | SDAC
CA5410009 | PIXLEY PUBLIC UTIL DIST | 2772 | 840 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 276681.5909 | Yes | 0 | 0 | Yes | 0 | 278461.4909 | 139230.7455 | 556922.9818 | HR2W | SDAC
CA2700622 | OUTLOOK WA | 45 | 18 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 47676.3531 | Yes | 0 | 0 | Yes | 0 | 49990.2231 | 24995.1116 | 99980.4463 | Not At-Risk | Non-DAC
CA4300912 | MECCHI WATER COMPANY | 104 | 27 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 55146.3786 | No | 0 | 1154908.008 | No | 83198.808 | 1295602.6626 | 647801.3313 | 2591205.3253 | At-Risk | Non-DAC
CA2701202 | CAL AM WATER COMPANY - CHUALAR | 1139 | 193 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA4900546 | HAWKINS WATER CO-CAL WATER SERVICE (PUC) | 127 | 51 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | Potentially At-Risk | Non-DAC
CA0707576 | PLEASANTIMES MUTUAL WATER CO | 380 | 195 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 85519.8205 | Yes | 0 | 0 | Yes | 0 | 85519.8205 | 42759.9103 | 171039.641 | Not At-Risk | SDAC
CA1500584 | GOOSELAKE WATER COMPANY | 90 | 32 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 41035.4031 | Yes | 0 | 0 | No | 70567.8 | 113383.1031 | 56691.5515 | 226766.2062 | HR2W | Non-DAC
CA3400169 | SPINDRIFT MARINA | 100 | 50 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 54687.8221 | No | 2531961.4313 | 0 | No | 123001.56 | 2712000.2814 | 1356000.1407 | 5424000.5628 | At-Risk | SDAC
CA3110026 | NEVADA ID - NORTH AUBURN | 6719 | 2366 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 623473.352 | Yes | 0 | 0 | Yes | 0 | 623473.352 | 311736.676 | 1246946.7041 | Not At-Risk | DAC
CA3100029 | TAHOE CITY PUD - TIMBERLAND | 200 | 137 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 164797.8 | 164797.8 | 82398.9 | 329595.6 | Not At-Risk | Missing
CA0707507 | WILLOW PARK MARINA | 380 | 125 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 243636.9 | 245950.77 | 122975.385 | 491901.54 | HR2W | Non-DAC
CA3610112 | HELENDALE COMMUNITY SERVICE DISTRICT | 5849 | 2830 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 703328.5459 | Yes | 0 | 0 | Yes | 0 | 703328.5459 | 351664.273 | 1406657.0918 | Not At-Risk | DAC
CA5301102 | TRINITY KNOLLS MUTUAL WATER COMPANY | 338 | 66 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 62825.2072 | Yes | 0 | 0 | Yes | 0 | 64605.1072 | 32302.5536 | 129210.2144 | Not At-Risk | SDAC
CA1910255 | SANTA CLARITA VALLEY W.A.-TESORO DIV. | 6088 | 1157 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA4700549 | LAKE SISKIYOU M.W.C. | 240 | 84 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | No | 54214.7201 | Yes | 0 | 0 | Yes | 0 | 54214.7201 | 27107.36 | 108429.4402 | At-Risk | DAC
CA1000554 | FCSA #10A/MANSIONETTE ESTATES | 81 | 29 | DISTRICT 23 - FRESNO | C | O - OTHER AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | Non-DAC
CA0400149 | HUMBOLDT WOODLANDS MUTUAL | 75 | 31 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2013732.3483 | 0 | Yes | 0 | 2015512.2483 | 1007756.1241 | 4031024.4965 | Not At-Risk | Missing
CA1009039 | PAPPAS & CO (MENDOTA) | 25 | 13 | DISTRICT 23 - FRESNO | C | OTHER RESIDENTIAL AREA | N/A | 0 | N/A | 0 | No | 0 | 805834.02 | N/A | 0 | 805834.02 | 402917.01 | 1611668.04 | HR2W | DAC
CA4700528 | SISKIYOU CO. ROLLING HILLS MWC | 300 | 95 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA1400099 | MOUNTAIN VIEW TRAILER COURT | 53 | 24 | DISTRICT 13 - SAN BERNARDINO | C | R - MOBILE HOME PARK | No | 1779.9 | No | 37784.5049 | No | 2011831.0985 | 0 | No | 56747.4 | 2108142.9034 | 1054071.4517 | 4216285.8068 | Not At-Risk | SDAC
CA3900991 | LA TORRES PARK | 40 | 14 | LPA69 - SAN JOAQUIN COUNTY | C | OTHER TRANSIENT AREA | N/A | 0 | N/A | 0 | No | 0 | 815853.81 | N/A | 0 | 815853.81 | 407926.905 | 1631707.62 | At-Risk | Non-DAC
CA2600620 | MOUNTAIN MEADOWS MWC | 366 | 116 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 65285.3464 | Yes | 0 | 0 | Yes | 0 | 65285.3464 | 32642.6732 | 130570.6927 | Not At-Risk | Non-DAC
CA1610700 | LEMOORE NAVAL AIR STATION | 14000 | 1396 | DISTRICT 12 - VISALIA | C | T - OTHER TRANSIENT AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 1597093.8 | 1597093.8 | 798546.9 | 3194187.6 | Not At-Risk | DAC
CA2702554 | HIDDEN CANYON RANCH MWC | 100 | 27 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 53889.4597 | Yes | 0 | 0 | Yes | 0 | 53889.4597 | 26944.7299 | 107778.9194 | Not At-Risk | Non-DAC
CA4400502 | TROUT GULCH MUTUAL WATER COMPANY | 614 | 186 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1710002 | GOLDEN STATE WATER CO.-CLEARLAKE SYSTEM | 4104 | 2160 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES | N/A | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA0910012 | TAHOE CITY PUD - RUBICON | 703 | 625 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 122007.701 | Yes | 0 | 0 | Yes | 0 | 122007.701 | 61003.8505 | 244015.402 | Not At-Risk | Missing
CA2700792 | SUMMERHILL MHP WS | 95 | 34 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 53324.6319 | No | 2499171.3388 | 0 | No | 95004.78 | 2649814.6207 | 1324907.3103 | 5299629.2414 | At-Risk | Non-DAC
CA3310030 | PINE COVE WATER DISTRICT | 1540 | 1107 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 219768.1812 | Yes | 0 | 0 | Yes | 0 | 219768.1812 | 109884.0906 | 439536.3624 | Not At-Risk | DAC
CA5610029 | VINEYARD AVENUE ACRES MWC | 1820 | 336 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | DAC
CA2700740 | SAN MIGUEL WS #03 | 45 | 16 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 47676.3531 | N/A | 0 | 0 | No | 65605.02 | 113281.3731 | 56640.6866 | 226562.7463 | Not At-Risk | Non-DAC
CA5601122 | TICO MUTUAL WATER CO | 70 | 38 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 51248.6479 | Yes | 0 | 0 | Yes | 0 | 51248.6479 | 25624.324 | 102497.2959 | Potentially At-Risk | Non-DAC
CA0400155 | BIGGERS GLEN MUTUAL WATER CO | 25 | 29 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2009411.3261 | 0 | No | 66798.6 | 2077989.8261 | 1038994.913 | 4155979.6522 | At-Risk | Missing
CA5510003 | TUD - TUOLUMNE WATER SYSTEM | 1691 | 686 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | N/A | 0 | No | 181702.6465 | N/A | 0 | 0 | Yes | 0 | 181702.6465 | 90851.3232 | 363405.2929 | Not At-Risk | Non-DAC
CA4900794 | SUNSET PARK COMMUNITY | 141 | 42 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | No | 2313.87 | No | 58521.0483 | No | 0 | 1323250.95 | Yes | 0 | 1384085.8683 | 692042.9341 | 2768171.7365 | Potentially At-Risk | DAC
CA4900905 | MARK WEST MEADOWS MUTUAL WATER | 25 | 15 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 45417.0417 | Yes | 0 | 0 | No | 63971.7 | 111702.6117 | 55851.3058 | 223405.2233 | Not At-Risk | Non-DAC
CA2900502 | FLORISTON WATER SYSTEM | 75 | 46 | LPA59 - NEVADA COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 88157.4 | 88157.4 | 44078.7 | 176314.8 | HR2W | Non-DAC
CA3110024 | PLACER CWA - ALTA | 875 | 270 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1500426 | ROSE VILLA APARTMENTS | 65 | 32 | DISTRICT 19 - TEHACHAPI | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | No | 38838.8503 | No | 2012868.1438 | 0 | No | 70567.8 | 2124054.6941 | 1062027.347 | 4248109.3882 | HR2W | Missing
CA1500571 | KERN MOBILE ESTATES LLC | 73 | 60 | DISTRICT 19 - TEHACHAPI | C | R - MOBILE HOME PARK | No | 1779.9 | No | 39541.7472 | No | 2013559.5074 | 0 | No | 105747 | 2160628.1545 | 1080314.0773 | 4321256.3091 | HR2W | Missing
CA1502232 | ROSAMOND MOBILEHOME PARK | 175 | 79 | DISTRICT 19 - TEHACHAPI | C | R - MOBILE HOME PARK | No | 1779.9 | No | 48503.6827 | No | 2022374.3926 | 0 | No | 129618.6 | 2202276.5753 | 1101138.2877 | 4404553.1506 | HR2W | Missing
CA1910066 | LEISURE LAKE MOBILE ESTATES | 325 | 211 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA | Yes | 0 | No | 80481.6282 | Yes | 0 | 0 | No | 390011.688 | 470493.3162 | 235246.6581 | 940986.6324 | Potentially At-Risk | SDAC
CA1900693 | DESERT PALMS MOBILE HOME PARK | 140 | 56 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 59273.3876 | No | 0 | 1509608.574 | Yes | 0 | 1571231.4296 | 785615.7148 | 3142462.8592 | Not At-Risk | SDAC
CA1900907 | SHERWOOD MOBILE HOME PARK | 540 | 185 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 105129.0429 | Yes | 0 | 0 | Yes | 0 | 107478.5109 | 53739.2555 | 214957.0219 | Potentially At-Risk | DAC
CA3310017 | SOUTH MESA WC | 11953 | 2978 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 1413505.5281 | Yes | 0 | 0 | Yes | 0 | 1413505.5281 | 706752.7641 | 2827011.0563 | Not At-Risk | Non-DAC
CA3110012 | AGATE BAY WATER COMPANY | 2500 | 584 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | No | 252783.0961 | Yes | 0 | 0 | Yes | 0 | 252783.0961 | 126391.5481 | 505566.1922 | Not At-Risk | Non-DAC
CA3600220 | CSA 42 ORO GRANDE | 544 | 147 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA4300575 | TWIN VALLEY INC | 317 | 96 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 79564.5151 | Yes | 0 | 0 | Yes | 0 | 81913.9831 | 40956.9915 | 163827.9662 | HR2W | Non-DAC
CA2701740 | BLUFFS WS | 120 | 44 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | No | 2501850.3726 | 0 | No | 111337.98 | 2615502.2226 | 1307751.1113 | 5231004.4451 | Not At-Risk | Non-DAC
CA1900809 | LANDALE MUTUAL WATER COMPANY | 752 | 172 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 129432.5402 | No | 0 | 2928410.838 | Yes | 0 | 3057843.3782 | 1528921.6891 | 6115686.7565 | At-Risk | SDAC
CA3500527 | VALENZUELA WATER SYSTEM | 55 | 17 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48806.0089 | No | 2494884.8848 | 0 | No | 67238.34 | 2613243.1037 | 1306621.5519 | 5226486.2074 | At-Risk | Non-DAC
CA4000705 | LAGUNA NEGRA MUTUAL WATER CO. | 80 | 29 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | Not At-Risk | Non-DAC
CA3210011 | PLUMAS EUREKA CSD | 1525 | 554 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 167117.5357 | Yes | 0 | 0 | No | 723895.8 | 891013.3357 | 445506.6678 | 1782026.6713 | Not At-Risk | Non-DAC
CA3200134 | BLAIRSDEN WATER USERS ASSN | 200 | 50 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 93183 | 93183 | 46591.5 | 186366 | Not At-Risk | DAC
CA4900787 | PLAZA MOBILE HOME PARK | 125 | 71 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | No | 2313.87 | No | 56713.5991 | Yes | 0 | 0 | Yes | 0 | 59027.4691 | 29513.7345 | 118054.9382 | Not At-Risk | SDAC
CA4900791 | WESTERN MOBILE HOME PARK | 225 | 73 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | Yes | 0 | No | 68010.1565 | Yes | 0 | 0 | No | 158704.26 | 226714.4165 | 113357.2082 | 453428.833 | Potentially At-Risk | DAC
CA1700554 | LAKE COUNTY CSA 13 - KONO TAYEE | 395 | 144 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA3301879 | SHARONDALE MESA HOA | 330 | 244 | DISTRICT 20 - RIVERSIDE | C | R - MOBILE HOME PARK | Yes | 0 | No | 81054.8239 | Yes | 0 | 0 | Yes | 0 | 81054.8239 | 40527.4119 | 162109.6478 | Not At-Risk | DAC
CA5000058 | FISHERMAN'S BEND MHP | 120 | 66 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 43671.2665 | No | 2017621.2682 | 0 | No | 113285.4 | 2176357.8347 | 1088178.9173 | 4352715.6694 | At-Risk | SDAC
CA1910241 | LIBERTY UTILITIES - MESA CREST | 2336 | 708 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1910099 | PARADISE RANCH MHP | 345 | 95 | DISTRICT 15 - METROPOLITAN | C | R - MOBILE HOME PARK | Yes | 0 | No | 82774.411 | Yes | 0 | 0 | No | 41737.608 | 124512.019 | 62256.0095 | 249024.0379 | Potentially At-Risk | Non-DAC
CA4810011 | SID - ELMIRA | 314 | 88 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 0 | 1879522.05 | Yes | 0 | 1879522.05 | 939761.025 | 3759044.1 | Not At-Risk | Non-DAC
CA1502247 | DESERT BREEZE MOBILE HOME ESTATES | 82 | 63 | DISTRICT 19 - TEHACHAPI | C | R - MOBILE HOME PARK | No | 1779.9 | No | 40332.5062 | No | 2014337.2914 | 0 | No | 109516.2 | 2165965.8975 | 1082982.9488 | 4331931.7951 | HR2W | Missing
CA1500407 | CWS-SPLIT MOUNTAIN WATER SYSTEM | 211 | 162 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | SDAC
CA4500008 | LAKESHORE VILLA MUTUAL WATER CO | 81 | 40 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2014250.8709 | 0 | No | 80619 | 2094869.8709 | 1047434.9355 | 4189739.7418 | Not At-Risk | SDAC
CA4500098 | ANDERSON MOBILE HOME PARK | 70 | 21 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 39278.1608 | No | 2013300.246 | 0 | Yes | 0 | 2054358.3069 | 1027179.1534 | 4108716.6137 | At-Risk | DAC
CA4010832 | ATASCADERO STATE HOSPITAL | 4128 | 875 | DISTRICT 06 - SANTA BARBARA | C | NT - INSTITUTION | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 1468626.9 | 1468626.9 | 734313.45 | 2937253.8 | Not At-Risk | SDAC
CA4110020 | PALO ALTO PARK MUTUAL WATER COMPANY | 2900 | 692 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 1128021.048 | 1128021.048 | 564010.524 | 2256042.096 | HR2W | Non-DAC
CA4310013 | STANFORD UNIVERSITY | 32218 | 1497 | DISTRICT 17 - SANTA CLARA | C | NT - SCHOOL | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1502663 | TOWN & COUNTRY WATER COMPANY | 73 | 22 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39541.7472 | Yes | 0 | 0 | Yes | 0 | 41321.6472 | 20660.8236 | 82643.2943 | Not At-Risk | Non-DAC
CA2701676 | SAN LUCAS WD | 315 | 98 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 2313.87 | No | 78177.0582 | Yes | 0 | 0 | Yes | 0 | 80490.9282 | 40245.4641 | 160981.8564 | HR2W | SDAC
CA4300563 | MT. PLEASANT WATER USERS ASSOCIATION | 300 | 90 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 77615.6497 | N/A | 0 | 0 | Yes | 0 | 77615.6497 | 38807.8249 | 155231.2995 | Not At-Risk | Non-DAC
CA0409183 | SIERRA MOON WATER COMPANY | 120 | 86 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 43671.2665 | Yes | 0 | 0 | No | 138413.4 | 183864.5665 | 91932.2832 | 367729.133 | Not At-Risk | Non-DAC
CA0400090 | MOUNTAIN VILLAGE HOMEOWNER'S ASSOC | 40 | 17 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36642.2974 | No | 2010707.6327 | 0 | Yes | 0 | 2049129.8302 | 1024564.9151 | 4098259.6603 | Potentially At-Risk | Missing
CA3610045 | LACSD - RIMFOREST | 820 | 292 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | DAC
CA5610015 | VENTURA CWWD NO. 19 - SOMIS | 3275 | 1085 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 418667.0861 | Yes | 0 | 0 | Yes | 0 | 418667.0861 | 209333.5431 | 837334.1723 | Not At-Risk | Non-DAC
CA1900046 | PETER PITCHESS HONOR RANCHO DETN. CTR | 7000 | 1952 | DISTRICT 22 - ANGELES | C | NT - INSTITUTION | Yes | 0 | No | 845697.8762 | Yes | 0 | 0 | No | 3277369.656 | 4123067.5322 | 2061533.7661 | 8246135.0645 | Not At-Risk | Missing
CA5602140 | SATICOY COUNTRY CLUB-CITY OF VENTURA | 196 | 82 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 53346.744 | 53346.744 | 26673.372 | 106693.488 | Potentially At-Risk | Non-DAC
CA2702439 | WOODLAND HEIGHTS MWC | 57 | 37 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49031.94 | Yes | 0 | 0 | No | 99904.74 | 151250.55 | 75625.275 | 302501.1001 | At-Risk | Non-DAC
CA1910195 | GSWC - HOLLYDALE | 7691 | 1663 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 924913.5208 | Yes | 0 | 0 | Yes | 0 | 924913.5208 | 462456.7604 | 1849827.0416 | Not At-Risk | DAC
CA5200559 | ABBEY OF NEW CLAIRVAUX | 25 | 22 | LPA82 - TEHAMA COUNTY | C | NT - INSTITUTION | No | 1779.9 | Yes | 0 | No | 2009411.3261 | 0 | No | 58003.8 | 2069195.0261 | 1034597.513 | 4138390.0522 | Potentially At-Risk | DAC
CA3910018 | SAN JOAQUIN RIVER CLUB INC | 600 | 385 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 85845.0809 | Yes | 0 | 0 | No | 514077 | 601701.9809 | 300850.9904 | 1203403.9617 | Potentially At-Risk | SDAC
CA5805001 | PLUMAS LAKE | 8807 | 2669 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA4900568 | VALLEY FORD WATER ASSOCIATION | 61 | 23 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49483.8023 | Yes | 0 | 0 | Yes | 0 | 51797.6723 | 25898.8362 | 103595.3447 | HR2W | Non-DAC
CA2700992 | MILLER'S LODGE WS | 25 | 51 | LPA57 - MONTEREY COUNTY | C | T - RECREATION AREA | No | 2313.87 | No | 45417.0417 | No | 2491670.0443 | 0 | No | 122771.22 | 2662172.176 | 1331086.088 | 5324344.352 | HR2W | Non-DAC
CA5200007 | HOWELL'S LAKESIDE WATER CO. | 75 | 55 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39717.4714 | No | 0 | 1226665.2 | No | 99465 | 1367627.5714 | 683813.7857 | 2735255.1428 | Not At-Risk | SDAC
CA0410004 | CITY OF GRIDLEY | 7246 | 2264 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA1502465 | PANAMA ROAD PROPERTY OWNERS ASSOC | 45 | 16 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37081.608 | No | 2011139.735 | 0 | No | 50465.4 | 2100466.6429 | 1050233.3215 | 4200933.2859 | At-Risk | SDAC
CA3310033 | SANTA ANA RIVER WATER COMPANY | 6774 | 2050 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 819789.431 | Yes | 0 | 0 | Yes | 0 | 819789.431 | 409894.7155 | 1639578.862 | Not At-Risk | DAC
CA3210006 | LAKE ALMANOR COUNTRY CLUB MWC | 6000 | 1688 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 560300.4926 | Yes | 0 | 0 | Yes | 0 | 560300.4926 | 280150.2463 | 1120600.9852 | Not At-Risk | Non-DAC
CA2000512 | EAST ACRES MUTUAL WATER COMPANY | 250 | 85 | LPA50 - MADERA COUNTY | C | NT - INDUSTRIAL/AGRICULTURAL | Yes | 0 | No | 55093.3412 | No | 2028855.9258 | 0 | No | 137157 | 2221106.2671 | 1110553.1335 | 4442212.5341 | HR2W | SDAC
CA2000724 | SA 14 CHUK CHANSE SUBDIVISION | 100 | 31 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 41914.0242 | No | 2015892.8593 | 0 | No | 69311.4 | 2127118.2836 | 1063559.1418 | 4254236.5671 | At-Risk | DAC
CA4500101 | LAKE SHASTA PINES RV PARK & CAMPGROUND | 121 | 50 | LPA75 - SHASTA COUNTY | C | T - RECREATION AREA | No | 1779.9 | No | 43759.1286 | Yes | 0 | 0 | No | 93183 | 138722.0286 | 69361.0143 | 277444.0572 | At-Risk | SDAC
CA3010047 | GOLDEN STATE WC - COWAN HEIGHTS | 7236 | 2526 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 860011.7973 | Yes | 0 | 0 | Yes | 0 | 860011.7973 | 430005.8987 | 1720023.5947 | Not At-Risk | Non-DAC
CA4200703 | EL CAPITAN MUTUAL WATER COMPANY | 325 | 28 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 79306.7139 | Yes | 0 | 0 | Yes | 0 | 79306.7139 | 39653.357 | 158613.4278 | Not At-Risk | SDAC
CA5000005 | CROWS LANDING COMM SVC DISTRICT | 500 | 138 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 77058.8695 | Yes | 0 | 0 | No | 203746.2 | 280805.0695 | 140402.5348 | 561610.1391 | At-Risk | SDAC
CA4100512 | LOMA MAR MUTUAL | 65 | 34 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 96466.392 | 96466.392 | 48233.196 | 192932.784 | At-Risk | Non-DAC
CA5500193 | TAMARRON MOBILE HOME PARK | 225 | 100 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK | No | 1779.9 | No | 52896.7884 | Yes | 0 | 0 | No | 156003 | 210679.6884 | 105339.8442 | 421359.3768 | Not At-Risk | SDAC
CA1700546 | CLEAR WATER MUTUAL WATER COMPANY | 252 | 89 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK | N/A | 0 | No | 55269.0654 | N/A | 0 | 0 | Yes | 0 | 55269.0654 | 27634.5327 | 110538.1309 | At-Risk | DAC
CA2700682 | PARADISE RD WS #09 | 206 | 17 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 65863.8106 | No | 2511066.2487 | 0 | No | 67238.34 | 2646482.2692 | 1323241.1346 | 5292964.5385 | Potentially At-Risk | Non-DAC
CA2300743 | DOLPHIN ISLE MARINA | 560 | 86 | DISTRICT 03 - MENDOCINO | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2055646.2633 | 0 | No | 138413.4 | 2195839.5633 | 1097919.7816 | 4391679.1266 | Potentially At-Risk | SDAC
CA3107339 | FOLSOM LAKE MUTUAL WATER CO | 333 | 101 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 157259.4 | 157259.4 | 78629.7 | 314518.8 | Not At-Risk | Non-DAC
CA2300705 | LITTLE LAKE MOBILE HOME PARK | 38 | 19 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2010534.7918 | 0 | No | 31619.4 | 2043934.0918 | 1021967.0459 | 4087868.1837 | Not At-Risk | Non-DAC
CA2810002 | CALISTOGA, CITY OF | 5610 | 1497 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 676329.7737 | N/A | 0 | 0 | Yes | 0 | 676329.7737 | 338164.8868 | 1352659.5473 | Potentially At-Risk | Non-DAC
CA2300590 | SURFWOOD MUTUAL WATER CORPORATION | 160 | 107 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | Non-DAC
CA4710009 | WEED, CITY OF | 2963 | 1110 | DISTRICT 01 - KLAMATH | C | T - RECREATION AREA | No | 1779.9 | No | 293463.2546 | Yes | 0 | 0 | No | 54234.6 | 349477.7546 | 174738.8773 | 698955.5091 | Not At-Risk | SDAC
CA0202522 | SIERRA PINES MOBILE HOME PARK | 70 | 32 | LPA32 - ALPINE COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2013300.246 | 0 | No | 70567.8 | 2085647.946 | 1042823.973 | 4171295.8921 | Not At-Risk | SDAC
CA3400135 | KORTHS PIRATES LAIR | 150 | 64 | LPA64 - SACRAMENTO COUNTY | C | T - RECREATION AREA | Yes | 0 | Yes | 0 | No | 2537388.6352 | 0 | No | 146219.832 | 2683608.4672 | 1341804.2336 | 5367216.9343 | At-Risk | SDAC
CA1010006 | CITY OF FOWLER | 6600 | 1920 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 613017.7606 | Yes | 0 | 0 | Yes | 0 | 613017.7606 | 306508.8803 | 1226035.5211 | HR2W | DAC
CA1000570 | JUVENILE JUSTICE CAMPUS | 400 | 15 | DISTRICT 23 - FRESNO | C | O - OTHER AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA3210003 | CITY OF PORTOLA | 1970 | 1153 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 206216.1761 | Yes | 0 | 0 | Yes | 0 | 206216.1761 | 103108.088 | 412432.3521 | Not At-Risk | DAC
CA1000551 | FCSA #43/RAISIN CITY | 190 | 68 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 49821.6144 | No | 2023670.6992 | 0 | Yes | 0 | 2073492.3137 | 1036746.1568 | 4146984.6273 | At-Risk | SDAC
CA3310081 | PALM SPRINGS CREST | 532 | 173 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA0800557 | HUNTER VALLEY CSD | 96 | 62 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2015547.1776 | 0 | No | 108259.8 | 2123806.9776 | 1061903.4888 | 4247613.9551 | Not At-Risk | SDAC
CA2010004 | MADERA CO CMD19-PARKWOOD | 1637 | 496 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 176958.0923 | No | 0 | 5645392.59 | No | 653537.4 | 6475888.0823 | 3237944.0412 | 12951776.1647 | At-Risk | Non-DAC
CA4210020 | SANTA YNEZ RIVER WATER CONS. DIST. ID#1 | 6737 | 2600 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 803641.9758 | Yes | 0 | 0 | Yes | 0 | 803641.9758 | 401820.9879 | 1607283.9516 | Not At-Risk | Non-DAC
CA5110007 | SUTTER COMMUNITY S.D. | 2904 | 1080 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 288279.3899 | Yes | 0 | 0 | Yes | 0 | 288279.3899 | 144139.6949 | 576558.7797 | Not At-Risk | Non-DAC
CA3310076 | WESTERN MWD (ID A - RAINBOW) | 100 | 40 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | Non-DAC
CA3701934 | PINE VALLEY BIBLE CONFERENCE CENTER | 350 | 57 | LPA67 - SAN DIEGO COUNTY | C | T - RECREATION AREA | Yes | 0 | Yes | 0 | No | 2559097.4505 | 0 | No | 134610.696 | 2693708.1465 | 1346854.0733 | 5387416.2931 | Potentially At-Risk | Non-DAC
CA2000554 | MD 33 FAIRMEAD | 568 | 164 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 83033.4932 | Yes | 0 | 0 | Yes | 0 | 83033.4932 | 41516.7466 | 166066.9865 | Not At-Risk | Non-DAC
CA3301588 | ROYAL CARRIZO HOA | 25 | 20 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 46089.8867 | Yes | 0 | 0 | Yes | 0 | 48439.3547 | 24219.6774 | 96878.7094 | Potentially At-Risk | DAC
CA5210005 | RIO ALTO WATER DISTRICT | 3329 | 1378 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 325620.788 | Yes | 0 | 0 | Yes | 0 | 325620.788 | 162810.394 | 651241.576 | Not At-Risk | DAC
CA4900789 | BLUE SPRUCE MOBILE HOME PARK | 90 | 56 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | No | 2313.87 | No | 52759.804 | No | 2498635.5321 | 0 | No | 130937.82 | 2684647.0261 | 1342323.513 | 5369294.0521 | Potentially At-Risk | SDAC
CA5401026 | DEER MEADOW MUTUAL WATER COMPANY | 67 | 25 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39014.5745 | No | 2013040.9847 | 0 | Yes | 0 | 2053835.4592 | 1026917.7296 | 4107670.9184 | Not At-Risk | Non-DAC
CA5410012 | STRATHMORE PUBLIC UTIL DIST | 2150 | 551 | DISTRICT 12 - VISALIA | C | O - WHOLESALER (SELLS WATER) | Yes | 0 | N/A | 0 | Yes | 0 | 0 | No | 721383 | 721383 | 360691.5 | 1442766 | Not At-Risk | SDAC
CA3301541 | RECHE CANYON MUTUAL WATER CO. | 150 | 53 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 60419.779 | Yes | 0 | 0 | Yes | 0 | 60419.779 | 30209.8895 | 120839.558 | Not At-Risk | DAC
CA1900541 | WESTERN SKIES MOBILE HOME PARK | 198 | 61 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 65922.4576 | No | 2542598.7509 | 0 | No | 141244.488 | 2752115.1645 | 1376057.5822 | 5504230.329 | At-Risk | DAC
CA2610700 | USMC/MTN WARFARE TRNG CTR - BRIDGEPORT | 1200 | 30 | DISTRICT 13 - SAN BERNARDINO | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 68055 | 68055 | 34027.5 | 136110 | Not At-Risk | DAC
CA2110005 | BOLINAS COMMUNITY PUD | 2620 | 587 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | Non-DAC
CA5500096 | SIERRA TWAIN HARTE MHP | 129 | 46 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK | Yes | 0 | No | 44462.0255 | Yes | 0 | 0 | No | 88157.4 | 132619.4255 | 66309.7128 | 265238.851 | Not At-Risk | Non-DAC
CA5500064 | MULLER MUTUAL WATER COMPANY | 154 | 55 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA4900850 | BODEGA WATER COMPANY | 77 | 38 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | HR2W | Non-DAC
CA1910167 | VERNON-CITY, WATER DEPT. | 28000 | 1077 | DISTRICT 15 - METROPOLITAN | C | NT - INDUSTRIAL/AGRICULTURAL | Yes | 0 | No | 3253119.7801 | Yes | 0 | 0 | Yes | 0 | 3253119.7801 | 1626559.8901 | 6506239.5603 | Not At-Risk | SDAC
CA2310005 | WILLOW COUNTY WATER DISTRICT | 3797 | 1073 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA4901246 | DOWNTOWN GRATON MUTUAL WATER SYSTEM | 118 | 24 | DISTRICT 18 - SONOMA | C | T - OTHER TRANSIENT AREA | No | 2313.87 | No | 55922.8401 | Yes | 0 | 0 | Yes | 0 | 58236.7101 | 29118.355 | 116473.4201 | Not At-Risk | Non-DAC
CA5610702 | U.S.N., SAN NICOLAS ISLAND | 187 | 106 | DISTRICT 06 - SANTA BARBARA | C | R - OTHER RESIDENTIAL AREA | No | 2349.468 | No | 64661.4271 | No | 2541404.766 | 0 | No | 207582.408 | 2815998.0691 | 1407999.0346 | 5631996.1383 | At-Risk | Missing
CA3600504 | KNOLL ENTERPRISES | 500 | 25 | LPA66 - SAN BERNARDINO COUNTY | C | T - OTHER TRANSIENT AREA | No | 2313.87 | No | 99075.6894 | Yes | 0 | 0 | No | 80304.9 | 181694.4594 | 90847.2297 | 363388.9188 | HR2W | SDAC
CA3500836 | BETABEL RV RESORT | 49 | 176 | DISTRICT 05 - MONTEREY | C | T - RECREATION AREA | No | 2313.87 | Yes | 0 | No | 2494241.9167 | 0 | No | 326936.22 | 2823492.0067 | 1411746.0034 | 5646984.0135 | Potentially At-Risk | Non-DAC
CA1010053 | SHAVER LAKE HEIGHTS MWC | 1230 | 220 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 141198.2122 | Yes | 0 | 0 | No | 306771 | 447969.2122 | 223984.6061 | 895938.4245 | Not At-Risk | Non-DAC
CA2000502 | BASS LAKE HEIGHTS MUTUAL WATER | 250 | 90 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 55093.3412 | Yes | 0 | 0 | Yes | 0 | 56873.2412 | 28436.6206 | 113746.4824 | At-Risk | Non-DAC
CA1510027 | DESERT LAKE COMM SERV DIST | 1036 | 251 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | SDAC
CA1700527 | MOUNTAIN OF ATTENTION WATER | 40 | 26 | DISTRICT 03 - MENDOCINO | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2010707.6327 | 0 | No | 63029.4 | 2075516.9327 | 1037758.4664 | 4151033.8655 | At-Risk | DAC
CA5800803 | LOMA RICA WATER COMPANY | 200 | 70 | LPA88 - YUBA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 50700.2356 | No | 2024534.9037 | 0 | Yes | 0 | 2077015.0392 | 1038507.5196 | 4154030.0785 | At-Risk | Non-DAC
CA4500066 | CLEAR CREEK MOBILE PARK | 75 | 40 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 39717.4714 | Yes | 0 | 0 | Yes | 0 | 39717.4714 | 19858.7357 | 79434.9428 | Not At-Risk | SDAC
CA5510008 | LAKE DON PEDRO CSD | 3240 | 1492 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 317801.0599 | Yes | 0 | 0 | Yes | 0 | 317801.0599 | 158900.53 | 635602.1199 | Not At-Risk | DAC
CA0110016 | ALAMEDA POINT | 1500 | 412 | DISTRICT 04 - SAN FRANCISCO | C | O - OTHER AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA4901355 | TERRACE VIEW WATER SYSTEM | 60 | 16 | DISTRICT 18 - SONOMA | C | O - OTHER AREA | No | 2313.87 | No | 49370.8368 | Yes | 0 | 0 | Yes | 0 | 51684.7068 | 25842.3534 | 103369.4135 | Not At-Risk | Non-DAC
CA1010051 | FCWWD #18/FRIANT | 772 | 251 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 100957.3644 | N/A | 0 | 0 | Yes | 0 | 100957.3644 | 50478.6822 | 201914.7287 | Not At-Risk | Non-DAC
CA3900559 | WINE COUNTRY APARTMENTS | 40 | 16 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 36642.2974 | No | 2010707.6327 | 0 | No | 50465.4 | 2097815.3302 | 1048907.6651 | 4195630.6603 | Not At-Risk | Non-DAC
CA5000263 | OASIS INVESTMENTS | 75 | 31 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 39717.4714 | No | 2013732.3483 | 0 | No | 69311.4 | 2122761.2196 | 1061380.6098 | 4245522.4393 | Not At-Risk | Missing
CA3900983 | CHERRY LANE TRAILER PARK | 100 | 43 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 41914.0242 | No | 2015892.8593 | 0 | No | 84388.2 | 2142195.0836 | 1071097.5418 | 4284390.1671 | HR2W | SDAC
CA3901114 | KING ISLAND TRAILER PARK WATER SYSTEM | 200 | 76 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 50700.2356 | No | 2024534.9037 | 0 | No | 125849.4 | 2202864.4392 | 1101432.2196 | 4405728.8785 | Not At-Risk | DAC
CA2710019 | CWSC OAK HILLS | 3986 | 885 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 492873.6811 | Yes | 0 | 0 | Yes | 0 | 492873.6811 | 246436.8406 | 985747.3623 | At-Risk | Non-DAC
CA2700511 | NORMCO WC | 928 | 272 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 147424.9552 | Yes | 0 | 0 | Yes | 0 | 147424.9552 | 73712.4776 | 294849.9104 | Not At-Risk | Non-DAC
CA4200619 | SANTA YNEZ RANCHO ESTATES | 304 | 92 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 76934.4369 | Yes | 0 | 0 | Yes | 0 | 79248.3069 | 39624.1534 | 158496.6137 | Not At-Risk | Non-DAC
CA4300543 | WEST SAN MARTIN WATER WORKS INC | 1173 | 317 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 177695.6175 | Yes | 0 | 0 | Yes | 0 | 180045.0855 | 90022.5427 | 360090.1709 | Not At-Risk | Non-DAC
CA4810009 | CITY OF DIXON | 9037 | 2938 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA5200008 | BREESE SUBDIVISION 2 | 75 | 30 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39717.4714 | No | 2013732.3483 | 0 | No | 68055 | 2123284.7196 | 1061642.3598 | 4246569.4393 | Potentially At-Risk | SDAC
CA3400164 | VIEIRA'S RESORT, INC | 150 | 107 | LPA64 - SACRAMENTO COUNTY | C | T - RECREATION AREA | Yes | 0 | No | 60419.779 | Yes | 0 | 0 | No | 217533.096 | 277952.875 | 138976.4375 | 555905.75 | HR2W | SDAC
CA3900701 | CURRIER ESTATES WATER CORP | 148 | 37 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 46131.4057 | No | 2020041.0406 | 0 | No | 76849.8 | 2143022.2463 | 1071511.1231 | 4286044.4926 | Not At-Risk | Missing
CA0910019 | LAKESIDE PARK ASSOCIATION | 1000 | 139 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 264870.06 | 264870.06 | 132435.03 | 529740.12 | Not At-Risk | SDAC
CA4210013 | SOLVANG WATER DIVISION | 5792 | 2190 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 696889.5082 | Yes | 0 | 0 | Yes | 0 | 696889.5082 | 348444.7541 | 1393779.0163 | Not At-Risk | Non-DAC
CA5000072 | MULBERRY MHP | 148 | 53 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 46131.4057 | Yes | 0 | 0 | No | 96952.2 | 143083.6057 | 71541.8028 | 286167.2113 | Not At-Risk | SDAC
CA3301529 | RAMONA WATER COMPANY | 250 | 95 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 71883.6928 | Yes | 0 | 0 | No | 197631.72 | 271864.8808 | 135932.4404 | 543729.7617 | HR2W | SDAC
CA1500569 | VALLEY VIEW ESTATES MUTUAL WATER CO | 94 | 50 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 41386.8515 | Yes | 0 | 0 | Yes | 0 | 43166.7515 | 21583.3758 | 86333.5031 | Not At-Risk | Missing
CA1500449 | FOURTH STREET WATER SYSTEM | 56 | 28 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 65542.2 | 65542.2 | 32771.1 | 131084.4 | Not At-Risk | Missing
CA1500525 | LAKEVIEW RANCHOS MUTUAL WATER COMPANY | 120 | 71 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 43671.2665 | Yes | 0 | 0 | Yes | 0 | 43671.2665 | 21835.6332 | 87342.533 | HR2W | SDAC
CA3310802 | CHUCKAWALLA VALLEY STATE PRISON | 6507 | 1864 | DISTRICT 20 - RIVERSIDE | C | NT - INSTITUTION | No | 2349.468 | No | 789180.7811 | Yes | 0 | 0 | No | 3128109.336 | 3919639.5851 | 1959819.7925 | 7839279.1701 | Potentially At-Risk | SDAC
CA1500374 | CWS-GRAND OAKS WATER SYSTEM | 149 | 45 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 46219.2678 | Yes | 0 | 0 | Yes | 0 | 46219.2678 | 23109.6339 | 92438.5356 | Not At-Risk | Non-DAC
CA5200558 | RIVER VIEW MHC LLC | 100 | 55 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 41914.0242 | No | 2015892.8593 | 0 | Yes | 0 | 2059586.7836 | 1029793.3918 | 4119173.5671 | Not At-Risk | DAC
CA2700709 | RANCHO BORROMEO MWS | 100 | 36 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 53889.4597 | No | 2499707.1456 | 0 | No | 98271.42 | 2654181.8953 | 1327090.9476 | 5308363.7906 | Not At-Risk | DAC
CA2210002 | PONDEROSA BASIN MUTUAL WTR CO | 798 | 314 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 424872.6 | 424872.6 | 212436.3 | 849745.2 | Not At-Risk | DAC
CA5500080 | TWAIN HARTE VALLEY MWC | 202 | 106 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | N/A | 0 | No | 50875.9598 | No | 0 | 1737674.49 | No | 163541.4 | 1952091.8498 | 976045.9249 | 3904183.6996 | Not At-Risk | Non-DAC
CA5000054 | MORNINGSIDE MOBILEHOME PARK | 67 | 49 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 39014.5745 | Yes | 0 | 0 | Yes | 0 | 40794.4745 | 20397.2372 | 81588.949 | Not At-Risk | Non-DAC
CA2310001 | FORT BRAGG, CITY OF | 7250 | 2951 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 670128.1342 | Yes | 0 | 0 | Yes | 0 | 670128.1342 | 335064.0671 | 1340256.2684 | Not At-Risk | SDAC
CA5610068 | CLOVERDALE MUTUAL WATER CO. | 455 | 150 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 95384.7162 | Yes | 0 | 0 | Yes | 0 | 97734.1842 | 48867.0921 | 195468.3684 | Potentially At-Risk | DAC
CA2700669 | ORCHARD LN WS #02 | 32 | 16 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 46207.8007 | No | 2492420.1738 | 0 | No | 65605.02 | 2606546.8645 | 1303273.4322 | 5213093.7289 | Not At-Risk | Missing
CA2710006 | CAL AM WATER COMPANY - AMBLER PARK | 980 | 412 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 153299.165 | Yes | 0 | 0 | Yes | 0 | 153299.165 | 76649.5825 | 306598.3301 | Potentially At-Risk | Non-DAC
CA1910243 | CALIFORNIA WATER SERVICE CO-LEONA VALLEY | 900 | 429 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA | Yes | 0 | No | 146399.1327 | Yes | 0 | 0 | Yes | 0 | 146399.1327 | 73199.5664 | 292798.2654 | Potentially At-Risk | Non-DAC
CA1100203 | ARTOIS COMMUNITY S.D. | 198 | 58 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 50524.5113 | Yes | 0 | 0 | Yes | 0 | 50524.5113 | 25262.2557 | 101049.0227 | Not At-Risk | SDAC
CA1100444 | ORLAND ESTATES MOBILE H.P. | 200 | 74 | DISTRICT 21 - VALLEY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 50700.2356 | Yes | 0 | 0 | No | 123336.6 | 175816.7356 | 87908.3678 | 351633.4711 | Not At-Risk | SDAC
CA4400631 | LAS CUMBRES MUTUAL WATER CO | 342 | 125 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 81227.1287 | Yes | 0 | 0 | Yes | 0 | 83540.9987 | 41770.4993 | 167081.9974 | Not At-Risk | Non-DAC
CA3110042 | TAHOE SWISS VILLAGE UTILITY | 300 | 395 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 59486.4469 | Yes | 0 | 0 | No | 512820.6 | 574086.9469 | 287043.4734 | 1148173.8938 | Not At-Risk | DAC
CA4510016 | CLEAR CREEK CSD-ANDERSON | 8900 | 2366 | DISTRICT 02 - LASSEN | C | O - WHOLESALER (SELLS WATER) | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA1710004 | LAKEPORT, CITY OF | 4762 | 2278 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 451527.1963 | Yes | 0 | 0 | Yes | 0 | 451527.1963 | 225763.5982 | 903054.3927 | Not At-Risk | Non-DAC
CA1300550 | COUNTRY LIFE MH & RV PARK | 600 | 306 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK | N/A | 0 | No | 85845.0809 | N/A | 0 | 0 | No | 221335.8 | 307180.8809 | 153590.4404 | 614361.7617 | Not At-Risk | SDAC
CA1000053 | LANARE COMMUNITY SERVICES DIST | 660 | 156 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 91116.8077 | Yes | 0 | 0 | Yes | 0 | 91116.8077 | 45558.4038 | 182233.6153 | Potentially At-Risk | SDAC
CA5500128 | GOLD RUSH MOBILE HOME PARK | 67 | 53 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK | Yes | 0 | No | 39014.5745 | Yes | 0 | 0 | No | 37901.4 | 76915.9745 | 38457.9872 | 153831.949 | Not At-Risk | SDAC
CA4900913 | ROBIN WAY WATER SYSTEM | 66 | 20 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 50048.6302 | No | 0 | 1057208.25 | Yes | 0 | 1109570.7502 | 554785.3751 | 2219141.5004 | HR2W | Non-DAC
CA4900545 | BRANGER MUTUAL WATER COMPANY, INC. | 300 | 83 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 76482.5746 | Yes | 0 | 0 | Yes | 0 | 76482.5746 | 38241.2873 | 152965.1491 | Not At-Risk | Non-DAC
CA4000230 | CANYON CREST MUTUAL BENEFIT WC | 133 | 54 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA2910014 | NEVADA ID - LAKE OF PINES | 6932 | 2441 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 642187.9822 | N/A | 0 | 0 | Yes | 0 | 642187.9822 | 321093.9911 | 1284375.9643 | Not At-Risk | Non-DAC
CA5010035 | CITY OF MODESTO - CENTRAL TURLOCK | 116 | 36 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | No | 43319.818 | N/A | 0 | 0 | Yes | 0 | 43319.818 | 21659.909 | 86639.6361 | Not At-Risk | DAC
CA4500013 | LAKESIDE WOODS MUTUAL WATER CO | 310 | 112 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA2702110 | DELANY WC | 60 | 17 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49370.8368 | No | 2495420.6916 | 0 | Yes | 0 | 2547105.3983 | 1273552.6992 | 5094210.7967 | At-Risk | Non-DAC
CA3310036 | WESTERN MWD - MURRIETA DIVISION | 12810 | 2828 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 1511751.2696 | Yes | 0 | 0 | Yes | 0 | 1511751.2696 | 755875.6348 | 3023502.5393 | Not At-Risk | Non-DAC
CA1700606 | BAYCLIFF WATER | 70 | 56 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39278.1608 | No | 2013300.246 | 0 | Yes | 0 | 2054358.3069 | 1027179.1534 | 4108716.6137 | Not At-Risk | Non-DAC
CA1300616 | PALO VERDE COUNTY WATER DIST. | 410 | 134 | LPA43 - IMPERIAL COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | At-Risk | SDAC
CA4900513 | MADRONE MUTUAL WATER COMPANY | 76 | 23 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 68871.66 | 68871.66 | 34435.83 | 137743.32 | Not At-Risk | Non-DAC
CA4900792 | WAYSIDE GARDENS MOBILE HOME PARK | 75 | 50 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 121137.9 | 123451.77 | 61725.885 | 246903.54 | Not At-Risk | SDAC
CA3600391 | HILLCREST MOBILE ESTATES | 900 | 180 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | N/A | 0 | No | 0 | 2992064.25 | No | 333469.5 | 3325533.75 | 1662766.875 | 6651067.5 | HR2W | Non-DAC
CA5500048 | DON PEDRO REC AG:FLEM.MEADOWS | 1041 | 18 | DISTRICT 11 - MERCED | C | T - RECREATION AREA | N/A | 0 | No | 124592.2728 | N/A | 0 | 0 | No | 52978.2 | 177570.4728 | 88785.2364 | 355140.9457 | Not At-Risk | Non-DAC
CA4300611 | CASA DE FRUTA WATER SYSTEM | 250 | 37 | DISTRICT 17 - SANTA CLARA | C | R - MOBILE HOME PARK | No | 2349.468 | No | 71883.6928 | Yes | 0 | 0 | No | 89832.6 | 164065.7608 | 82032.8804 | 328131.5217 | Not At-Risk | Non-DAC
CA0510010 | VALLEY SPRINGS PUD | 900 | 263 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA2210924 | YOSEMITE WEST WATER SYSTEM | 420 | 186 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 70029.9005 | No | 2043547.4012 | 0 | Yes | 0 | 2113577.3017 | 1056788.6508 | 4227154.6034 | Potentially At-Risk | SDAC
CA1510036 | INYOKERN CSD | 805 | 265 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | Non-DAC
CA1410005 | INDIAN CREEK CSD | 1030 | 297 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 123625.7896 | Yes | 0 | 0 | No | 393462.6 | 517088.3896 | 258544.1948 | 1034176.7792 | Not At-Risk | Non-DAC
CA3610048 | TERRACE WATER COMPANY | 2000 | 605 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA3301294 | GLEN IVY HOT SPRINGS | 653 | 49 | LPA63 - RIVERSIDE COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 2349.468 | No | 118083.2656 | Yes | 0 | 0 | No | 108075.528 | 228508.2616 | 114254.1308 | 457016.5231 | Not At-Risk | Non-DAC
CA4710004 | ETNA, CITY OF | 720 | 413 | DISTRICT 01 - KLAMATH | C | T - RECREATION AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA0410007 | PARADISE IRRIGATION DISTRICT | 4600 | 2369 | DISTRICT 21 - VALLEY | C | R - MUNICIPALITY | No | 1779.9 | N/A | 0 | Yes | 0 | 0 | No | 3006774.6 | 3008554.5 | 1504277.25 | 6017109 | Not At-Risk | DAC
CA0707572 | BETHEL ISLAND MUTUAL WATER CO | 149 | 45 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 59424.7729 | No | 0 | 1359529.5 | No | 112971.3 | 1534239.4429 | 767119.7214 | 3068478.8857 | Not At-Risk | SDAC
CA3110044 | TAHOE CITY PUD - ALPINE PEAKS | 201 | 97 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | No | 50788.0977 | N/A | 0 | 0 | Yes | 0 | 50788.0977 | 25394.0488 | 101576.1953 | Not At-Risk | Missing
CA3110010 | TAHOE CITY PUD - MAIN | 5661 | 2902 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1400030 | GLENWOOD MOBILE ESTATES | 448 | 170 | DISTRICT 13 - SAN BERNARDINO | C | R - MOBILE HOME PARK | No | 1779.9 | No | 72490.0397 | Yes | 0 | 0 | No | 243951 | 318220.9397 | 159110.4698 | 636441.8793 | Not At-Risk | SDAC
CA3301990 | AMEZCUA - GARCIA WATER | 316 | 113 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 79449.876 | No | 0 | 2206778.652 | No | 227483.784 | 2516061.78 | 1258030.89 | 5032123.5599 | At-Risk | SDAC
CA5601141 | SOUTH MOUNTAIN MUTUAL WATER CO | 58 | 27 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 49872.9783 | Yes | 0 | 0 | No | 84857.256 | 137079.7023 | 68539.8511 | 274159.4046 | Not At-Risk | DAC
CA2810007 | TOWN OF YOUNTVILLE | 2751 | 833 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA2700586 | GABILAN WC | 535 | 162 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 103029.4845 | Yes | 0 | 0 | Yes | 0 | 105343.3545 | 52671.6773 | 210686.709 | Not At-Risk | Non-DAC
CA2702466 | SAN VICENTE MWC | 69 | 21 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 50387.5269 | Yes | 0 | 0 | No | 73771.62 | 124159.1469 | 62079.5735 | 248318.2938 | Potentially At-Risk | DAC
CA3110031 | WARD WELL WATER COMPANY | 375 | 226 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 66076.1054 | Yes | 0 | 0 | No | 314309.4 | 380385.5054 | 190192.7527 | 760771.0108 | Not At-Risk | Non-DAC
CA1910200 | SUBURBAN WATER SYSTEMS-COVINA KNOLLS | 2010 | 498 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1500557 | STOCKDALE RANCHOS MUTUAL WATER CO | 393 | 95 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 67657.6234 | No | 0 | 1627456.8 | No | 149721 | 1846615.3234 | 923307.6617 | 3693230.6468 | Potentially At-Risk | Non-DAC
CA1210023 | LOLETA C.S.D. | 750 | 281 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2072066.1475 | 0 | Yes | 0 | 2072066.1475 | 1036033.0738 | 4144132.295 | Not At-Risk | SDAC
CA1500481 | RIVERNOOK CAMPGROUND | 877 | 290 | DISTRICT 19 - TEHACHAPI | C | R - MOBILE HOME PARK | Yes | 0 | No | 110182.8862 | Yes | 0 | 0 | No | 394719 | 504901.8862 | 252450.9431 | 1009803.7725 | Not At-Risk | Missing
CA1500489 | BRITE LAKE MUTUAL WATER COMPANY | 89 | 27 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 40947.541 | Yes | 0 | 0 | No | 64285.8 | 105233.341 | 52616.6705 | 210466.682 | Not At-Risk | Non-DAC
CA1910010 | CALIFORNIA WATER SERVICE CO.-LANCASTER | 1422 | 673 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA | Yes | 0 | No | 206240.7629 | Yes | 0 | 0 | Yes | 0 | 206240.7629 | 103120.3814 | 412481.5258 | Potentially At-Risk | Non-DAC
CA3700074 | CUYAMACA WATER DISTRICT | 200 | 159 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 66151.7359 | Yes | 0 | 0 | No | 303772.392 | 369924.1279 | 184962.064 | 739848.2558 | HR2W | DAC
CA3110050 | PLACER CWA - APPLEGATE | 215 | 67 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA1500336 | BURLANDO HEIGHTS MUTUAL WATER CO. | 45 | 42 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA5610014 | OJAI WATER SYSTEM | 6712 | 2902 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 812681.8044 | Yes | 0 | 0 | Yes | 0 | 812681.8044 | 406340.9022 | 1625363.6088 | Not At-Risk | Non-DAC
CA2300545 | SHORELANDS ROAD & WATER COMPANY | 85 | 47 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 40596.0925 | Yes | 0 | 0 | Yes | 0 | 42375.9925 | 21187.9963 | 84751.9851 | Not At-Risk | Non-DAC
CA1100254 | VOYLES TRAILER PARK | 27 | 15 | DISTRICT 21 - VALLEY | C | T - RECREATION AREA | No | 1779.9 | No | 35500.09 | No | 2009584.167 | 0 | No | 49209 | 2096073.1569 | 1048036.5785 | 4192146.3139 | At-Risk | DAC
CA5304102 | TRINITY VILLAGE MUTUAL WATER | 301 | 193 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | No | 59574.309 | Yes | 0 | 0 | Yes | 0 | 59574.309 | 29787.1545 | 119148.618 | Not At-Risk | SDAC
CA1910027 | LOS ANGELES CWWD 40, REG. 35-N.E. L.A. | 811 | 223 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | Yes | 0 | No | 136196.2494 | Yes | 0 | 0 | Yes | 0 | 136196.2494 | 68098.1247 | 272392.4988 | Potentially At-Risk | SDAC
CA3710041 | MAJESTIC PINES COMMUNITY SD | 1502 | 706 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 215411.894 | Yes | 0 | 0 | Yes | 0 | 215411.894 | 107705.947 | 430823.7879 | Not At-Risk | DAC
CA3710009 | DESCANSO COMMUNITY SERVICES DISTRICT | 870 | 317 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 142959.9586 | No | 2615540.3705 | 0 | Yes | 0 | 2758500.3291 | 1379250.1645 | 5517000.6581 | HR2W | Non-DAC
CA2210510 | YOSEMITE NPS-WAWONA | 150 | 150 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA2710023 | TASCO SPRECKELS WATER COMPANY | 1079 | 328 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA2700548 | DOLAN RD MWC | 120 | 40 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 56148.7712 | No | 2501850.3726 | 0 | No | 81938.22 | 2642251.2338 | 1321125.6169 | 5284502.4676 | At-Risk | SDAC
CA1910072 | GSWC - WILLOWBROOK | 11069 | 1450 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1312164.5299 | Yes | 0 | 0 | Yes | 0 | 1312164.5299 | 656082.2649 | 2624329.0598 | Not At-Risk | SDAC
CA4900536 | OCCIDENTAL COMMUNITY SERVICES DISTRICT | 383 | 109 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 85858.7172 | No | 2530033.8076 | 0 | Yes | 0 | 2618206.3948 | 1309103.1974 | 5236412.7896 | Potentially At-Risk | Non-DAC
CA2700775 | TIERRA VERDE MWC | 48 | 16 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48015.2499 | Yes | 0 | 0 | No | 65605.02 | 115934.1399 | 57967.0699 | 231868.2797 | Not At-Risk | Non-DAC
CA5800823 | COUNTRY AIR MOBILE HOME PARK | 100 | 35 | LPA88 - YUBA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 41914.0242 | Yes | 0 | 0 | Yes | 0 | 43693.9242 | 21846.9621 | 87387.8485 | Not At-Risk | Missing
CA2300892 | COVELO MOBILE HOME PARK | 30 | 30 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK | No | 1779.9 | No | 35763.6763 | Yes | 0 | 0 | No | 68055 | 105598.5763 | 52799.2881 | 211197.1526 | Not At-Risk | SDAC
CA5200255 | CORNING RV PARK | 112 | 40 | LPA82 - TEHAMA COUNTY | C | T - OTHER TRANSIENT AREA | No | 1779.9 | No | 42968.3696 | No | 2016929.9047 | 0 | No | 80619 | 2142297.1742 | 1071148.5871 | 4284594.3485 | Potentially At-Risk | DAC
CA2702268 | NEW CAMALDOLI HERMITAGE WS | 54 | 54 | LPA57 - MONTEREY COUNTY | C | T - OTHER TRANSIENT AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | DAC
CA3600025 | BAR-LEN MWC | 124 | 42 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 56600.6335 | Yes | 0 | 0 | No | 108071.34 | 164671.9735 | 82335.9868 | 329343.947 | HR2W | SDAC
CA5200500 | REEDS CREEK ESTATES | 70 | 25 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 39278.1608 | No | 0 | 926071.5 | No | 61773 | 1027122.6608 | 513561.3304 | 2054245.3217 | Not At-Risk | DAC
CA4100538 | CAMP JONES GULCH | 357 | 65 | DISTRICT 17 - SANTA CLARA | C | T - RECREATION AREA | No | 2349.468 | No | 84150.0806 | Yes | 0 | 0 | No | 147878.28 | 234377.8286 | 117188.9143 | 468755.6573 | Not At-Risk | Non-DAC
CA5410041 | CWS - TULCO WATER COMPANY | 716 | 181 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | Non-DAC
CA3600382 | MWD OF SO CAL IRON MOUNTAIN | 27 | 38 | DISTRICT 13 - SAN BERNARDINO | C | T - SECONDARY RESIDENCES | N/A | 0 | No | 45642.9728 | N/A | 0 | 0 | No | 101538.06 | 147181.0328 | 73590.5164 | 294362.0656 | Not At-Risk | SDAC
CA5602110 | NAVALAIR MOBILE HOME PARK | 160 | 52 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 61566.1704 | Yes | 0 | 0 | Yes | 0 | 63915.6384 | 31957.8192 | 127831.2768 | HR2W | DAC
CA5602109 | GLENVIEW MOBILE PARK | 160 | 26 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 61566.1704 | No | 2538474.0759 | 0 | Yes | 0 | 2602389.7143 | 1301194.8572 | 5204779.4286 | HR2W | DAC
CA3500910 | DUNNEVILLE ESTATES CSA #50 | 120 | 30 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 56148.7712 | Yes | 0 | 0 | No | 88471.5 | 146934.1412 | 73467.0706 | 293868.2824 | Not At-Risk | Non-DAC
CA4100555 | PORTOLA IMPROVEMENT ASSOCIATION | 100 | 35 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 54687.8221 | N/A | 0 | 0 | Yes | 0 | 54687.8221 | 27343.911 | 109375.6442 | Not At-Risk | Non-DAC
CA2110007 | COAST SPRINGS - CAL. WATER SERVICE (PUC) | 210 | 251 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 66315.6729 | Yes | 0 | 0 | Yes | 0 | 68629.5429 | 34314.7714 | 137259.0858 | Not At-Risk | Non-DAC
CA3110020 | OLYMPIC VALLEY PSD | 1366 | 865 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 153147.4596 | Yes | 0 | 0 | Yes | 0 | 153147.4596 | 76573.7298 | 306294.9193 | Not At-Risk | Non-DAC
CA1009214 | WESTSIDE HARVESTING | 75 | 24 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 60516.6 | 60516.6 | 30258.3 | 121033.2 | Potentially At-Risk | SDAC
CA5710011 | WILD WINGS GOLF COMMUNITY | 1115 | 352 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 131094.0692 | Yes | 0 | 0 | Yes | 0 | 131094.0692 | 65547.0346 | 262188.1384 | Potentially At-Risk | Non-DAC
CA1805004 | CDCR-HIGH DESERT STATE PRISON | 8641 | 2724 | DISTRICT 02 - LASSEN | C | NT - INSTITUTION | Yes | 0 | No | 792344.3338 | Yes | 0 | 0 | No | 3452796.6 | 4245140.9338 | 2122570.4669 | 8490281.8675 | Not At-Risk | DAC
CA5510021 | TUD-PEACEFUL PINES WATER SYSTEM | 56 | 33 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 38048.0912 | No | 2012090.3598 | 0 | Yes | 0 | 2050138.4511 | 1025069.2255 | 4100276.9021 | At-Risk | SDAC
CA5200571 | MOUNTAIN VALLEY APTS & RVP | 131 | 47 | LPA82 - TEHAMA COUNTY | C | T - OTHER TRANSIENT AREA | No | 1779.9 | No | 44637.7497 | No | 0 | 1146506.88 | No | 89413.8 | 1282338.3297 | 641169.1649 | 2564676.6595 | Not At-Risk | SDAC
CA2702026 | APRICOT LN WS | 53 | 16 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48580.0777 | No | 2494670.5621 | 0 | No | 65605.02 | 2611169.5299 | 1305584.7649 | 5222339.0597 | Potentially At-Risk | Non-DAC
CA3900602 | TAHAMA VILLAGE MOBILE HOME PARK | 200 | 68 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 50700.2356 | Yes | 0 | 0 | No | 115798.2 | 166498.4356 | 83249.2178 | 332996.8711 | Not At-Risk | Non-DAC
CA1900785 | MITCHELL'S AVENUE E MOBILE HOME PARK | 24 | 24 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 45975.2476 | No | 2523712.0815 | 0 | No | 79881.912 | 2651918.7091 | 1325959.3545 | 5303837.4181 | HR2W | SDAC
CA3410045 | CALAM - ARDEN | 3908 | 1185 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 491233.6607 | Yes | 0 | 0 | Yes | 0 | 491233.6607 | 245616.8303 | 982467.3213 | Not At-Risk | SDAC
CA3410047 | CALAM - WALNUT GROVE | 651 | 197 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | SDAC
CA4910018 | ARMSTRONG VALLEY-CAL WATER SERVICE (PUC) | 424 | 269 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 90490.3058 | Yes | 0 | 0 | Yes | 0 | 92804.1758 | 46402.0879 | 185608.3515 | Not At-Risk | DAC
CA4910027 | SONOMA STATE UNIVERSITY | 10986 | 93 | DISTRICT 18 - SONOMA | C | NT - SCHOOL | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 145637.7 | 145637.7 | 72818.85 | 291275.4 | Not At-Risk | Non-DAC
CA4400598 | PURESOURCE WATER, INC | 200 | 77 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 65186.0171 | Yes | 0 | 0 | No | 145637.7 | 213137.5871 | 106568.7936 | 426275.1743 | Not At-Risk | Non-DAC
CA3400190 | IMPERIAL MANOR MOBILEHOME COMMUNITY | 200 | 186 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 66151.7359 | N/A | 0 | 0 | No | 348550.488 | 414702.2239 | 207351.112 | 829404.4478 | Potentially At-Risk | SDAC
CA4000649 | LOS ROBLES MOBILE HOME ESTATES | 420 | 160 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 90038.4435 | Yes | 0 | 0 | Yes | 0 | 92352.3135 | 46176.1567 | 184704.6269 | Not At-Risk | Non-DAC
CA1010042 | MALAGA COUNTY WATER DISTRICT | 5979 | 462 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA1300628 | IMPERIAL LAKES INC. | 40 | 15 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK | N/A | 0 | No | 36642.2974 | N/A | 0 | 0 | No | 49209 | 85851.2974 | 42925.6487 | 171702.5949 | Potentially At-Risk | DAC
CA4210018 | BUELLTON WATER DEPARTMENT | 5464 | 1831 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 659836.7998 | Yes | 0 | 0 | Yes | 0 | 659836.7998 | 329918.3999 | 1319673.5997 | Not At-Risk | Non-DAC
CA1710015 | HIDDEN VALLEY LAKE CSD | 8227 | 2490 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | DAC
CA2600621 | WHITE MOUNTAIN MUTUAL WATER COMPANY | 142 | 43 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2019522.518 | 0 | No | 84388.2 | 2105690.618 | 1052845.309 | 4211381.2359 | Potentially At-Risk | SDAC
CA3610026 | SBDNO COUNTY SERVICE AREA 70 CEDAR GLEN | 1236 | 342 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | Not At-Risk | SDAC
CA1200553 | WEOTT C.S.D. | 364 | 128 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA1500289 | ATHAL MUTUAL WATER SYSTEM | 150 | 55 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 46307.1299 | No | 2020213.8815 | 0 | No | 99465 | 2167765.9114 | 1083882.9557 | 4335531.8228 | HR2W | SDAC
CA1500546 | HARVEST MOON MUTUAL WATER CO | 138 | 49 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 45252.7845 | Yes | 0 | 0 | No | 91926.6 | 138959.2845 | 69479.6423 | 277918.5691 | HR2W | Non-DAC
CA3600070 | CENTER WATER CO | 662 | 50 | LPA66 - SAN BERNARDINO COUNTY | C | T - SECONDARY RESIDENCES | No | 2313.87 | No | 117376.1124 | Yes | 0 | 0 | Yes | 0 | 119689.9824 | 59844.9912 | 239379.9649 | Not At-Risk | SDAC
CA3910020 | STOCKTON VERDE MOBILE HOME PARK | 712 | 293 | DISTRICT 10 - STOCKTON | C | R - MOBILE HOME PARK | No | 1779.9 | No | 95685.6376 | Yes | 0 | 0 | No | 42927 | 140392.5376 | 70196.2688 | 280785.0751 | Not At-Risk | Non-DAC
CA3500524 | RIVER OAKS R.V.P. | 52 | 15 | DISTRICT 17 - SANTA CLARA | C | R - MOBILE HOME PARK | No | 2313.87 | No | 48467.1122 | No | 2494563.4008 | 0 | No | 62338.38 | 2607682.7629 | 1303841.3815 | 5215365.5259 | At-Risk | Missing
CA2610701 | USMC - HOUSING COLEVILLE | 325 | 116 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 61682.9997 | Yes | 0 | 0 | No | 174849 | 236531.9997 | 118265.9999 | 473063.9994 | At-Risk | SDAC
CA1210018 | TRINIDAD, CITY OF | 1072 | 324 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA3200138 | MEADOW EDGE MHP | 53 | 31 | LPA62 - PLUMAS COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 37784.5049 | Yes | 0 | 0 | No | 69311.4 | 108875.8049 | 54437.9025 | 217751.6098 | Not At-Risk | DAC
CA4300571 | SULLIVAN MUTUAL WATER | 53 | 16 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 49299.7826 | No | 0 | 1020366.414 | No | 66614.328 | 1138629.9926 | 569314.9963 | 2277259.9852 | Potentially At-Risk | Non-DAC
CA0510004 | CCWD - SHEEP RANCH | 134 | 48 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | No | 44901.3361 | N/A | 0 | 0 | Yes | 0 | 44901.3361 | 22450.668 | 89802.6722 | At-Risk | Missing
CA0900102 | GOLD BEACH PARK | 100 | 40 | LPA39 - EL DORADO COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | N/A | 0 | No | 2499707.1456 | 0 | No | 104804.7 | 2606825.7156 | 1303412.8578 | 5213651.4312 | At-Risk | Non-DAC
CA1300546 | GOLD ROCK RANCH | 50 | 76 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 37520.9186 | Yes | 0 | 0 | No | 125849.4 | 165150.2186 | 82575.1093 | 330300.4371 | HR2W | SDAC
CA4200693 | ELLWOOD MUTUAL WATER COMPANY | 186 | 56 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 63604.4991 | Yes | 0 | 0 | Yes | 0 | 65918.3691 | 32959.1846 | 131836.7382 | Not At-Risk | Non-DAC
CA3901075 | FAIRWAY ESTATES PWS CSA-18 | 68 | 47 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 39102.4366 | Yes | 0 | 0 | No | 89413.8 | 128516.2366 | 64258.1183 | 257032.4732 | Not At-Risk | Non-DAC
CA3500552 | VENTURE ESTATES MWC | 60 | 18 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49370.8368 | No | 0 | 1033022.55 | Yes | 0 | 1084707.2568 | 542353.6284 | 2169414.5135 | At-Risk | Non-DAC
CA2800543 | CAPELL VALLEY ESTATES | 250 | 63 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1400056 | BROOKSIDE ESTATES MUTUAL WATER COMPANY | 59 | 21 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 38311.6776 | Yes | 0 | 0 | No | 56747.4 | 96838.9776 | 48419.4888 | 193677.9552 | Not At-Risk | Non-DAC
CA3400128 | HAPPY HARBOR (SWS) | 60 | 45 | LPA64 - SACRAMENTO COUNTY | C | T - RECREATION AREA | Yes | 0 | No | 50102.2566 | No | 2527619.6683 | 0 | No | 114709.32 | 2692431.2448 | 1346215.6224 | 5384862.4896 | Potentially At-Risk | SDAC
CA4900637 | MAGIC MOUNTAIN MUTUAL WATER COMPANY | 100 | 67 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 53889.4597 | No | 2499707.1456 | 0 | Yes | 0 | 2555910.4753 | 1277955.2376 | 5111820.9506 | At-Risk | DAC
CA3600180 | NAVAJO MWC | 276 | 80 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 73771.4008 | Yes | 0 | 0 | Yes | 0 | 73771.4008 | 36885.7004 | 147542.8016 | Not At-Risk | SDAC
CA0605011 | DEL ORO WC - ARBUCKLE DISTRICT | 185 | 56 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA5510007 | DEL ORO WATER COMPANY - STRAWBERRY DIV. | 1283 | 388 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | N/A | 0 | No | 145854.9042 | Yes | 0 | 0 | Yes | 0 | 145854.9042 | 72927.4521 | 291709.8085 | HR2W | SDAC
CA1500465 | OAK KNOLLS MUTUAL WATER COMPANY | 123 | 47 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 43934.8528 | Yes | 0 | 0 | No | 89413.8 | 135128.5528 | 67564.2764 | 270257.1057 | Not At-Risk | SDAC
CA4700627 | JUNIPER CREEK ESTATES | 130 | 51 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK | No | 1779.9 | No | 44549.8876 | No | 2018485.4726 | 0 | No | 94439.4 | 2159254.6603 | 1079627.3301 | 4318509.3205 | Potentially At-Risk | SDAC
CA4300603 | OAK DELL PARK | 100 | 53 | DISTRICT 17 - SANTA CLARA | C | R - MOBILE HOME PARK | No | 2349.468 | No | 54687.8221 | No | 2531961.4313 | 0 | No | 127976.904 | 2716975.6254 | 1358487.8127 | 5433951.2508 | HR2W | Non-DAC
CA1010800 | CAL FIRE - MIRAMONTE CONSERVATION CAMP | 100 | 19 | DISTRICT 23 - FRESNO | C | NT - INSTITUTION | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 52978.2 | 52978.2 | 26489.1 | 105956.4 | Not At-Risk | DAC
CA1300622 | SPORTSMANS PARADISE | 60 | 30 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 38399.5397 | Yes | 0 | 0 | No | 68055 | 108234.4397 | 54117.2198 | 216468.8794 | Potentially At-Risk | SDAC
CA3100040 | SHADY GLEN COMM WATER SYSTEM | 200 | 121 | LPA61 - PLACER COUNTY | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | No | 50700.2356 | N/A | 0 | 0 | No | 182387.4 | 233087.6356 | 116543.8178 | 466175.2711 | At-Risk | SDAC
CA2000851 | MD 40 SUNSET RIDGE ESTATES | 150 | 27 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 46307.1299 | Yes | 0 | 0 | Yes | 0 | 46307.1299 | 23153.5649 | 92614.2598 | HR2W | DAC
CA1400070 | SIERRA GRANDE ESTATES MUTUAL WATER CO. | 200 | 49 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 50700.2356 | No | 2024534.9037 | 0 | No | 91926.6 | 2167161.7392 | 1083580.8696 | 4334323.4785 | Not At-Risk | Non-DAC
CA4900973 | GEORGE RANCH MUTUAL WATER COMPANY | 148 | 53 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA3900579 | CENTURY MOBILE HOME PARK | 50 | 19 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 37520.9186 | No | 2011571.8372 | 0 | Yes | 0 | 2050872.6557 | 1025436.3279 | 4101745.3115 | HR2W | SDAC
CA5400670 | TRIPLE R MUTUAL WATER CO | 408 | 154 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 68975.5551 | Yes | 0 | 0 | No | 37901.4 | 106876.9551 | 53438.4776 | 213753.9102 | HR2W | DAC
CA5510013 | TUD - COLUMBIA WATER SYSTEM | 4352 | 1925 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | N/A | 0 | No | 415503.7299 | Yes | 0 | 0 | Yes | 0 | 415503.7299 | 207751.8649 | 831007.4598 | Not At-Risk | SDAC
CA5510033 | TUD-SCENIC VIEW/SCENIC BROOK | 365 | 174 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 65197.4842 | Yes | 0 | 0 | Yes | 0 | 65197.4842 | 32598.7421 | 130394.9685 | Potentially At-Risk | Non-DAC
CA1710005 | LUCERNE WATER CO. - CAL WATER SERVICE | 2397 | 1236 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA4900640 | SONOMA COUNTY MUTUAL WATER COMPANY | 40 | 18 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 47111.5253 | No | 2493277.4646 | 0 | No | 68871.66 | 2611574.5199 | 1305787.2599 | 5223149.0397 | HR2W | SDAC
CA4500009 | CORTLAND PINES MUTUAL WATER CO | 92 | 33 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2015201.4958 | 0 | Yes | 0 | 2016981.3958 | 1008490.6979 | 4033962.7916 | Not At-Risk | DAC
CA1500378 | MAHER MUTUAL WATER COMPANY | 150 | 50 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 46307.1299 | N/A | 0 | 0 | No | 93183 | 141270.0299 | 70635.0149 | 282540.0598 | At-Risk | DAC
CA0210001 | LAKE ALPINE WATER COMPANY | 625 | 488 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | Non-DAC
CA3910019 | LINDEN COUNTY WATER DISTRICT | 1784 | 617 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 35388.6 | 35388.6 | 17694.3 | 70777.2 | Not At-Risk | Non-DAC
CA4000654 | RESTHAVEN MOBILE HOME PARK | 75 | 47 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 51065.3204 | Yes | 0 | 0 | Yes | 0 | 53379.1904 | 26689.5952 | 106758.3807 | HR2W | Non-DAC
CA3910008 | LOCKEFORD COMMUNITY SERV. DIST. | 2500 | 848 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA5400556 | RIVER RETREAT MUTUAL | 53 | 25 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37784.5049 | No | 2011831.0985 | 0 | No | 61773 | 2113168.5034 | 1056584.2517 | 4226337.0068 | Potentially At-Risk | Non-DAC
CA4910011 | SEBASTOPOL, CITY OF | 7786 | 2953 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 922142.8632 | Yes | 0 | 0 | Yes | 0 | 922142.8632 | 461071.4316 | 1844285.7263 | Potentially At-Risk | Non-DAC
CA3310004 | BOX SPRINGS MUTUAL WC | 3542 | 649 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 449275.7361 | Yes | 0 | 0 | Yes | 0 | 449275.7361 | 224637.868 | 898551.4721 | At-Risk | SDAC
CA3702236 | PALOMAR OBSERVATORY | 50 | 27 | LPA67 - SAN DIEGO COUNTY | C | T - SECONDARY RESIDENCES | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 84857.256 | 84857.256 | 42428.628 | 169714.512 | Not At-Risk | Non-DAC
CA3301717 | VALLEY VIEW TRAILER PARK | 135 | 37 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 58700.1919 | No | 0 | 1277218.548 | No | 101441.736 | 1439709.9439 | 719854.972 | 2879419.8879 | Potentially At-Risk | SDAC
CA1500563 | CHINA LAKE ACRES MUTUAL WATER COMPANY | 198 | 60 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | Missing
CA3600088 | DESERT DAWN MWC | 150 | 45 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | Not At-Risk | SDAC
CA3600139 | JUBILEE MWC | 710 | 215 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 122798.46 | Yes | 0 | 0 | Yes | 0 | 122798.46 | 61399.23 | 245596.92 | Not At-Risk | SDAC
CA3900649 | GLENWOOD MOBILE HOME PARK | 100 | 50 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 41914.0242 | No | 2015892.8593 | 0 | No | 93183 | 2152769.7836 | 1076384.8918 | 4305539.5671 | At-Risk | SDAC
CA3400217 | HOMETOWN COLONIAL ESTATES LLC | 438 | 146 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 93435.8508 | Yes | 0 | 0 | No | 282212.568 | 377997.8868 | 188998.9434 | 755995.7737 | Not At-Risk | Missing
CA3500549 | ROSA MORADA MUTUAL WATER COMPANY | 129 | 21 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 57165.4614 | Yes | 0 | 0 | Yes | 0 | 59479.3314 | 29739.6657 | 118958.6627 | Not At-Risk | Non-DAC
CA4910025 | KENWOOD VILLAGE WATER COMPANY (PUC) | 1000 | 309 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 155558.4765 | Yes | 0 | 0 | Yes | 0 | 155558.4765 | 77779.2383 | 311116.953 | Not At-Risk | Non-DAC
CA1700657 | WINDFLOWER POINT MUTUAL WATER COMPANY | 25 | 25 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2009411.3261 | 0 | Yes | 0 | 2011191.2261 | 1005595.613 | 4022382.4522 | Not At-Risk | SDAC
CA1500406 | TRADEWIND WATER ASSOC. | 632 | 234 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 88656.6685 | Yes | 0 | 0 | Yes | 0 | 90436.5685 | 45218.2842 | 180873.137 | HR2W | Missing
CA1510004 | CASA LOMA WATER CO, INC. | 900 | 248 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 112203.7149 | Yes | 0 | 0 | No | 341950.2 | 455933.8149 | 227966.9074 | 911867.6297 | Not At-Risk | SDAC
CA4900788 | EL CRYSTAL MOBILE HOME PARK | 130 | 57 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | No | 2313.87 | No | 57278.4269 | Yes | 0 | 0 | No | 132571.14 | 192163.4369 | 96081.7185 | 384326.8739 | HR2W | SDAC
CA3610105 | GOLDEN STATE WATER CO - APPLE VLY NORTH | 2106 | 731 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 280498.4016 | Yes | 0 | 0 | Yes | 0 | 280498.4016 | 140249.2008 | 560996.8032 | Not At-Risk | DAC
CA3600279 | GOLDEN STATE WATER DESERT VIEW | 125 | 60 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 56713.5991 | Yes | 0 | 0 | Yes | 0 | 56713.5991 | 28356.7995 | 113427.1982 | Not At-Risk | SDAC
CA5810005 | NEVADA ID - SMARTSVILLE | 122 | 43 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 43846.9907 | N/A | 0 | 0 | Yes | 0 | 43846.9907 | 21923.4954 | 87693.9814 | Not At-Risk | DAC
CA5710007 | ESPARTO C.S.D. | 3108 | 1007 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 306203.261 | Yes | 0 | 0 | Yes | 0 | 306203.261 | 153101.6305 | 612406.522 | Not At-Risk | Non-DAC
CA4400599 | SUNSET BEACH MUTUAL WATER CO | 150 | 65 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA2300667 | WOODS, THE (MENDOCINO) | 153 | 115 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2020473.1428 | 0 | No | 174849 | 2197102.0428 | 1098551.0214 | 4394204.0857 | Not At-Risk | SDAC
CA0310002 | AWA, IONE | 6170 | 2106 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | Non-DAC
CA2410010 | WINTON WATER & SANITARY DIST | 9500 | 2672 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 867817.8891 | Yes | 0 | 0 | Yes | 0 | 867817.8891 | 433908.9445 | 1735635.7781 | HR2W | SDAC
CA2010801 | VALLEY STATE PRISON | 3095 | 74 | DISTRICT 11 - MERCED | C | NT - INSTITUTION | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 119567.4 | 119567.4 | 59783.7 | 239134.8 | At-Risk | DAC
CA1910086 | MAYWOOD MUTUAL WATER CO. #3 | 9500 | 2014 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1132295.7219 | Yes | 0 | 0 | Yes | 0 | 1132295.7219 | 566147.861 | 2264591.4439 | Not At-Risk | SDAC
CA1010025 | CITY OF PARLIER | 15286 | 2663 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 49209 | 49209 | 24604.5 | 98418 | HR2W | SDAC
CA4200804 | WALKING M RANCHES | 54 | 19 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1010039 | CARUTHERS COMM SERV DIST | 2503 | 746 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | SDAC
CA4400526 | BIG REDWOOD PARK WATER | 130 | 65 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 57278.4269 | N/A | 0 | 0 | Yes | 0 | 57278.4269 | 28639.2135 | 114556.8539 | Not At-Risk | Non-DAC
CA1910081 | LYNWOOD PARK MUTUAL WATER CO. | 2300 | 470 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | Yes | 0 | No | 306893.9263 | Yes | 0 | 0 | Yes | 0 | 306893.9263 | 153446.9632 | 613787.8526 | At-Risk | SDAC
CA5403110 | SIERRA MUTUAL WATER CO | 43 | 16 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36905.8838 | Yes | 0 | 0 | Yes | 0 | 38685.7838 | 19342.8919 | 77371.5675 | At-Risk | Non-DAC
CA3700859 | RANCHO DEL CAMPO WATER SYSTEM | 290 | 110 | LPA67 - SAN DIEGO COUNTY | C | T - SECONDARY RESIDENCES | Yes | 0 | No | 76469.2584 | Yes | 0 | 0 | No | 136269.144 | 212738.4024 | 106369.2012 | 425476.8047 | At-Risk | SDAC
CA4900892 | SUMMIT VIEW RANCH MUTUAL WATER CO. | 45 | 24 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2493813.2713 | 0 | No | 44371.86 | 2538185.1313 | 1269092.5657 | 5076370.2627 | Potentially At-Risk | Non-DAC
CA2701498 | HARBOR VIEW WA | 75 | 29 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 51065.3204 | No | 2497028.1118 | 0 | No | 86838.18 | 2637245.4822 | 1318622.7411 | 5274490.9644 | At-Risk | Non-DAC
CA3205006 | GRIZZLY RANCH CSD | 25 | 62 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA3200078 | FRCCSD OLD MILL RANCH | 32 | 23 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2010016.2692 | 0 | No | 59260.2 | 2071056.3692 | 1035528.1846 | 4142112.7384 | Potentially At-Risk | SDAC
CA1500461 | FOUNTAIN TRAILER PARK WATER | 68 | 33 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 39102.4366 | No | 2013127.4051 | 0 | No | 71824.2 | 2124054.0418 | 1062027.0209 | 4248108.0835 | HR2W | SDAC
CA2701279 | COASTLANDS MWS (POST CREEK) | 129 | 32 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | DAC
CA5010007 | HILLSVIEW HOMES | 887 | 230 | DISTRICT 10 - STOCKTON | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 319335 | 319335 | 159667.5 | 638670 | HR2W | Non-DAC
CA5000316 | HAKAM MISSON | 45 | 14 | LPA80 - STANISLAUS COUNTY | C | RESIDENTIAL AREA | N/A | 0 | N/A | 0 | No | 0 | 815853.81 | N/A | 0 | 815853.81 | 407926.905 | 1631707.62 | HR2W | SDAC
CA1700610 | BELLA LAGO MOBILE HOME PARK | 152 | 46 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK | No | 1779.9 | No | 46482.8541 | No | 2020386.7224 | 0 | No | 88157.4 | 2156806.8765 | 1078403.4383 | 4313613.753 | Potentially At-Risk | DAC
CA2500503 | CALIFORNIA PINES C.S.D. | 300 | 169 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA5200864 | R-WILD HORSE RANCH | 55 | 17 | LPA82 - TEHAMA COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 51721.8 | 53501.7 | 26750.85 | 107003.4 | Potentially At-Risk | Non-DAC
CA3200195 | GREENHAVEN HOA | 38 | 18 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2010534.7918 | 0 | No | 52978.2 | 2065292.8918 | 1032646.4459 | 4130585.7837 | Potentially At-Risk | SDAC
CA1000259 | NEW HORIZONS MOBILE/RV PARK | 82 | 77 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK | No | 1779.9 | No | 40332.5062 | No | 2014337.2914 | 0 | No | 127105.8 | 2183555.4975 | 1091777.7488 | 4367110.9951 | Potentially At-Risk | SDAC
CA4010023 | GOLDEN STATE WATER COMPANY - EDNA | 1299 | 587 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1210020 | FIELDBROOK GLENDALE C.S.D. | 1848 | 551 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | No | 195496.9982 | N/A | 0 | 0 | Yes | 0 | 195496.9982 | 97748.4991 | 390993.9965 | Not At-Risk | DAC
CA5601117 | SENIOR CANYON MUTUAL WATER CO | 800 | 218 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 134935.2189 | Yes | 0 | 0 | Yes | 0 | 137284.6869 | 68642.3434 | 274569.3738 | Not At-Risk | Non-DAC
CA2310006 | MILLVIEW COUNTY WATER DISTRICT | 5500 | 1609 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 516369.4359 | Yes | 0 | 0 | Yes | 0 | 516369.4359 | 258184.718 | 1032738.8719 | Not At-Risk | Non-DAC
CA2210903 | FISHCAMP MUTUAL WATER COMPANY | 275 | 75 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 57289.8941 | Yes | 0 | 0 | No | 124593 | 181882.8941 | 90941.447 | 363765.7881 | Not At-Risk | Non-DAC
CA5200512 | BEND MOBILEHOME & RV PARK | 99 | 42 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 41826.1621 | Yes | 0 | 0 | No | 83131.8 | 126737.8621 | 63368.9311 | 253475.7242 | Not At-Risk | SDAC
CA3600155 | RIVER RANCH MHP | 700 | 138 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 121668.8043 | Yes | 0 | 0 | No | 264870.06 | 388852.7343 | 194426.3671 | 777705.4685 | HR2W | SDAC
CA5610701 | NAVAL BASE VENTURA COUNTY, PORT HUENEME | 3500 | 609 | DISTRICT 06 - SANTA BARBARA | C | R - OTHER RESIDENTIAL AREA | No | 2349.468 | No | 444460.8922 | Yes | 0 | 0 | No | 935641.08 | 1382451.4402 | 691225.7201 | 2764902.8805 | Not At-Risk | SDAC
CA1900649 | GOLDEN SANDS MOBILE HOME PARK | 450 | 152 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 94811.5205 | No | 0 | 2683789.758 | No | 292163.256 | 3073114.0025 | 1536557.0012 | 6146228.005 | Not At-Risk | DAC
CA1600023 | AZCAL MANAGEMENT CO | 73 | 21 | DISTRICT 12 - VISALIA | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | No | 39541.7472 | N/A | 0 | 0 | No | 56747.4 | 96289.1472 | 48144.5736 | 192578.2943 | Potentially At-Risk | DAC
CA3410005 | RANCHO MURIETA COMMUNITY SERVI | 5744 | 2726 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 701711.1185 | N/A | 0 | 0 | Yes | 0 | 701711.1185 | 350855.5593 | 1403422.2371 | Not At-Risk | Non-DAC
CA3900805 | MOREHEAD PARK | 300 | 113 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 59486.4469 | Yes | 0 | 0 | No | 172336.2 | 231822.6469 | 115911.3234 | 463645.2938 | Not At-Risk | Non-DAC
CA3301577 | CSA 62 | 700 | 117 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | SDAC
CA3410030 | FOLSOM, CITY OF - ASHLAND | 3538 | 1079 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA3600185 | OAK GLEN DOMESTIC WATER | 175 | 49 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA5800832 | CASTLEWOOD MOBILE HOME PARK | 200 | 88 | LPA88 - YUBA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 50700.2356 | No | 0 | 1557318.27 | No | 140926.2 | 1750724.6056 | 875362.3028 | 3501449.2111 | Potentially At-Risk | SDAC
CA1500405 | AERIAL ACRES WATER COMPANY, INC. | 96 | 49 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | Missing
CA0800605 | WEST PARK PROPERTIES | 112 | 42 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK | No | 1779.9 | No | 42968.3696 | No | 2016929.9047 | 0 | No | 83131.8 | 2144809.9742 | 1072404.9871 | 4289619.9485 | Not At-Risk | SDAC
CA2400167 | BALLICO CSD | 238 | 73 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2027818.8805 | 0 | No | 122080.2 | 2151678.9805 | 1075839.4903 | 4303357.961 | HR2W | DAC
CA4800564 | HIDDEN ACRES TRAILER VILLA | 80 | 54 | DISTRICT 04 - SAN FRANCISCO | C | R - MOBILE HOME PARK | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 127671.18 | 129985.05 | 64992.525 | 259970.1 | Not At-Risk | Non-DAC
CA2300610 | CASPAR SOUTH SERVICE COMPANY | 188 | 95 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 49645.8902 | Yes | 0 | 0 | Yes | 0 | 51425.7902 | 25712.8951 | 102851.5804 | Not At-Risk | Non-DAC
CA4010018 | GOLDEN STATE WATER COMPANY - NIPOMO | 4409 | 1505 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 540658.119 | Yes | 0 | 0 | Yes | 0 | 540658.119 | 270329.0595 | 1081316.2381 | Not At-Risk | Non-DAC
CA5310001 | WEAVERVILLE C.S.D. | 3400 | 1654 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | No | 331858.9981 | Yes | 0 | 0 | Yes | 0 | 331858.9981 | 165929.499 | 663717.9961 | Not At-Risk | SDAC
CA1910189 | SAN GABRIEL VALLEY WATER CO.-MONTEBELLO | 8630 | 1579 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA | N/A | 0 | No | 1032559.6716 | Yes | 0 | 0 | Yes | 0 | 1032559.6716 | 516279.8358 | 2065119.3433 | Not At-Risk | Non-DAC
CA3010093 | EAST ORANGE COUNTY WD - WZ | 0 | 16 | DISTRICT 08 - SANTA ANA | C | O - WHOLESALER (SELLS WATER) | N/A | 0 | N/A | 0 | Yes | 0 | 0 | No | 41105.22 | 41105.22 | 20552.61 | 82210.44 | Not At-Risk | Missing
CA2300735 | HOLLY RANCH VILLAGE | 50 | 19 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37520.9186 | Yes | 0 | 0 | No | 54234.6 | 93535.4186 | 46767.7093 | 187070.8371 | Not At-Risk | DAC
CA1310008 | WESTMORLAND, CITY OF | 2444 | 501 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | No | 247862.8178 | N/A | 0 | 0 | No | 32875.8 | 280738.6178 | 140369.3089 | 561477.2355 | Potentially At-Risk | SDAC
CA1502620 | POND MUTUAL WATER COMPANY | 48 | 18 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37345.1943 | No | 2011398.9963 | 0 | No | 52978.2 | 2103502.2906 | 1051751.1453 | 4207004.5812 | At-Risk | DAC
CA3610051 | VALLEY OF ENCHANTMENT MWC | 1992 | 823 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA4000568 | SAN SIMEON CSD | 462 | 206 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 41105.22 | 41105.22 | 20552.61 | 82210.44 | Not At-Risk | DAC
CA2000593 | OAKHURST MOBILE HOME ESTATES | 164 | 116 | LPA50 - MADERA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 47537.1995 | Yes | 0 | 0 | Yes | 0 | 49317.0995 | 24658.5497 | 98634.199 | At-Risk | SDAC
CA5000237 | NORTH OAKS MUTUAL WATER CO | 234 | 78 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 53687.5474 | Yes | 0 | 0 | No | 128362.2 | 182049.7474 | 91024.8737 | 364099.4948 | Not At-Risk | Non-DAC
CA3600262 | SNOWCREST HEIGHTS IMP ASSOC | 600 | 125 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 110372.2468 | Yes | 0 | 0 | No | 243636.9 | 356323.0168 | 178161.5084 | 712646.0337 | Not At-Risk | Non-DAC
CA5000016 | OID #41 - MOUNTAIN VIEW | 147 | 42 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 46043.5436 | Yes | 0 | 0 | No | 83131.8 | 130955.2436 | 65477.6218 | 261910.4871 | Not At-Risk | Non-DAC
CA0800526 | REDWOOD PARK C.S.D. | 200 | 44 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | SDAC
CA5200014 | WILSON ACRES MUTUAL WATER | 75 | 28 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39717.4714 | No | 2013732.3483 | 0 | No | 65542.2 | 2120771.9196 | 1060385.9598 | 4241543.8393 | Potentially At-Risk | DAC
CA2300605 | RIVER ESTATES MUTUAL WATER COMPANY | 250 | 83 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA5000017 | PARK HEIGHTS MUTUAL WATER CO | 250 | 95 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 55093.3412 | Yes | 0 | 0 | No | 149721 | 204814.3412 | 102407.1706 | 409628.6824 | Not At-Risk | Non-DAC
CA4400608 | FOREST SPRINGS | 385 | 126 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA3900705 | FINNLEES TRAILER PARK | 55 | 26 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 37960.2291 | No | 2012003.9394 | 0 | No | 63029.4 | 2114773.4685 | 1057386.7343 | 4229546.937 | At-Risk | Non-DAC
CA1910169 | WALNUT PARK MUTUAL WATER CO. | 16180 | 2832 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA1900038 | LANCASTER PARK MOBILE HOME PARK | 61 | 21 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 50216.8957 | No | 2527728.2123 | 0 | No | 74906.568 | 2655201.144 | 1327600.572 | 5310402.288 | HR2W | DAC
CA0310003 | AWA, TANNER | 4943 | 1742 | DISTRICT 10 - STOCKTON | C | O - WHOLESALER (SELLS WATER) | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA1500593 | UPLANDS OF THE KERN MUTUAL WATER COMPANY | 80 | 20 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 40156.782 | Yes | 0 | 0 | No | 55491 | 97427.682 | 48713.841 | 194855.3639 | Potentially At-Risk | DAC
CA1700596 | BLUE LAKES VILLAGE | 65 | 44 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2012868.1438 | 0 | No | 85644.6 | 2100292.6438 | 1050146.3219 | 4200585.2876 | At-Risk | DAC
CA3700073 | H & J WATER COMPANY | 50 | 39 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 48955.8652 | No | 2526534.2275 | 0 | Yes | 0 | 2577839.5607 | 1288919.7803 | 5155679.1213 | At-Risk | DAC
CA3310040 | FERN VALLEY WD | 900 | 1175 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 146399.1327 | Yes | 0 | 0 | Yes | 0 | 146399.1327 | 73199.5664 | 292798.2654 | Not At-Risk | Non-DAC
CA1510701 | EDWARDS AFB - MAIN BASE | 12403 | 1058 | DISTRICT 19 - TEHACHAPI | C | NT - INSTITUTION | Yes | 0 | No | 1122881.6039 | Yes | 0 | 0 | No | 1359634.2 | 2482515.8039 | 1241257.902 | 4965031.6079 | Not At-Risk | Non-DAC
CA3610016 | GLEN MARTIN MWC | 450 | 338 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 93427.4107 | Yes | 0 | 0 | No | 591534.06 | 684961.4707 | 342480.7353 | 1369922.9414 | Not At-Risk | DAC
CA5000049 | LONE PINE MHP | 64 | 32 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 38750.9881 | Yes | 0 | 0 | Yes | 0 | 38750.9881 | 19375.4941 | 77501.9763 | Not At-Risk | Non-DAC
CA1000345 | PANOCHE WATER DISTRICT | 146 | 46 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | No | 45955.6814 | N/A | 0 | 0 | No | 88157.4 | 134113.0814 | 67056.5407 | 268226.1629 | HR2W | SDAC
CA3601036 | CALICO LAKE HOMEOWNERS | 150 | 56 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 59537.7384 | Yes | 0 | 0 | Yes | 0 | 61851.6084 | 30925.8042 | 123703.2169 | Potentially At-Risk | SDAC
CA0300016 | VOLCANO COMMUNITY SERVICE DIST | 160 | 80 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 47185.751 | Yes | 0 | 0 | Yes | 0 | 48965.651 | 24482.8255 | 97931.302 | Not At-Risk | DAC
CA3700938 | YUIMA MUNICIPAL WATER DISTRICT IDA | 759 | 232 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 130235.0142 | Yes | 0 | 0 | Yes | 0 | 130235.0142 | 65117.5071 | 260470.0284 | Not At-Risk | SDAC
CA5500057 | LONG BARN PROPERTY OWNERS | 567 | 162 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | Yes | 0 | 0 | No | 233899.8 | 233899.8 | 116949.9 | 467799.6 | Not At-Risk | SDAC
CA4310028 | SAN JOSE STATE UNIVERSITY | 30000 | 54 | DISTRICT 17 - SANTA CLARA | C | NT - SCHOOL | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA5800850 | REBEL RIDGE VILLAGE | 60 | 41 | LPA88 - YUBA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 38399.5397 | No | 2012436.0416 | 0 | No | 50465.4 | 2103080.8813 | 1051540.4406 | 4206161.7626 | At-Risk | DAC
CA3510002 | SAN JUAN BAUTISTA, CITY OF | 2335 | 834 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 306367.5181 | Yes | 0 | 0 | No | 44371.86 | 353053.2481 | 176526.6241 | 706106.4962 | Not At-Risk | Non-DAC
CA2702374 | COUNTRYSIDE ESTATES MWC | 223 | 23 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 2313.87 | No | 67784.2254 | No | 2512887.9916 | 0 | Yes | 0 | 2582986.0869 | 1291493.0435 | 5165972.1739 | Potentially At-Risk | DAC
CA2701822 | ROBLEY PROPERTY MWS | 92 | 33 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 52985.7351 | Yes | 0 | 0 | No | 93371.46 | 148671.0651 | 74335.5326 | 297342.1303 | Not At-Risk | Non-DAC
CA3400335 | HOLIDAY MOBILE VILLAGE | 200 | 115 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 66151.7359 | Yes | 0 | 0 | No | 230800.68 | 299301.8839 | 149650.942 | 598603.7678 | Not At-Risk | SDAC
CA3110017 | SIERRA LAKES COUNTY WATER DIST | 185 | 1223 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 49382.3039 | Yes | 0 | 0 | No | 1063123.8 | 1114286.0039 | 557143.0019 | 2228572.0077 | Not At-Risk | Non-DAC
CA2702588 | CANADA WOODS WC | 610 | 174 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 111501.9026 | Yes | 0 | 0 | Yes | 0 | 111501.9026 | 55750.9513 | 223003.8051 | Not At-Risk | Non-DAC
CA5403084 | FAIRWAY MUTUAL WATER CO | 126 | 45 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 44198.4392 | Yes | 0 | 0 | No | 86901 | 132879.3392 | 66439.6696 | 265758.6783 | Not At-Risk | DAC
CA1200501 | ALDERPOINT COUNTY WATER | 219 | 79 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 129618.6 | 129618.6 | 64809.3 | 259237.2 | At-Risk | SDAC
CA5700797 | MONROE/LEINBERGER CNTR - WATERS | 800 | 10 | LPA87 - YOLO COUNTY | C | INSTITUTION | N/A | 0 | Yes | 0 | No | 0 | 775774.65 | N/A | 0 | 775774.65 | 387887.325 | 1551549.3 | Potentially At-Risk | Non-DAC
CA4300999 | UVAS PINES RV PARK | 86 | 43 | DISTRICT 17 - SANTA CLARA | C | R - MOBILE HOME PARK | No | 2349.468 | No | 53082.8742 | No | 2530441.8142 | 0 | No | 111392.424 | 2697266.5804 | 1348633.2902 | 5394533.1608 | Not At-Risk | Non-DAC
CA2700547 | DESMOND RD WS #03 | 56 | 19 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48918.9745 | No | 2494992.0462 | 0 | No | 70504.98 | 2616729.8706 | 1308364.9353 | 5233459.7413 | At-Risk | Non-DAC
CA4210009 | CUYAMA COMMUNITY SERVICES DISTRICT | 763 | 254 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 128785.6354 | No | 2570755.1205 | 0 | Yes | 0 | 2699540.7559 | 1349770.378 | 5399081.5118 | At-Risk | DAC
CA0409181 | BLUE OAK TERRACE MUTUAL | 50 | 23 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2011571.8372 | 0 | No | 59260.2 | 2070832.0372 | 1035416.0186 | 4141664.0743 | Not At-Risk | SDAC
CA2810004 | ST. HELENA, CITY OF | 6152 | 2681 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 737557.1149 | Yes | 0 | 0 | Yes | 0 | 737557.1149 | 368778.5574 | 1475114.2298 | HR2W | Non-DAC
CA1400110 | PARK WEST MUTUAL WATER COMPANY | 200 | 67 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 50700.2356 | Yes | 0 | 0 | No | 114541.8 | 167021.9356 | 83510.9678 | 334043.8711 | Not At-Risk | Non-DAC
CA4000775 | MUSTANG SPRINGS MUTUAL WATER | 30 | 16 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 45981.8695 | No | 0 | 1008836.85 | No | 65605.02 | 1122737.6095 | 561368.8048 | 2245475.2191 | HR2W | Non-DAC
CA3710004 | DEL MAR, CITY OF | 4268 | 1866 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1300588 | IID VILLAGE | 30 | 18 | LPA43 - IMPERIAL COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 35763.6763 | Yes | 0 | 0 | Yes | 0 | 37543.5763 | 18771.7881 | 75087.1526 | HR2W | SDAC
CA4210005 | SAN VICENTE WATER COMPANY | 550 | 278 | DISTRICT 06 - SANTA BARBARA | C | R - MOBILE HOME PARK | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 493534.86 | 493534.86 | 246767.43 | 987069.72 | Not At-Risk | SDAC
CA3710012 | RANCHO PAUMA MUTUAL WC | 899 | 379 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 146284.4936 | Yes | 0 | 0 | Yes | 0 | 146284.4936 | 73142.2468 | 292568.9871 | Not At-Risk | Non-DAC
CA1310005 | HOLTVILLE, CITY OF | 6355 | 1642 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | DAC
CA4910004 | SWEETWATER SPRINGS CWD - GUERNEVILLE | 6000 | 2565 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA2710016 | LITTLE BEAR WATER COMPANY | 2327 | 705 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | Not At-Risk | Non-DAC
CA4500081 | LAZY LANDING MOBILE HOME PARK | 250 | 110 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 55093.3412 | Yes | 0 | 0 | No | 168567 | 225440.2412 | 112720.1206 | 450880.4824 | Not At-Risk | SDAC
CA4000660 | BEAR VALLEY WATER COMPANY | 45 | 17 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 47676.3531 | Yes | 0 | 0 | Yes | 0 | 49990.2231 | 24995.1116 | 99980.4463 | Not At-Risk | Non-DAC
CA4010901 | SLOCSA #10A - CAYUCOS | 1200 | 771 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 178151.5914 | N/A | 0 | 0 | Yes | 0 | 178151.5914 | 89075.7957 | 356303.1827 | Not At-Risk | Non-DAC
CA4000808 | MONTE SERENO MUTUAL BENEFIT WATER | 60 | 26 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49370.8368 | Yes | 0 | 0 | Yes | 0 | 51684.7068 | 25842.3534 | 103369.4135 | Not At-Risk | Non-DAC
CA1210019 | HYDESVILLE CO. W.D. | 1409 | 419 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA1510043 | CWS-ONYX WATER SYSTEM | 268 | 206 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | SDAC
CA1510039 | CWS SOUTHLAKE SYSTEM | 1394 | 804 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA1910185 | LOS ANGELES CWWD 36-VAL VERDE | 5289 | 1384 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | Yes | 0 | No | 649550.3106 | Yes | 0 | 0 | Yes | 0 | 649550.3106 | 324775.1553 | 1299100.6213 | Not At-Risk | Non-DAC
CA2701789 | HOLLY HILLS MWC | 108 | 27 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 54793.1843 | Yes | 0 | 0 | Yes | 0 | 57107.0543 | 28553.5272 | 114214.1086 | Not At-Risk | Non-DAC
CA3610117 | DEVORE WC | 1633 | 467 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 227065.685 | Yes | 0 | 0 | Yes | 0 | 227065.685 | 113532.8425 | 454131.37 | HR2W | Non-DAC
CA2310002 | ROGINA WATER COMPANY INC. | 3700 | 1016 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA4010016 | LOS OSOS COMMUNITY SERVICES DISTRICT | 7086 | 2772 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 843066.9612 | Yes | 0 | 0 | Yes | 0 | 843066.9612 | 421533.4806 | 1686133.9224 | Not At-Risk | Non-DAC
CA4300760 | SANTA TERESA MEADOWS WATER COMPANY | 68 | 23 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 51019.3697 | Yes | 0 | 0 | Yes | 0 | 53368.8377 | 26684.4188 | 106737.6753 | Not At-Risk | Non-DAC
CA1400034 | KEOUGH'S HOT SPRINGS | 175 | 36 | DISTRICT 13 - SAN BERNARDINO | C | R - MOBILE HOME PARK | Yes | 0 | No | 48503.6827 | Yes | 0 | 0 | No | 75593.4 | 124097.0827 | 62048.5414 | 248194.1654 | Not At-Risk | Non-DAC
CA3900517 | ALMOND PARK WATER SYSTEM | 60 | 20 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 38399.5397 | No | 2012436.0416 | 0 | No | 55491 | 2106326.5813 | 1053163.2906 | 4212653.1626 | At-Risk | Non-DAC
CA4400652 | CATHEDRAL HILLS MWC, INC | 60 | 25 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49370.8368 | Yes | 0 | 0 | Yes | 0 | 51684.7068 | 25842.3534 | 103369.4135 | Not At-Risk | Non-DAC
CA5400940 | SIERRA KING HOMEOWNERS ASSN | 200 | 49 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 50700.2356 | Yes | 0 | 0 | No | 91926.6 | 144406.7356 | 72203.3678 | 288813.4711 | Not At-Risk | SDAC
CA1400026 | RAWSON CREEK MUTUAL WATER COMPANY | 90 | 40 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 41035.4031 | Yes | 0 | 0 | No | 80619 | 123434.3031 | 61717.1515 | 246868.6062 | Not At-Risk | Non-DAC
CA4400604 | BRACKEN BRAE COUNTRY CLUB | 54 | 24 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48693.0433 | Yes | 0 | 0 | Yes | 0 | 51006.9133 | 25503.4567 | 102013.8266 | Not At-Risk | Non-DAC
CA5700700 | CACHEVILLE SERVICE DIST | 400 | 157 | LPA87 - YOLO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 68272.6582 | Yes | 0 | 0 | Yes | 0 | 68272.6582 | 34136.3291 | 136545.3164 | Not At-Risk | SDAC
CA1900303 | LLANO MUTUAL WATER COMPANY | 264 | 78 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 73488.6408 | N/A | 0 | 0 | Yes | 0 | 73488.6408 | 36744.3204 | 146977.2815 | Not At-Risk | SDAC
CA3200127 | ARLINGTON HEIGHTS MHP | 33 | 39 | LPA62 - PLUMAS COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2010102.6896 | 0 | Yes | 0 | 2011882.5896 | 1005941.2948 | 4023765.1793 | Not At-Risk | SDAC
CA4510009 | SHASTA FOREST VILLAGE M.W.C. | 750 | 399 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA1900808 | LANCASTER WATER COMPANY | 80 | 22 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 52395.0393 | Yes | 0 | 0 | Yes | 0 | 54744.5073 | 27372.2537 | 109489.0146 | At-Risk | DAC
CA1510009 | ERSKINE CREEK WC | 2500 | 1111 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | SDAC
CA4200870 | CASMALIA COMMUNITY SERVICES DISTRICT | 234 | 53 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 69026.8467 | Yes | 0 | 0 | Yes | 0 | 71340.7167 | 35670.3583 | 142681.4333 | Not At-Risk | DAC
CA1500452 | RIVERDALE VILLAGE | 750 | 290 | DISTRICT 12 - VISALIA | C | R - MOBILE HOME PARK | Yes | 0 | No | 99024.3979 | Yes | 0 | 0 | No | 394719 | 493743.3979 | 246871.6989 | 987486.7957 | Not At-Risk | SDAC
CA3610022 | DWP - FAWNSKIN | 469 | 724 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | Not At-Risk | DAC
CA4700638 | OAK VALLEY ACRES P.O.A. | 80 | 27 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | No | 40156.782 | Yes | 0 | 0 | No | 64285.8 | 104442.582 | 52221.291 | 208885.1639 | Not At-Risk | Non-DAC
CA1910160 | TRACT 349 MUTUAL WATER CO. | 7500 | 922 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA | Yes | 0 | No | 903017.4454 | Yes | 0 | 0 | Yes | 0 | 903017.4454 | 451508.7227 | 1806034.8907 | Not At-Risk | SDAC
CA2000595 | MADERA MH & RV PARK | 450 | 99 | LPA50 - MADERA COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 72665.7639 | No | 0 | 1667535.96 | Yes | 0 | 1740201.7239 | 870100.8619 | 3480403.4478 | At-Risk | SDAC
CA3900653 | ISLANDER MARINA | 150 | 73 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 46307.1299 | Yes | 0 | 0 | Yes | 0 | 48087.0299 | 24043.5149 | 96174.0598 | Not At-Risk | Non-DAC
CA5800827 | WHISPERING PINES MOBILE HOME PARK | 25 | 19 | LPA88 - YUBA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 35324.3657 | No | 2009411.3261 | 0 | No | 54234.6 | 2100750.1918 | 1050375.0959 | 4201500.3836 | Potentially At-Risk | Missing
CA3610093 | ARROWHEAD VILLAS MUTUAL SERVICE COMPANY | 2654 | 798 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA2900546 | SIERRA FRIENDS CENTER | 125 | 13 | LPA59 - NEVADA COUNTY | C | NT - SCHOOL | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Potentially At-Risk | DAC
CA3702754 | RANCHO CORRIDO RV RESORT | 350 | 120 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 83347.6067 | Yes | 0 | 0 | Yes | 0 | 83347.6067 | 41673.8033 | 166695.2133 | HR2W | SDAC
CA3610023 | GREEN VALLEY MWC | 1350 | 1169 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 195096.4275 | Yes | 0 | 0 | Yes | 0 | 195096.4275 | 97548.2137 | 390192.855 | Not At-Risk | SDAC
CA1500588 | SON SHINE PROPERTIES | 438 | 106 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 71611.4185 | Yes | 0 | 0 | No | 163541.4 | 236932.7185 | 118466.3593 | 473865.437 | HR2W | DAC
CA3301209 | DESERT VIEW TRAILER PARK | 60 | 22 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 50102.2566 | No | 0 | 1093752.738 | No | 76565.016 | 1222769.4786 | 611384.7393 | 2445538.9571 | Potentially At-Risk | SDAC
CA3301028 | BALDY MOUNTAIN RANCH | 144 | 80 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | Yes | 0 | No | 2536737.3707 | 0 | No | 123001.56 | 2662088.3987 | 1331044.1994 | 5324176.7974 | At-Risk | DAC
CA1400135 | WILSON CIRCLE MUTUAL WATER COMPANY | 129 | 48 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 44462.0255 | Yes | 0 | 0 | No | 90670.2 | 136912.1255 | 68456.0628 | 273824.251 | HR2W | Non-DAC
CA3900842 | DOUBLE L MOBILE ESTATES | 320 | 150 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 61243.6891 | Yes | 0 | 0 | No | 218823 | 280066.6891 | 140033.3446 | 560133.3783 | Not At-Risk | DAC
CA3110029 | ALPINE SPRINGS COUNTY WATER DISTRICT | 200 | 658 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA3910701 | DEFENSE DISTRIB. DEPOT, SHARPE SITE | 500 | 70 | DISTRICT 10 - STOCKTON | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 118311 | 118311 | 59155.5 | 236622 | At-Risk | DAC
CA3700933 | PALOMAR MOUNTAIN MUTUAL WATER CO. | 70 | 197 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 51248.6479 | Yes | 0 | 0 | Yes | 0 | 51248.6479 | 25624.324 | 102497.2959 | Not At-Risk | Non-DAC
CA1710006 | KONOCTI COUNTY WATER DISTRICT | 5928 | 1800 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | SDAC
CA1010062 | FCWWD #18/MIRA BELLA | 274 | 50 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1700568 | HARBOR VIEW MUTUAL WATER COMPANY | 550 | 246 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | DAC
CA2000553 | MD 28 RIPPERDAN SELF HELP | 48 | 17 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 37345.1943 | No | 2011398.9963 | 0 | Yes | 0 | 2048744.1906 | 1024372.0953 | 4097488.3812 | HR2W | SDAC
CA4500194 | VILLAGE GREEN | 90 | 32 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 41035.4031 | No | 2015028.6549 | 0 | No | 70567.8 | 2128411.758 | 1064205.879 | 4256823.516 | Not At-Risk | DAC
CA4910003 | PENNGROVE WATER COMPANY (PUC) | 1712 | 520 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1710007 | KELSEYVILLE CO WATERWORKS DISTRICT 3 | 4280 | 1280 | DISTRICT 03 - MENDOCINO | C | O - WHOLESALER (SELLS WATER) | Yes | 0 | No | 409177.6577 | Yes | 0 | 0 | Yes | 0 | 409177.6577 | 204588.8289 | 818355.3155 | Not At-Risk | DAC
CA5403023 | DELFT COLONY WATER | 454 | 99 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 73017.2123 | Yes | 0 | 0 | No | 154746.6 | 227763.8123 | 113881.9062 | 455527.6247 | Not At-Risk | SDAC
CA0810002 | SMITH RIVER C.S.D. | 2568 | 600 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | No | 258757.7198 | Yes | 0 | 0 | Yes | 0 | 258757.7198 | 129378.8599 | 517515.4396 | Not At-Risk | DAC
CA2310007 | NORTH GUALALA WATER COMPANY | 2593 | 1059 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 260954.2726 | Yes | 0 | 0 | Yes | 0 | 260954.2726 | 130477.1363 | 521908.5453 | Not At-Risk | DAC
CA2701355 | PRINCES CAMP RESORT WS | 126 | 55 | LPA57 - MONTEREY COUNTY | C | T - RECREATION AREA | No | 2313.87 | Yes | 0 | No | 2502493.3407 | 0 | No | 129304.5 | 2634111.7107 | 1317055.8553 | 5268223.4213 | At-Risk | Non-DAC
CA1210013 | HUMBOLDT BAY MWD | 680 | 206 | DISTRICT 01 - KLAMATH | C | O - WHOLESALER (SELLS WATER) | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA4200556 | FOSTER ROAD MUTUAL WATER COMPANY | 150 | 49 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 0 | 1407900.9 | Yes | 0 | 1407900.9 | 703950.45 | 2815801.8 | Potentially At-Risk | Non-DAC
CA4700884 | SHASTINA MOBILE ESTATES | 32 | 32 | DISTRICT 01 - KLAMATH | C | T - OTHER TRANSIENT AREA | Yes | 0 | No | 35939.4005 | Yes | 0 | 0 | Yes | 0 | 35939.4005 | 17969.7003 | 71878.801 | Not At-Risk | DAC
CA1503536 | GLENNVILLE MUTUAL WATER COMPANY | 100 | 25 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 41914.0242 | No | 2015892.8593 | 0 | Yes | 0 | 2059586.7836 | 1029793.3918 | 4119173.5671 | Not At-Risk | DAC
CA1503475 | WESTERN ACRES MUTUAL WATER COMPANY | 310 | 90 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 60365.068 | Yes | 0 | 0 | No | 143439 | 205583.968 | 102791.984 | 411167.936 | HR2W | DAC
CA1300555 | MITCHELLS CAMP FAMILY ASSOC. | 175 | 70 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | Yes | 0 | No | 2022374.3926 | 0 | No | 118311 | 2140685.3926 | 1070342.6963 | 4281370.7852 | HR2W | SDAC
CA0800800 | PINE GROVE TRAILER PARK | 100 | 51 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK | No | 1779.9 | No | 41914.0242 | No | 2015892.8593 | 0 | No | 94439.4 | 2154026.1836 | 1077013.0918 | 4308052.3671 | At-Risk | DAC
CA4500094 | RIVERLAND MOBILEHOME PARK | 274 | 93 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 57202.0319 | Yes | 0 | 0 | No | 147208.2 | 206190.1319 | 103095.066 | 412380.2639 | Not At-Risk | SDAC
CA5000019 | RIVERDALE PARK TRACT CSD | 610 | 182 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 86723.702 | No | 0 | 2499178.53 | No | 256515 | 2844197.132 | 1422098.566 | 5688394.264 | HR2W | SDAC
CA5602103 | CYPRESS MUTUAL WATER CO INC | 228 | 68 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA2701904 | SAN JERARDO COOP WS | 249 | 67 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 70721.3303 | No | 2515674.1867 | 0 | Yes | 0 | 2588709.387 | 1294354.6935 | 5177418.7739 | At-Risk | Non-DAC
CA4900612 | HEIGHTS MUTUAL WATER COMPANY | 363 | 110 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 83599.4057 | Yes | 0 | 0 | Yes | 0 | 83599.4057 | 41799.7029 | 167198.8115 | Not At-Risk | Non-DAC
CA3100069 | AUBURN RIDGE WOODS | 131 | 54 | LPA61 - PLACER COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 0 | 1216645.41 | No | 98208.6 | 1316633.91 | 658316.955 | 2633267.82 | At-Risk | SDAC
CA1009028 | HARRIS FARMS SOUTH #101-144 | 160 | 40 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | No | 47185.751 | N/A | 0 | 0 | No | 80619 | 127804.751 | 63902.3755 | 255609.5021 | Potentially At-Risk | SDAC
CA3600123 | HI DESERT MWC | 112 | 42 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA4410001 | BIG BASIN WATER COMPANY | 1120 | 482 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 0 | 6644104.95 | Yes | 0 | 6644104.95 | 3322052.475 | 13288209.9 | At-Risk | Non-DAC
CA1400066 | ASPENDELL MUTUAL WATER COMPANY | 60 | 94 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 38399.5397 | Yes | 0 | 0 | No | 148464.6 | 188644.0397 | 94322.0198 | 377288.0794 | Not At-Risk | Non-DAC
CA2701452 | MONTEREY DUNES MWA | 243 | 124 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 42738.54 | 42738.54 | 21369.27 | 85477.08 | Not At-Risk | Non-DAC
CA3600064 | CAMP WATERMAN MWC | 55 | 30 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 88471.5 | 88471.5 | 44235.75 | 176943 | Not At-Risk | Missing
CA3100061 | SIERRA MEADOWS APARTMENT | 52 | 28 | LPA61 - PLACER COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | No | 37696.6428 | No | 0 | 956130.87 | Yes | 0 | 995607.4128 | 497803.7064 | 1991214.8256 | Not At-Risk | DAC
CA3100011 | AUBURN VALLEY COMMUNITY SERVICE DIS | 290 | 143 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 58607.8258 | Yes | 0 | 0 | Yes | 0 | 60387.7258 | 30193.8629 | 120775.4515 | Not At-Risk | Non-DAC
CA1510703 | CHINA LAKE NAVAL AIR WEAPONS STATION | 5000 | 1380 | DISTRICT 19 - TEHACHAPI | C | NT - INSTITUTION | Yes | 0 | No | 472438.3793 | Yes | 0 | 0 | No | 61773 | 534211.3793 | 267105.6897 | 1068422.7586 | Not At-Risk | Non-DAC
CA3200102 | WHITEHAWK RANCH MWC | 765 | 197 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1000550 | FCSA #44D/MONTE VERDI | 344 | 124 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 31619.4 | 31619.4 | 15809.7 | 63238.8 | Not At-Risk | Non-DAC
CA4400617 | SUMMIT WEST MUTUAL WATER CO. | 468 | 142 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 95460.791 | N/A | 0 | 0 | Yes | 0 | 95460.791 | 47730.3955 | 190921.5821 | Potentially At-Risk | Non-DAC
CA3500900 | ASHFORD HIGHLANDS MWC | 132 | 56 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA3610107 | GOLDEN STATE WATER CO - APPLE VLY SOUTH | 6340 | 1935 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 758794.6428 | Yes | 0 | 0 | Yes | 0 | 758794.6428 | 379397.3214 | 1517589.2857 | Not At-Risk | SDAC
CA4700521 | SISKIYOU CO.SERVICE AREA #5/CARRICK | 142 | 58 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 45604.233 | Yes | 0 | 0 | Yes | 0 | 47384.133 | 23692.0665 | 94768.266 | Not At-Risk | DAC
CA3301107 | CARVER TRACT MUTUAL WATER COMP | 300 | 188 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 77615.6497 | No | 0 | 3124107.702 | Yes | 0 | 3204072.8197 | 1602036.4099 | 6408145.6395 | At-Risk | SDAC
CA0901217 | BEAR STATE WATER WORKS | 100 | 56 | LPA39 - EL DORADO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 53889.4597 | Yes | 0 | 0 | Yes | 0 | 56203.3297 | 28101.6649 | 112406.6594 | Not At-Risk | SDAC
CA3110051 | NORTHSTAR CSD - MARTIS VALLEY | 1218 | 1107 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 140143.8669 | Yes | 0 | 0 | Yes | 0 | 140143.8669 | 70071.9334 | 280287.7338 | Not At-Risk | Non-DAC
CA3610854 | SEARLES VALLEY MINERALS OPERATIONS INC | 1818 | 779 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 247964.3162 | Yes | 0 | 0 | No | 44371.86 | 292336.1762 | 146168.0881 | 584672.3525 | At-Risk | SDAC
CA2900531 | CREEKSIDE VILLAGE | 300 | 131 | LPA59 - NEVADA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2033176.948 | 0 | Yes | 0 | 2034956.848 | 1017478.424 | 4069913.696 | Not At-Risk | SDAC
CA3600027 | BAR "H" MWC | 260 | 45 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 71963.9516 | Yes | 0 | 0 | Yes | 0 | 71963.9516 | 35981.9758 | 143927.9032 | HR2W | SDAC
CA1910153 | SOUTH MONTEBELLO IRRIGATION DIST. | 8205 | 2374 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA | Yes | 0 | No | 983838.0379 | Yes | 0 | 0 | Yes | 0 | 983838.0379 | 491919.0189 | 1967676.0757 | HR2W | DAC
CA1009147 | FARMING D | 110 | 29 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | No | 42792.6454 | N/A | 0 | 0 | No | 66798.6 | 109591.2454 | 54795.6227 | 219182.4907 | HR2W | SDAC
CA1900717 | CASA DULCE ESTATES | 28 | 17 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 46433.8041 | No | 2524146.2578 | 0 | Yes | 0 | 2570580.0619 | 1285290.031 | 5141160.1238 | Not At-Risk | Non-DAC
CA1510051 | LEBEC COUNTY WATER DISTRICT | 1379 | 303 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 154289.6671 | Yes | 0 | 0 | Yes | 0 | 154289.6671 | 77144.8336 | 308579.3342 | HR2W | SDAC
CA5010008 | HUGHSON, CITY OF | 6082 | 2065 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | Non-DAC
CA0405001 | DEL ORO WATER CO.-LIME SADDLE MARINA | 792 | 240 | DISTRICT 21 - VALLEY | C | T - RECREATION AREA | Yes | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA4500062 | LONE TREE MOBILE HOME PARK | 85 | 26 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 40596.0925 | No | 2014596.5527 | 0 | No | 63029.4 | 2120001.9452 | 1060000.9726 | 4240003.8904 | Not At-Risk | SDAC
CA1510023 | LAKE OF THE WOODS MWC | 1103 | 390 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 130039.7238 | Yes | 0 | 0 | Yes | 0 | 130039.7238 | 65019.8619 | 260079.4477 | At-Risk | SDAC
CA3901474 | HESKETT, JOE WATER SYSTEM | 39 | 15 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 36554.4353 | No | 0 | 825873.6 | No | 49209 | 911637.0353 | 455818.5177 | 1823274.0706 | HR2W | SDAC
CA3900624 | IL VINETO | 160 | 83 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 47185.751 | Yes | 0 | 0 | No | 134644.2 | 183609.851 | 91804.9255 | 367219.7021 | Not At-Risk | Non-DAC
CA1700549 | CORINTHIAN BAY MUTUAL WATER COMPANY | 150 | 74 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 46307.1299 | Yes | 0 | 0 | No | 123336.6 | 171423.6299 | 85711.8149 | 342847.2598 | Not At-Risk | DAC
CA1900555 | LOS ANGELES, CITY OF - POWER PLANT #1 | 20 | 19 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA | N/A | 0 | No | 45516.691 | N/A | 0 | 0 | No | 71589.672 | 117106.363 | 58553.1815 | 234212.7261 | At-Risk | Non-DAC
CA1700519 | CRESCENT BAY IMPROVEMENT COMPANY | 30 | 24 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 35763.6763 | N/A | 0 | 0 | No | 60516.6 | 96280.2763 | 48140.1381 | 192560.5526 | HR2W | Non-DAC
CA4500317 | SHASTA CSA - FRENCH GULCH, #11 | 277 | 84 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA5410801 | PORTERVILLE DEVELOPMENTAL CENTER | 1327 | 99 | DISTRICT 24 - TULARE | C | NT - INSTITUTION | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 154746.6 | 154746.6 | 77373.3 | 309493.2 | At-Risk | Non-DAC
CA3410003 | GOLDEN STATE WATER CO - ARDEN WATER SERV | 5154 | 1716 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 634074.027 | Yes | 0 | 0 | No | 924031.944 | 1558105.971 | 779052.9855 | 3116211.9419 | Not At-Risk | DAC
CA3110043 | TAHOE CITY PUD - MADDEN CREEK | 300 | 183 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2033176.948 | 0 | No | 225105 | 2258281.948 | 1129140.974 | 4516563.896 | Not At-Risk | DAC
CA0707547 | KNIGHTSEN COMMUNITY WATER SYSTEM | 250 | 18 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 70834.2959 | No | 0 | 1033022.55 | No | 68871.66 | 1172728.5059 | 586364.2529 | 2345457.0117 | Not At-Risk | Non-DAC
CA0707501 | ANGLER S RANCH #3 | 60 | 32 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 49370.8368 | No | 2495420.6916 | 0 | No | 91738.14 | 2636529.6683 | 1318264.8342 | 5273059.3367 | Not At-Risk | SDAC
CA4910021 | BODEGA BAY PUBLIC UTILITY DISTRICT | 1068 | 1215 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA5410017 | LONDON COMMUNITY SERV DIST | 2138 | 320 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 220977.0111 | Yes | 0 | 0 | No | 432411 | 653388.0111 | 326694.0055 | 1306776.0222 | HR2W | SDAC
CA4900559 | FIRCREST MUTUAL WATER COMPANY | 126 | 47 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 56826.5647 | Yes | 0 | 0 | Yes | 0 | 56826.5647 | 28413.2823 | 113653.1293 | Not At-Risk | Non-DAC
CA4200580 | SAN MARCOS MUTUAL WATER COMPANY | 120 | 33 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 56148.7712 | Yes | 0 | 0 | Yes | 0 | 56148.7712 | 28074.3856 | 112297.5424 | Not At-Risk | Non-DAC
CA0310005 | PINE GROVE COMM SERV DIST | 907 | 388 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | Non-DAC
CA4300578 | ANGELO LANE WATER COMPANY | 52 | 15 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 49185.1435 | No | 2526751.3156 | 0 | Yes | 0 | 2578285.9271 | 1289142.9635 | 5156571.8542 | Not At-Risk | Non-DAC
CA3301482 | ORTEGA OAKS RV PARK&CAMPGROUND | 180 | 77 | LPA63 - RIVERSIDE COUNTY | C | T - RECREATION AREA | No | 2349.468 | No | 63858.9532 | Yes | 0 | 0 | Yes | 0 | 66208.4212 | 33104.2106 | 132416.8423 | At-Risk | Non-DAC
CA3210004 | AMERICAN VALLEY CSD | 4300 | 1607 | DISTRICT 02 - LASSEN | C | O - OTHER AREA | Yes | 0 | No | 410934.9 | Yes | 0 | 0 | Yes | 0 | 410934.9 | 205467.45 | 821869.8 | Not At-Risk | SDAC
CA1510028 | MIL POTRERO MWC | 1600 | 2354 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 173707.1941 | Yes | 0 | 0 | Yes | 0 | 173707.1941 | 86853.5971 | 347414.3883 | Not At-Risk | DAC
CA4110010 | MONTARA WATER AND SANITARY DISTRICT | 5289 | 1673 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 649550.3106 | Yes | 0 | 0 | Yes | 0 | 651899.7786 | 325949.8893 | 1303799.5573 | Not At-Risk | Non-DAC
CA0400151 | KEEFER CREEK ESTATES | 160 | 55 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 99465 | 101244.9 | 50622.45 | 202489.8 | Not At-Risk | Non-DAC
CA0400003 | HARTLEY MUTUAL WATER SYSTEM | 31 | 15 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 35851.5384 | No | 2009929.8487 | 0 | Yes | 0 | 2047561.2872 | 1023780.6436 | 4095122.5743 | Not At-Risk | Missing
CA3910022 | LITTLE POTATO SLOUGH MUTUAL | 950 | 202 | DISTRICT 10 - STOCKTON | C | O - WHOLESALER (SELLS WATER) | N/A | 0 | No | 116596.8205 | N/A | 0 | 0 | Yes | 0 | 116596.8205 | 58298.4103 | 233193.641 | Not At-Risk | DAC
CA1900145 | REESEDALE MUTUAL | 76 | 23 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 51936.4828 | Yes | 0 | 0 | Yes | 0 | 54285.9508 | 27142.9754 | 108571.9015 | Not At-Risk | SDAC
CA1500404 | PINEBROOK COMMUNITY WATER WELL | 68 | 42 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 39102.4366 | Yes | 0 | 0 | No | 83131.8 | 122234.2366 | 61117.1183 | 244468.4732 | Not At-Risk | Missing
CA0707569 | ANGLERS SUBDIVISION 4 | 210 | 89 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 66315.6729 | Yes | 0 | 0 | No | 184837.38 | 251153.0529 | 125576.5264 | 502306.1058 | Not At-Risk | SDAC
CA4910008 | RUSSIAN RIVER COUNTY WATER DISTRICT | 4150 | 1253 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 511400.0353 | Yes | 0 | 0 | Yes | 0 | 511400.0353 | 255700.0177 | 1022800.0706 | Not At-Risk | DAC
CA2910001 | CITY OF GRASS VALLEY | 4947 | 2486 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 467781.6873 | No | 0 | 25584774.69 | No | 32875.8 | 26085432.1773 | 13042716.0887 | 52170864.3546 | Potentially At-Risk | SDAC
CA3600200 | RANCHERITOS MWC | 655 | 286 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 116585.3534 | Yes | 0 | 0 | Yes | 0 | 116585.3534 | 58292.6767 | 233170.7068 | Not At-Risk | DAC
CA5700788 | NORTH DAVIS MEADOWS | 314 | 96 | LPA87 - YOLO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 60716.5165 | Yes | 0 | 0 | No | 150977.4 | 211693.9165 | 105846.9582 | 423387.8329 | HR2W | Non-DAC
CA1900976 | THE OAKS | 67 | 26 | LPA49 - LA COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 2349.468 | No | 50904.7305 | Yes | 0 | 0 | No | 83198.808 | 136453.0065 | 68226.5033 | 272906.013 | Potentially At-Risk | Non-DAC
CA1900158 | LITTLE BALDY WATER | 55 | 36 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 49529.0609 | Yes | 0 | 0 | No | 99783.288 | 151661.8169 | 75830.9084 | 303323.6337 | Not At-Risk | SDAC
CA2800528 | LINDA VISTA MUTUAL WATER CO | 50 | 36 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 48241.181 | Yes | 0 | 0 | Yes | 0 | 48241.181 | 24120.5905 | 96482.362 | Not At-Risk | Non-DAC
CA4900797 | NORTH STAR MOBILE HOME PARK | 75 | 79 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | No | 2313.87 | No | 51065.3204 | No | 0 | 1770686.4 | Yes | 0 | 1824065.5904 | 912032.7952 | 3648131.1807 | Potentially At-Risk | SDAC
CA4300615 | THOUSAND TRAILS - MORGAN HILL | 508 | 320 | DISTRICT 17 - SANTA CLARA | C | T - RECREATION AREA | No | 2349.468 | No | 101460.5905 | No | 2576247.4147 | 0 | No | 570782.52 | 3250839.9932 | 1625419.9966 | 6501679.9864 | Not At-Risk | Non-DAC
CA2900511 | SHADY LAKE WATER ASSOCIATION | 90 | 28 | LPA59 - NEVADA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 41035.4031 | No | 2015028.6549 | 0 | No | 65542.2 | 2123386.158 | 1061693.079 | 4246772.316 | At-Risk | DAC
CA2310011 | LAYTONVILLE COUNTY WATER DISTRICT | 2000 | 413 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA0910007 | LUKINS BROTHERS WATER COMPANY | 3200 | 982 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 1395127.5 | 1395127.5 | 697563.75 | 2790255 | Not At-Risk | Non-DAC
CA4700686 | SUN MOUNTAIN M.W.C. | 55 | 31 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37960.2291 | Yes | 0 | 0 | Yes | 0 | 39740.1291 | 19870.0646 | 79480.2583 | Potentially At-Risk | DAC
CA3900596 | VILLA CEREZOS | 200 | 82 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 50700.2356 | No | 2024534.9037 | 0 | No | 133387.8 | 2208622.9392 | 1104311.4696 | 4417245.8785 | Not At-Risk | SDAC
CA4200505 | CACHUMA VILLAGE | 60 | 24 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2495420.6916 | 0 | Yes | 0 | 2495420.6916 | 1247710.3458 | 4990841.3832 | Potentially At-Risk | SDAC
CA1300009 | WINTERHAVEN COUNTY WATER DISTRICT | 660 | 124 | LPA43 - IMPERIAL COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | SDAC
CA5400935 | CWS - MULLEN WATER COMPANY | 138 | 42 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 45252.7845 | Yes | 0 | 0 | Yes | 0 | 45252.7845 | 22626.3923 | 90505.5691 | Not At-Risk | SDAC
CA2010017 | TESORO VIEJO MASTER MWC, INC. | 2640 | 301 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | N/A | 0 | No | 265083.792 | Yes | 0 | 0 | Yes | 0 | 265083.792 | 132541.896 | 530167.5839 | Not At-Risk | Missing
CA3600008 | APPLE VALLEY FOOTHILL CWD | 729 | 218 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 124944.8059 | Yes | 0 | 0 | Yes | 0 | 127258.6759 | 63629.338 | 254517.3518 | Not At-Risk | Non-DAC
CA4100510 | REDWOOD TERRACE MUTUAL | 43 | 17 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | Non-DAC
CA1410503 | NPS - DEATH VALLEY, COW CREEK/NEVARES | 88 | 61 | DISTRICT 13 - SAN BERNARDINO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | No | 40859.6789 | N/A | 0 | 0 | No | 107003.4 | 147863.0789 | 73931.5394 | 295726.1577 | At-Risk | SDAC
CA3103835 | LAKEVIEW HILLS COMMUNITY ASSOC | 499 | 152 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 76971.0074 | N/A | 0 | 0 | No | 221335.8 | 298306.8074 | 149153.4037 | 596613.6149 | Not At-Risk | Non-DAC
CA5410503 | NPS-WOLVERTON | 2940 | 125 | DISTRICT 12 - VISALIA | C | T - RECREATION AREA | No | 1779.9 | No | 291442.4259 | Yes | 0 | 0 | Yes | 0 | 293222.3259 | 146611.163 | 586444.6519 | HR2W | Non-DAC
CA1010501 | NPS-GRANT GROVE | 2950 | 100 | DISTRICT 23 - FRESNO | C | T - RECREATION AREA | No | 1779.9 | No | 292321.0471 | Yes | 0 | 0 | No | 156003 | 450103.9471 | 225051.9735 | 900207.8942 | Not At-Risk | DAC
CA1500371 | UNION PACIFIC RAILROAD CO.-KEENE WATER | 208 | 26 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | N/A | 0 | No | 51403.1325 | N/A | 0 | 0 | Yes | 0 | 51403.1325 | 25701.5662 | 102806.2649 | At-Risk | Missing
CA2600622 | SIERRA EAST HOA | 84 | 30 | LPA56 - MONO COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 40508.2304 | Yes | 0 | 0 | No | 68055 | 110343.1304 | 55171.5652 | 220686.2608 | HR2W | DAC
CA3500579 | VINEYARD ESTATES MWC | 90 | 26 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 52759.804 | No | 2498635.5321 | 0 | Yes | 0 | 2553709.2061 | 1276854.603 | 5107418.4121 | Potentially At-Risk | Non-DAC
CA4900665 | RUSSIAN RIVER MUTUAL WATER CO. | 84 | 30 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 52082.0105 | No | 2497992.564 | 0 | No | 88471.5 | 2640859.9445 | 1320429.9723 | 5281719.889 | Not At-Risk | Non-DAC
CA1200541 | PHILLIPSVILLE C.S.D. | 300 | 66 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 59486.4469 | Yes | 0 | 0 | No | 112029 | 173295.3469 | 86647.6734 | 346590.6938 | Not At-Risk | SDAC
CA4000744 | AFUERA DE CHORRO WATER COMPANY | 79 | 24 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 51517.1827 | Yes | 0 | 0 | Yes | 0 | 51517.1827 | 25758.5913 | 103034.3653 | At-Risk | Non-DAC
CA4010017 | GOLDEN STATE WATER COMPANY - LOS OSOS | 5518 | 2684 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 665936.9408 | Yes | 0 | 0 | Yes | 0 | 665936.9408 | 332968.4704 | 1331873.8817 | Not At-Risk | Non-DAC
CA2000692 | MD 95 RANCHOS WEST | 150 | 27 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 46307.1299 | Yes | 0 | 0 | Yes | 0 | 46307.1299 | 23153.5649 | 92614.2598 | Not At-Risk | Non-DAC
CA4500195 | STARLITE PINES MUTUAL WATER CO INC | 510 | 165 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 237669 | 239448.9 | 119724.45 | 478897.8 | Not At-Risk | SDAC
CA5000095 | SUNRISE VILLAGE MHP | 339 | 103 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 62913.0693 | Yes | 0 | 0 | Yes | 0 | 64692.9693 | 32346.4847 | 129385.9386 | Not At-Risk | SDAC
CA2300668 | POINT CABRILLO HIGHLANDS | 42 | 21 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK | No | 1779.9 | No | 36818.0217 | No | 2010880.4736 | 0 | No | 56747.4 | 2106225.7953 | 1053112.8976 | 4212451.5906 | Not At-Risk | Non-DAC
CA3400125 | FREEPORT MARINA | 42 | 27 | LPA64 - SACRAMENTO COUNTY | C | T - RECREATION AREA | Yes | 0 | No | 48038.7521 | Yes | 0 | 0 | No | 84857.256 | 132896.0081 | 66448.004 | 265792.0161 | Not At-Risk | DAC
CA3610053 | WESTERN HEIGHTS WATER COMPANY | 7521 | 2340 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 892206.986 | Yes | 0 | 0 | Yes | 0 | 892206.986 | 446103.493 | 1784413.972 | Not At-Risk | Non-DAC
CA4400571 | DAVENPORT COUNTY SANITATION | 350 | 108 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | No | 68871.66 | 68871.66 | 34435.83 | 137743.32 | Not At-Risk | Non-DAC
CA1900537 | OAK GROVE FAMILY PARK | 109 | 40 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 55719.5743 | No | 2532938.328 | 0 | Yes | 0 | 2591007.3704 | 1295503.6852 | 5182014.7407 | At-Risk | Non-DAC
CA1900961 | WINTERHAVEN MOBILE ESTATES | 56 | 20 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 49643.7 | No | 2527185.4919 | 0 | No | 73248.12 | 2652426.7799 | 1326213.39 | 5304853.5599 | HR2W | DAC
CA4200616 | SKYLINE PARK | 300 | 95 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 76482.5746 | Yes | 0 | 0 | No | 194637.3 | 271119.8746 | 135559.9373 | 542239.7491 | Not At-Risk | Non-DAC
CA4400684 | APTOS RIDGE MUTUAL WATER CO | 52 | 16 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 48467.1122 | No | 2494563.4008 | 0 | Yes | 0 | 2543030.5129 | 1271515.2565 | 5086061.0259 | At-Risk | Non-DAC
CA3600031 | BIG PINE TRACT | 300 | 136 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 76482.5746 | Yes | 0 | 0 | No | 261603.42 | 338085.9946 | 169042.9973 | 676171.9891 | Not At-Risk | DAC
CA3600156 | LUCERNE VALLEY MWC | 275 | 69 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 73658.4352 | Yes | 0 | 0 | Yes | 0 | 75972.3052 | 37986.1526 | 151944.6104 | Not At-Risk | SDAC
CA2300609 | SEAFAIR ROAD AND WATER COMPANY | 50 | 31 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37520.9186 | Yes | 0 | 0 | Yes | 0 | 39300.8186 | 19650.4093 | 78601.6371 | Not At-Risk | Non-DAC
CA4500093 | RED HILL MOBILEHOME PARK | 35 | 24 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 36202.9869 | Yes | 0 | 0 | Yes | 0 | 37982.8869 | 18991.4434 | 75965.7737 | Not At-Risk | SDAC
CA3701408 | YUIMA MUNICIPAL WATER DISTRICT | 350 | 106 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 83347.6067 | Yes | 0 | 0 | Yes | 0 | 83347.6067 | 41673.8033 | 166695.2133 | Not At-Risk | SDAC
CA2700771 | SPRINGFIELD WATER COMPANY | 200 | 34 | LPA57 - MONTEREY COUNTY | C | T - SECONDARY RESIDENCES | Yes | 0 | No | 65186.0171 | No | 2510423.2806 | 0 | No | 95004.78 | 2670614.0777 | 1335307.0388 | 5341228.1554 | HR2W | Non-DAC
CA2110350 | NPS GGNRA | 18447 | 227 | DISTRICT 25 - MARIN | C | T - RECREATION AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA2210503 | YOSEMITE NPS-YOSEMITE VALLEY | 1000 | 235 | DISTRICT 11 - MERCED | C | T - RECREATION AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA4000765 | VARIAN RANCH MUTUAL WATER | 111 | 49 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 55132.081 | Yes | 0 | 0 | Yes | 0 | 55132.081 | 27566.0405 | 110264.1621 | Not At-Risk | Non-DAC
CA4910026 | ODD FELLOWS RECREATION CLUB | 309 | 268 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 477201.66 | 479515.53 | 239757.765 | 959031.06 | Not At-Risk | DAC
CA5410019 | IVANHOE PUBLIC UTILITY DIST | 4495 | 1118 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 428068.0121 | Yes | 0 | 0 | Yes | 0 | 428068.0121 | 214034.006 | 856136.0242 | At-Risk | SDAC
CA3310052 | LAKE HEMET-GARNER VALLEY | 709 | 307 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 124503.0573 | Yes | 0 | 0 | Yes | 0 | 124503.0573 | 62251.5287 | 249006.1146 | Not At-Risk | DAC
CA4300516 | ALDERCROFT HEIGHTS COUNTY WATER DISTRICT | 338 | 116 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 81971.937 | N/A | 0 | 0 | Yes | 0 | 81971.937 | 40985.9685 | 163943.874 | Not At-Risk | Non-DAC
CA2100508 | MUIR BEACH COMMUNITY | 336 | 161 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 80549.3352 | Yes | 0 | 0 | Yes | 0 | 80549.3352 | 40274.6676 | 161098.6705 | Not At-Risk | Non-DAC
CA4300520 | RAINERI MUTUAL WATER COMPANY | 145 | 44 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA2702409 | EL CAMINO WC INC | 133 | 21 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | No | 2503243.4701 | 0 | Yes | 0 | 2505557.3401 | 1252778.6701 | 5011114.6802 | HR2W | Non-DAC
CA1210007 | DEL ORO WATER CO-FERNDALE | 1998 | 785 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | No | 208676.3152 | Yes | 0 | 0 | No | 41670.6 | 250346.9152 | 125173.4576 | 500693.8305 | Not At-Risk | SDAC
CA4510015 | DEL ORO WATER CO.-JOHNSON PARK | 917 | 278 | DISTRICT 02 - LASSEN | C | T - RECREATION AREA | Yes | 0 | No | 113697.3708 | Yes | 0 | 0 | Yes | 0 | 113697.3708 | 56848.6854 | 227394.7416 | Not At-Risk | SDAC
CA1400031 | RANCH ROAD ESTATES MUTUAL WATER COMPANY | 65 | 27 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 38838.8503 | Yes | 0 | 0 | No | 64285.8 | 103124.6503 | 51562.3251 | 206249.3005 | Not At-Risk | Non-DAC
CA4900799 | EL PORTAL MOBILE ESTATES | 200 | 122 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | No | 2313.87 | No | 65186.0171 | Yes | 0 | 0 | No | 238736.94 | 306236.8271 | 153118.4136 | 612473.6543 | At-Risk | SDAC
CA1500555 | MUSTANG MUTUAL WATER SYSTEM | 200 | 51 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | N/A | 0 | N/A | 0 | 0 | No | 94439.4 | 96219.3 | 48109.65 | 192438.6 | HR2W | Non-DAC
CA3400150 | DELTA CROSSING MHP | 30 | 22 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 46663.0824 | No | 2524363.3459 | 0 | No | 76565.016 | 2649940.9124 | 1324970.4562 | 5299881.8247 | Not At-Risk | DAC
CA1200592 | BIG LAGOON CSD | 112 | 42 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA3500550 | SAN JUSTO MUTUAL WATER COMPANY | 160 | 60 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 60667.3942 | No | 2506136.8266 | 0 | Yes | 0 | 2566804.2207 | 1283402.1104 | 5133608.4415 | Potentially At-Risk | Missing
CA4000749 | TERRA DE ORO WATER COMPANY | 38 | 17 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 46885.5941 | Yes | 0 | 0 | No | 67238.34 | 116437.8041 | 58218.9021 | 232875.6082 | Not At-Risk | Non-DAC
CA4900570 | PALOMINO LAKES MUTUAL WATER CO. | 250 | 113 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2515781.348 | 0 | Yes | 0 | 2515781.348 | 1257890.674 | 5031562.6961 | Potentially At-Risk | Non-DAC
CA5400710 | BADGER HILL ESTATES | 272 | 98 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 57026.3077 | Yes | 0 | 0 | Yes | 0 | 58806.2077 | 29403.1039 | 117612.4154 | Not At-Risk | Non-DAC
CA5000408 | WESTLEY CSD | 70 | 35 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 74337 | 74337 | 37168.5 | 148674 | At-Risk | DAC
CA3301267 | FISHERMAN'S RETREAT | 402 | 172 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 89308.8418 | No | 2564741.7425 | 0 | No | 325332.216 | 2981732.2684 | 1490866.1342 | 5963464.5368 | HR2W | Non-DAC
CA0800556 | HRC C.S.D. | 150 | 54 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 46307.1299 | No | 2020213.8815 | 0 | No | 98208.6 | 2166509.5114 | 1083254.7557 | 4333019.0228 | Not At-Risk | DAC
CA5410022 | CAMP NELSON WATER COMPANY | 122 | 301 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | No | 407283 | 407283 | 203641.5 | 814566 | Not At-Risk | SDAC
CA2701263 | PARTINGTON MWC | 35 | 26 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA4110012 | CUESTA LA HONDA GUILD INC | 832 | 297 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 138603.6713 | Yes | 0 | 0 | Yes | 0 | 140953.1393 | 70476.5697 | 281906.2786 | HR2W | Non-DAC
CA1200715 | GREEN DIAMOND RESOURCE COMPANY - KORBEL | 250 | 18 | DISTRICT 01 - KLAMATH | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | No | 55093.3412 | Yes | 0 | 0 | No | 51721.8 | 108595.0412 | 54297.5206 | 217190.0824 | Not At-Risk | DAC
CA2701364 | PEDRAZZI MWC | 273 | 96 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 73432.5041 | No | 2518246.0591 | 0 | No | 196270.62 | 2790263.0531 | 1395131.5266 | 5580526.1063 | Potentially At-Risk | Non-DAC
CA5000061 | MARTIN'S MOBILE HOME COURT | 60 | 20 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 38399.5397 | No | 2012436.0416 | 0 | No | 55491 | 2108106.4813 | 1054053.2406 | 4216212.9626 | HR2W | SDAC
CA4500003 | MEL MAR MUTUAL WATER CO | 300 | 91 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2033176.948 | 0 | No | 144695.4 | 2177872.348 | 1088936.174 | 4355744.696 | Not At-Risk | Non-DAC
CA0707598 | CAMINO MOBILEHOME | 210 | 75 | LPA37 - CONTRA COSTA COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | Yes | 0 | No | 2511494.8941 | 0 | No | 161970.9 | 2675779.6641 | 1337889.832 | 5351559.3281 | Potentially At-Risk | DAC
CA1200547 | MILL CREEK M.W.C. | 65 | 36 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 38838.8503 | Yes | 0 | 0 | No | 75593.4 | 116212.1503 | 58106.0751 | 232424.3005 | Not At-Risk | SDAC
CA5000060 | CASA DE AMIGOS MOBILE HOME PARK | 220 | 73 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 52457.4778 | No | 2026263.3125 | 0 | No | 122080.2 | 2200800.9904 | 1100400.4952 | 4401601.9807 | Not At-Risk | Non-DAC
CA1500314 | DEL ORO WC - COUNTRY ESTATES DIST | 297 | 90 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2032917.6867 | 0 | Yes | 0 | 2032917.6867 | 1016458.8433 | 4065835.3734 | HR2W | SDAC
CA4900514 | RANCHO DEL PARADISO-CAL WATER SVC (PUC) | 162 | 60 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA4400618 | RIDGE MUTUAL WATER COMPANY | 240 | 76 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 69704.6401 | N/A | 0 | 0 | Yes | 0 | 69704.6401 | 34852.3201 | 139409.2802 | Not At-Risk | Non-DAC
CA1110003 | CAL-WATER SERVICE CO.-WILLOWS | 7153 | 2387 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 661605.5092 | Yes | 0 | 0 | Yes | 0 | 661605.5092 | 330802.7546 | 1323211.0184 | At-Risk | SDAC
CA1010017 | FCWWD #41/SHAVER LAKE | 2037 | 960 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 212102.9377 | Yes | 0 | 0 | Yes | 0 | 212102.9377 | 106051.4688 | 424205.8753 | Not At-Risk | Non-DAC
CA3110013 | TAHOE CITY PUD - TAHOE CEDARS | 793 | 1181 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 1456377 | 1456377 | 728188.5 | 2912754 | Not At-Risk | Non-DAC
CA3301045 | BLYTHE MOBILE HOME ESTATES | 35 | 25 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 47236.2781 | No | 2524906.0663 | 0 | No | 81540.36 | 2656032.1724 | 1328016.0862 | 5312064.3449 | HR2W | SDAC
CA4900603 | RIEBLI MUTUAL WATER COMPANY | 150 | 47 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 59537.7384 | Yes | 0 | 0 | No | 116237.94 | 178089.5484 | 89044.7742 | 356179.0969 | Not At-Risk | Non-DAC
CA3301330 | INDIAN OAKS TRAILER PARK | 90 | 63 | LPA63 - RIVERSIDE COUNTY | C | T - OTHER TRANSIENT AREA | No | 2349.468 | No | 53541.4307 | No | 2530875.9906 | 0 | No | 144561.384 | 2731328.2733 | 1365664.1366 | 5462656.5465 | HR2W | Missing
CA2010009 | BAKMAN WATER-ROLLING HILLS | 1106 | 339 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 130303.3102 | Yes | 0 | 0 | No | 456282.6 | 586585.9102 | 293292.9551 | 1173171.8204 | Potentially At-Risk | Non-DAC
CA3701961 | PINE VALLEY TRAILER PARK | 200 | 92 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 66151.7359 | Yes | 0 | 0 | No | 192656.376 | 258808.1119 | 129404.056 | 517616.2238 | Potentially At-Risk | Non-DAC
CA4900646 | ALEXANDER VALLEY ACRES WATER COMPANY | 37 | 16 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 46772.6285 | Yes | 0 | 0 | Yes | 0 | 49086.4985 | 24543.2493 | 98172.9971 | Not At-Risk | Missing
CA5410007 | LSID - TONYVILLE | 500 | 50 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 77058.8695 | Yes | 0 | 0 | Yes | 0 | 77058.8695 | 38529.4348 | 154117.7391 | HR2W | SDAC
CA1600507 | HARDWICK WATER COMPANY | 69 | 20 | LPA46 - KINGS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39190.2987 | No | 2013213.8256 | 0 | Yes | 0 | 2054184.0243 | 1027092.0122 | 4108368.0486 | At-Risk | Non-DAC
CA2710020 | PAJARO COMMUNITY SERVICES DISTRICT | 6500 | 461 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 776869.1347 | Yes | 0 | 0 | Yes | 0 | 776869.1347 | 388434.5674 | 1553738.2694 | Not At-Risk | Non-DAC
CA3600071 | CHAMISAL MWC | 63 | 29 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49709.7335 | No | 2495742.1756 | 0 | Yes | 0 | 2547765.7791 | 1273882.8896 | 5095531.5582 | HR2W | SDAC
CA3610033 | MT BALDY HOMEOWNERS ASSN. | 1700 | 112 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 219137.1 | 219137.1 | 109568.55 | 438274.2 | Not At-Risk | Non-DAC
CA3610032 | NEEDLES, CITY OF | 5183 | 1706 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 628093.4735 | Yes | 0 | 0 | Yes | 0 | 630407.3435 | 315203.6717 | 1260814.687 | HR2W | SDAC
CA3900569 | EL RIO MOBILE HOME PARK | 60 | 28 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 38399.5397 | Yes | 0 | 0 | No | 65542.2 | 105721.6397 | 52860.8198 | 211443.2794 | Potentially At-Risk | Missing
CA1010026 | PINEDALE COUNTY WATER DISTRICT | 16735 | 2120 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1503500.2787 | Yes | 0 | 0 | No | 2530599 | 4034099.2787 | 2017049.6393 | 8068198.5573 | Not At-Risk | DAC
CA4500104 | SUNRISE MOBILEHOME PARK | 35 | 16 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 36202.9869 | No | 2010275.5305 | 0 | No | 50465.4 | 2098723.8174 | 1049361.9087 | 4197447.6348 | Not At-Risk | DAC
CA3010068 | EAST ORANGE COUNTY WD - RZ | 3247 | 1206 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 409392.1218 | Yes | 0 | 0 | Yes | 0 | 409392.1218 | 204696.0609 | 818784.2436 | Not At-Risk | Non-DAC
CA4900580 | SONOMA MOUNTAIN COUNTY WATER DISTRICT | 181 | 55 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1000005 | BIG CREEK COMMUNITY SERV DIST | 72 | 67 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 46696.2 | 46696.2 | 23348.1 | 93392.4 | Not At-Risk | Non-DAC
CA0900422 | CRYSTAL CAVES MHP | 112 | 40 | LPA39 - EL DORADO COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 55245.0466 | No | 2500993.0818 | 0 | No | 104804.7 | 2663356.6984 | 1331678.3492 | 5326713.3968 | Not At-Risk | DAC
CA2700612 | LAGUNA SECA WC | 162 | 58 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 60893.3253 | Yes | 0 | 0 | No | 134204.46 | 197411.6553 | 98705.8277 | 394823.3106 | HR2W | Non-DAC
CA2701800 | TULARCITOS MWC | 129 | 46 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 57165.4614 | Yes | 0 | 0 | Yes | 0 | 59479.3314 | 29739.6657 | 118958.6627 | Not At-Risk | Non-DAC
CA1200718 | WADDINGTON W.W. | 75 | 25 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | N/A | 0 | No | 2013732.3483 | 0 | Yes | 0 | 2015512.2483 | 1007756.1241 | 4031024.4965 | Not At-Risk | SDAC
CA2000509 | CASCADEL MUTUAL WATER SYSTEM | 314 | 120 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 60716.5165 | Yes | 0 | 0 | Yes | 0 | 62496.4165 | 31248.2082 | 124992.8329 | Not At-Risk | SDAC
CA2000647 | JOHN HOVANNISIAN WATER SYSTEM | 80 | 18 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 40156.782 | Yes | 0 | 0 | Yes | 0 | 41936.682 | 20968.341 | 83873.3639 | HR2W | SDAC
CA4900608 | SIX ACRES WATER COMPANY | 66 | 22 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 50048.6302 | No | 2496063.6597 | 0 | Yes | 0 | 2548426.1599 | 1274213.0799 | 5096852.3198 | HR2W | DAC
CA2600699 | CHALFANT VALLEY WEST M.W.C. | 45 | 15 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 49209 | 50988.9 | 25494.45 | 101977.8 | Not At-Risk | SDAC
CA0400008 | GRAN MUTUAL WATER CO | 200 | 105 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 98208.6 | 98208.6 | 49104.3 | 196417.2 | Not At-Risk | Non-DAC
CA2600546 | CROWLEY LAKE MUTUAL WATER COMPANY | 175 | 57 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 48503.6827 | No | 2022374.3926 | 0 | No | 101977.8 | 2174635.7753 | 1087317.8877 | 4349271.5506 | Potentially At-Risk | Non-DAC
CA2700509 | OAK MANOR WS | 92 | 28 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 52985.7351 | Yes | 0 | 0 | Yes | 0 | 55299.6051 | 27649.8026 | 110599.2103 | Not At-Risk | Non-DAC
CA0800532 | BIG ROCK C.S.D. | 400 | 107 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | No | 68272.6582 | No | 2041818.9923 | 0 | Yes | 0 | 2110091.6506 | 1055045.8253 | 4220183.3011 | Not At-Risk | DAC
CA3100538 | ROSECREST MUTUAL | 31 | 15 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 35851.5384 | No | 2009929.8487 | 0 | No | 49209 | 2096770.2872 | 1048385.1436 | 4193540.5743 | Not At-Risk | DAC
CA1000054 | LAS DELTAS MUTUAL WATER SYSTEM | 375 | 107 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 66076.1054 | N/A | 0 | 0 | No | 163541.4 | 229617.5054 | 114808.7527 | 459235.0108 | HR2W | SDAC
CA1200566 | ORLEANS MUTUAL WATER CO. | 85 | 38 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 78106.2 | 78106.2 | 39053.1 | 156212.4 | Potentially At-Risk | SDAC
CA3900664 | NEW HOPE LANDING GENERAL STORE | 125 | 44 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 44110.5771 | No | 2018053.3704 | 0 | No | 85644.6 | 2147808.5475 | 1073904.2737 | 4295617.095 | Not At-Risk | DAC
CA5710009 | UC - DAVIS | 48828 | 686 | DISTRICT 09 - SACRAMENTO | C | NT - SCHOOL | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 534179.4 | 534179.4 | 267089.7 | 1068358.8 | Not At-Risk | SDAC
CA1810003 | LASSEN COUNTY WATER DISTRICT #1 | 450 | 147 | DISTRICT 02 - LASSEN | C | O - OTHER AREA | No | 1779.9 | No | 72665.7639 | Yes | 0 | 0 | No | 215053.8 | 289499.4639 | 144749.7319 | 578998.9278 | Potentially At-Risk | SDAC
CA4901309 | HILTON MUTUAL WATER COMPANY | 100 | 16 | DISTRICT 18 - SONOMA | C | O - OTHER AREA | No | 2313.87 | Yes | 0 | No | 2499707.1456 | 0 | No | 63971.7 | 2565992.7156 | 1282996.3578 | 5131985.4312 | Not At-Risk | SDAC
CA4200837 | RANCHO YNECITA | 129 | 39 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 57165.4614 | Yes | 0 | 0 | Yes | 0 | 59479.3314 | 29739.6657 | 118958.6627 | At-Risk | Non-DAC
CA2000557 | MD 43 MIAMI CREEK KNOLLS | 100 | 26 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 41914.0242 | Yes | 0 | 0 | Yes | 0 | 41914.0242 | 20957.0121 | 83828.0485 | Not At-Risk | DAC
CA3610703 | USMC - 29 PALMS | 18811 | 2480 | DISTRICT 13 - SAN BERNARDINO | C | NT - INSTITUTION | Yes | 0 | No | 2167588.3189 | Yes | 0 | 0 | No | 3799374.54 | 5966962.8589 | 2983481.4295 | 11933925.7179 | Not At-Risk | SDAC
CA1500585 | OASIS PROPERTY OWNERS ASSOCIATION | 100 | 39 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 41914.0242 | Yes | 0 | 0 | No | 79362.6 | 123056.5242 | 61528.2621 | 246113.0485 | HR2W | SDAC
CA3301169 | MURRIETA PALMS MOBILE HOME PARK | 237 | 71 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 70393.384 | No | 0 | 1693074.384 | Yes | 0 | 1763467.768 | 881733.884 | 3526935.5361 | Not At-Risk | Non-DAC
CA4910019 | FORESTVILLE WATER DISTRICT | 3291 | 997 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA3400433 | EDGEWATER MOBILE HOME PARK | 40 | 22 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 47809.4738 | Yes | 0 | 0 | No | 76565.016 | 126723.9578 | 63361.9789 | 253447.9156 | At-Risk | SDAC
CA3301040 | RIVERDALE ESTATES | 300 | 186 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 77615.6497 | No | 0 | 3099645.594 | No | 348550.488 | 3528161.1997 | 1764080.5999 | 7056322.3995 | Potentially At-Risk | SDAC
CA2000849 | MD 60 DILLON ESTATES | 150 | 38 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 46307.1299 | No | 2020213.8815 | 0 | Yes | 0 | 2066521.0114 | 1033260.5057 | 4133042.0228 | At-Risk | DAC
CA4500107 | ZUFALL'S MOBILEHOME PARK | 96 | 78 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 128362.2 | 130142.1 | 65071.05 | 260284.2 | Not At-Risk | SDAC
CA1010049 | BIOLA COMMUNITY SERVICES DIST | 1623 | 1200 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 175728.0228 | Yes | 0 | 0 | Yes | 0 | 177507.9228 | 88753.9614 | 355015.8455 | At-Risk | SDAC
CA3410007 | DEL PASO MANOR COUNTY WATER DI | 4520 | 1796 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 561392.8133 | Yes | 0 | 0 | No | 2849490.072 | 3410882.8853 | 1705441.4426 | 6821765.7706 | Not At-Risk | Non-DAC
CA1503329 | HART CREEK ESTATES MUTUAL WATER CO. | 148 | 73 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 46131.4057 | Yes | 0 | 0 | Yes | 0 | 46131.4057 | 23065.7028 | 92262.8113 | Not At-Risk | Non-DAC
CA1100237 | WILLOWS MOBILE HOME COMMUNITY & RV PARK | 190 | 87 | DISTRICT 21 - VALLEY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 49821.6144 | No | 2023670.6992 | 0 | No | 139669.8 | 2214942.0137 | 1107471.0068 | 4429884.0273 | At-Risk | SDAC
CA0400036 | MOUNTAIN VIEW MHC LLC | 230 | 129 | LPA34-BUTTE COUNTY | C | MOBILE HOME PARK | No | 1779.9 | No | 53336.099 | No | 0 | 1968129.66 | No | 192438.6 | 2215684.259 | 1107842.1295 | 4431368.5179 | Potentially At-Risk | SDAC
CA3700909 | JULIAN COMMUNITY SERVICES DISTRICT | 1517 | 185 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 217131.481 | Yes | 0 | 0 | Yes | 0 | 217131.481 | 108565.7405 | 434262.9621 | Not At-Risk | Non-DAC
CA2210515 | YOSEMITE NPS-EL PORTAL | 635 | 235 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | SDAC
CA2702325 | FERNWOOD WS | 133 | 17 | LPA57 - MONTEREY COUNTY | C | T - HOTEL/MOTEL | No | 2313.87 | Yes | 0 | No | 2503243.4701 | 0 | No | 67238.34 | 2572795.6801 | 1286397.8401 | 5145591.3602 | Potentially At-Risk | DAC
CA5301002 | LEWISTON COMMUNITY SERVICES DISTRICT | 701 | 231 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 94719.1543 | Yes | 0 | 0 | Yes | 0 | 96499.0543 | 48249.5272 | 192998.1086 | Not At-Risk | DAC
CA4500007 | VERDE VALE WATER COMPANY | 356 | 108 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 166054.2 | 167834.1 | 83917.05 | 335668.2 | Not At-Risk | SDAC
CA2300506 | MEADOW ESTATES MUTUAL | 100 | 35 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 41914.0242 | Yes | 0 | 0 | Yes | 0 | 43693.9242 | 21846.9621 | 87387.8485 | Not At-Risk | SDAC
CA0500075 | LAKESIDE MOBILE ESTATES | 54 | 24 | LPA35 - CALAVERAS COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 37872.367 | No | 2011917.5189 | 0 | No | 60516.6 | 2112086.386 | 1056043.193 | 4224172.7719 | Potentially At-Risk | Missing
CA3510004 | AROMAS WATER DISTRICT | 2988 | 968 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 380134.0381 | Yes | 0 | 0 | Yes | 0 | 380134.0381 | 190067.019 | 760268.0761 | Not At-Risk | Non-DAC
CA0410003 | DURHAM IRRIGATION DISTRICT | 1561 | 479 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 170280.5717 | Yes | 0 | 0 | No | 202489.8 | 374550.2717 | 187275.1359 | 749100.5435 | Not At-Risk | Non-DAC
CA1500409 | BROCK MUTUAL WATER COMPANY | 462 | 155 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 73720.1092 | Yes | 0 | 0 | No | 225105 | 300605.0092 | 150302.5046 | 601210.0185 | HR2W | DAC
CA4901346 | DELORES LANE WATER SYSTEM | 56 | 17 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48918.9745 | Yes | 0 | 0 | Yes | 0 | 51232.8445 | 25616.4222 | 102465.6889 | Not At-Risk | SDAC
CA1000004 | BELMONT WATER CORPORATION | 264 | 40 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 56323.4108 | Yes | 0 | 0 | No | 80619 | 136942.4108 | 68471.2054 | 273884.8216 | HR2W | Non-DAC
CA4610002 | DOWNIEVILLE PUBLIC U.D. | 783 | 234 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | Non-DAC
CA4300560 | GREEN MOUNTAIN WATER COMPANY | 80 | 38 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 52395.0393 | No | 2529790.5498 | 0 | Yes | 0 | 2582185.5891 | 1291092.7946 | 5164371.1782 | Not At-Risk | Non-DAC
CA5410038 | TERRA BELLA IRRIGATION DISTRICT - TBT | 4957 | 803 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 468660.3084 | Yes | 0 | 0 | Yes | 0 | 468660.3084 | 234330.1542 | 937320.6169 | Potentially At-Risk | SDAC
CA1910117 | MONTEBELLO-CITY, WATER DEPT. | 8157 | 1503 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA | Yes | 0 | No | 978335.3592 | Yes | 0 | 0 | Yes | 0 | 978335.3592 | 489167.6796 | 1956670.7184 | Not At-Risk | DAC
CA1000472 | PG&E HELMS SUPPORT FACILITY | 40 | 22 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2010707.6327 | 0 | No | 58003.8 | 2068711.4327 | 1034355.7164 | 4137422.8655 | At-Risk | DAC
CA5400754 | SOUTH KAWEAH MUTUAL WATER COMPANY | 384 | 138 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 66866.8644 | Yes | 0 | 0 | Yes | 0 | 68646.7644 | 34323.3822 | 137293.5288 | At-Risk | Non-DAC
CA5401003 | EAST OROSI CSD | 932 | 103 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 115015.3025 | Yes | 0 | 0 | No | 159772.2 | 276567.4025 | 138283.7012 | 553134.805 | HR2W | SDAC
CA3100528 | GOLDEN HILLS MUTUAL WATER CO | 84 | 32 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA4900647 | SERENO DEL MAR WATER COMPANY (PUC) | 435 | 136 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 91732.9271 | Yes | 0 | 0 | Yes | 0 | 91732.9271 | 45866.4635 | 183465.8542 | Not At-Risk | DAC
CA4510002 | MOUNTAIN GATE C.S.D. | 2227 | 669 | DISTRICT 02 - LASSEN | C | O - OTHER AREA | No | 1779.9 | No | 228796.7392 | Yes | 0 | 0 | Yes | 0 | 230576.6392 | 115288.3196 | 461153.2784 | Not At-Risk | SDAC
CA2300507 | CALPELLA COUNTY WATER DISTRICT | 548 | 185 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA5200574 | DEL ORO WC - LARKSPUR MEADOWS | 112 | 34 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Missing
CA2900548 | SIERRA ESTATES MUTUAL WATER COMPANY | 100 | 32 | LPA59 - NEVADA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 41914.0242 | No | 2015892.8593 | 0 | Yes | 0 | 2059586.7836 | 1029793.3918 | 4119173.5671 | Potentially At-Risk | SDAC
CA5400665 | DEL ORO RIVER ISLAND SERV TERR #1 | 1296 | 397 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 146997.1117 | Yes | 0 | 0 | Yes | 0 | 146997.1117 | 73498.5559 | 293994.2234 | HR2W | DAC
CA3400107 | RIVER'S EDGE MARINA & RESORT | 150 | 83 | LPA64 - SACRAMENTO COUNTY | C | T - RECREATION AREA | No | 2349.468 | No | 60419.779 | No | 2537388.6352 | 0 | No | 177730.344 | 2777888.2262 | 1388944.1131 | 5555776.4523 | Not At-Risk | SDAC
CA3600187 | OLIVE DELL RANCH | 350 | 100 | LPA66 - SAN BERNARDINO COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 2313.87 | No | 82130.8533 | Yes | 0 | 0 | No | 202803.9 | 287248.6233 | 143624.3116 | 574497.2466 | Not At-Risk | DAC
CA5210003 | LOS MOLINOS COMM. SERVICES DIST. | 1450 | 376 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 160527.8772 | Yes | 0 | 0 | Yes | 0 | 160527.8772 | 80263.9386 | 321055.7543 | HR2W | SDAC
CA3610701 | USMC NEBO (BARSTOW) | 1150 | 419 | DISTRICT 13 - SAN BERNARDINO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 720566.34 | 720566.34 | 360283.17 | 1441132.68 | Not At-Risk | SDAC
CA5800572 | FAIRWAY DOWNS MUTUAL WATER CO | 100 | 27 | LPA88 - YUBA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 41914.0242 | No | 2015892.8593 | 0 | No | 64285.8 | 2123872.5836 | 1061936.2918 | 4247745.1671 | Not At-Risk | Non-DAC
CA1800511 | LAKE FOREST MUTUAL W.C. | 565 | 220 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 82769.9069 | Yes | 0 | 0 | No | 306771 | 391320.8069 | 195660.4035 | 782641.6138 | Not At-Risk | DAC
CA4010015 | MORRO ROCK MUTUAL WATER CO | 1881 | 649 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 255081.1474 | Yes | 0 | 0 | Yes | 0 | 255081.1474 | 127540.5737 | 510162.2948 | Not At-Risk | DAC
CA4900639 | REDWOOD HEIGHTS MUTUAL WATER COMPANY | 30 | 18 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2492205.8511 | 0 | No | 68871.66 | 2561077.5111 | 1280538.7555 | 5122155.0222 | HR2W | Non-DAC
CA1000369 | ZONNEVELD DAIRY - CEDAR | 70 | 15 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | No | 39278.1608 | No | 2013300.246 | 0 | No | 49209 | 2103567.3069 | 1051783.6534 | 4207134.6137 | At-Risk | SDAC
CA1400005 | OWENS VALLEY WATER COMPANY | 300 | 111 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 59486.4469 | Yes | 0 | 0 | No | 169823.4 | 229309.8469 | 114654.9234 | 458619.6938 | Not At-Risk | Non-DAC
CA2510002 | CEDARVILLE COUNTY WATER DIST. | 500 | 290 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA4200842 | SAINT MARIE MOBILE HOME PARK | 315 | 80 | LPA72 - SANTA BARBARA COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | N/A | 0 | No | 0 | 1782779.25 | No | 170137.5 | 1955230.62 | 977615.31 | 3910461.24 | HR2W | DAC
CA5500074 | SIERRA VILLAGE MUTUAL WATER CO | 272 | 129 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 57026.3077 | Yes | 0 | 0 | Yes | 0 | 57026.3077 | 28513.1539 | 114052.6154 | Not At-Risk | Non-DAC
CA2701423 | ECHO VALLEY RD WS #05 | 45 | 16 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 47676.3531 | Yes | 0 | 0 | No | 65605.02 | 115595.2431 | 57797.6216 | 231190.4863 | Not At-Risk | Non-DAC
CA2700713 | ROLLING HILLS RANCHO WA | 184 | 56 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | At-Risk | Non-DAC
CA1900520 | THE VILLAGE MOBILE HOME PARK | 50 | 34 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 48955.8652 | No | 0 | 1240525.386 | Yes | 0 | 1291830.7192 | 645915.3596 | 2583661.4383 | HR2W | DAC
CA2701515 | MOSS LANDING HARBOR WS | 402 | 143 | LPA57 - MONTEREY COUNTY | C | T - SECONDARY RESIDENCES | Yes | 0 | No | 88005.0631 | Yes | 0 | 0 | Yes | 0 | 88005.0631 | 44002.5316 | 176010.1263 | Not At-Risk | Non-DAC
CA3210009 | CHESTER PUBLIC U.D. | 2316 | 1209 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | No | 1779.9 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Potentially At-Risk | DAC
CA4901381 | LICHAU HYLANDS MUTUAL WATER COMPANY | 56 | 20 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48918.9745 | Yes | 0 | 0 | Yes | 0 | 51232.8445 | 25616.4222 | 102465.6889 | Not At-Risk | Non-DAC
CA4200862 | MESA HILLS MUTUAL WATER COMPANY | 54 | 18 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 48693.0433 | Yes | 0 | 0 | No | 42738.54 | 91431.5833 | 45715.7917 | 182863.1666 | Not At-Risk | Non-DAC
CA2800532 | VAILIMA ESTATES MUTUAL WATER | 25 | 15 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | Not At-Risk | Non-DAC
CA1310800 | CALIPATRIA STATE PRISON | 4800 | 2001 | DISTRICT 14 - SAN DIEGO | C | NT - INSTITUTION | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 2544419.4 | 2544419.4 | 1272209.7 | 5088838.8 | Not At-Risk | Missing
CA5500353 | SIERRA VILLAGE MOBILE HOME PARK | 30 | 30 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK | No | 1779.9 | No | 35763.6763 | No | 2009843.4283 | 0 | No | 68055 | 2115442.0046 | 1057721.0023 | 4230884.0092 | HR2W | Non-DAC
CA2800516 | TUCKER ACRES MUTUAL WATER CO. | 200 | 23 | LPA58 - NAPA COUNTY | C | NT - INDUSTRIAL/AGRICULTURAL | No | 2313.87 | No | 65186.0171 | Yes | 0 | 0 | Yes | 0 | 67499.8871 | 33749.9436 | 134999.7743 | Not At-Risk | Non-DAC
CA5000433 | OID-OAKDALE RURAL WATER SYSTEM #1 | 1570 | 476 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 171071.3308 | Yes | 0 | 0 | Yes | 0 | 172851.2308 | 86425.6154 | 345702.4615 | Not At-Risk | Non-DAC
CA0202503 | WOODFORDS MUTUAL WATER COMPANY | 50 | 16 | LPA32 - ALPINE COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 50465.4 | 52245.3 | 26122.65 | 104490.6 | Not At-Risk | SDAC
CA5400536 | KINGS RIVER ESTATES MUTUAL WATER COMPANY | 106 | 38 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 42441.1969 | Yes | 0 | 0 | No | 78106.2 | 120547.3969 | 60273.6985 | 241094.7938 | Not At-Risk | DAC
CA2700579 | ELKHORN RD WS #04 | 60 | 20 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 49370.8368 | No | 2495420.6916 | 0 | No | 72138.3 | 2616929.8283 | 1308464.9142 | 5233859.6567 | HR2W | Non-DAC
CA3900543 | MAURLAND MANOR WATER SYSTEM | 110 | 28 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 42792.6454 | N/A | 0 | 0 | No | 65542.2 | 108334.8454 | 54167.4227 | 216669.6907 | Not At-Risk | Non-DAC
CA1200729 | ORLEANS C.S.D. | 636 | 167 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | SDAC
CA3910010 | SAN JOAQUIN COUNTY - LINCOLN VILLAGE | 5990 | 1815 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 2279319 | 2279319 | 1139659.5 | 4558638 | Not At-Risk | Non-DAC
CA3210001 | IVCSD-GREENVILLE | 1129 | 576 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 132324.1388 | Yes | 0 | 0 | Yes | 0 | 134104.0388 | 67052.0194 | 268208.0776 | Potentially At-Risk | SDAC
CA3901113 | WALNUT ACRES | 100 | 32 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 70567.8 | 70567.8 | 35283.9 | 141135.6 | At-Risk | SDAC
CA2701295 | ESALEN INSTITUTE WS | 246 | 42 | LPA57 - MONTEREY COUNTY | C | NT - INSTITUTION | N/A | 0 | N/A | 0 | Yes | 0 | 0 | No | 108071.34 | 108071.34 | 54035.67 | 216142.68 | Not At-Risk | DAC
CA3400137 | LINCOLN CHAN-HOME RANCH | 33 | 19 | LPA64 - SACRAMENTO COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 47006.9998 | Yes | 0 | 0 | No | 71589.672 | 120946.1398 | 60473.0699 | 241892.2796 | At-Risk | SDAC
CA0400020 | PLEASANT GROVE MHP | 327 | 88 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 61858.7239 | Yes | 0 | 0 | No | 140926.2 | 204564.8239 | 102282.412 | 409129.6479 | Not At-Risk | SDAC
CA3500904 | HOLLISTER RANCH ESTATES | 150 | 37 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 59537.7384 | Yes | 0 | 0 | No | 99904.74 | 159442.4784 | 79721.2392 | 318884.9569 | At-Risk | Non-DAC
CA4500092 | RIVER BREEZE MOBILE HOME PARK | 87 | 32 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2014769.3936 | 0 | No | 70567.8 | 2087117.0936 | 1043558.5468 | 4174234.1871 | Not At-Risk | SDAC
CA1200706 | TRINIDAD EXTENDED STAY RV | 130 | 72 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK | N/A | 0 | No | 44549.8876 | N/A | 0 | 0 | No | 120823.8 | 165373.6876 | 82686.8438 | 330747.3753 | Not At-Risk | SDAC
CA1400004 | CHARLES BROWN WATER COMPANY | 242 | 31 | DISTRICT 13 - SAN BERNARDINO | C | T - SECONDARY RESIDENCES | N/A | 0 | No | 54390.4443 | N/A | 0 | 0 | No | 69311.4 | 123701.8443 | 61850.9222 | 247403.6886 | At-Risk | SDAC
CA4700880 | SISKIYOU LAKE HIGHLANDS MWC | 100 | 83 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | SDAC
CA1000378 | SUNSET WEST COMMUNITY LLC | 350 | 159 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK | No | 1779.9 | No | 63879.5525 | Yes | 0 | 0 | No | 230130.6 | 295790.0525 | 147895.0263 | 591580.1051 | Not At-Risk | SDAC
CA4900871 | DE ANZA MOON VALLEY WATER COMPANY | 691 | 247 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | Yes | 0 | No | 120652.1141 | No | 0 | 3802285.2 | No | 442901.94 | 4365839.2541 | 2182919.627 | 8731678.5082 | Not At-Risk | Non-DAC
CA4200822 | SANTA RITA WATER | 59 | 18 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | Non-DAC
CA1000244 | SHADY LAKES MOBILE HOME PARK | 160 | 65 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK | Yes | 0 | No | 47185.751 | No | 2021078.0859 | 0 | Yes | 0 | 2068263.837 | 1034131.9185 | 4136527.6739 | Potentially At-Risk | SDAC
CA3900721 | WOODBRIDGE MOBILE ESTATES | 110 | 37 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 42792.6454 | No | 2016757.0638 | 0 | No | 76849.8 | 2138179.4091 | 1069089.7046 | 4276358.8183 | At-Risk | Non-DAC
CA5601116 | SAN CAYETANO MUTUAL WATER CO | 46 | 50 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 48497.3086 | Yes | 0 | 0 | No | 51688.296 | 100185.6046 | 50092.8023 | 200371.2092 | Not At-Risk | Non-DAC
CA3700866 | DEL DIOS MUTUAL WATER COMPANY | 330 | 150 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 2349.468 | 1174.734 | 4698.936 | At-Risk | Non-DAC
CA2210901 | MPWD-COULTERVILLE CSA 1 | 193 | 98 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 50085.2008 | No | 2023929.9606 | 0 | Yes | 0 | 2074015.1613 | 1037007.5807 | 4148030.3227 | At-Risk | SDAC
CA1400144 | SUNLAND VILLAGE MOBILE HOME PARK | 42 | 26 | DISTRICT 13 - SAN BERNARDINO | C | R - MOBILE HOME PARK | Yes | 0 | No | 36818.0217 | No | 2010880.4736 | 0 | No | 63029.4 | 2110727.8953 | 1055363.9476 | 4221455.7906 | Not At-Risk | Non-DAC
CA1610001 | ARMONA COMMUNITY SERVICES DIST | 4143 | 1246 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 397140.5482 | Yes | 0 | 0 | No | 31619.4 | 428759.9482 | 214379.9741 | 857519.8964 | At-Risk | DAC
CA3100043 | GOLD HILL MOBILEHOME PARK | 75 | 32 | LPA61 - PLACER COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 39717.4714 | No | 2013732.3483 | 0 | No | 70567.8 | 2125797.5196 | 1062898.7598 | 4251595.0393 | Not At-Risk | Non-DAC
CA1009023 | BRITZ/COLUSA | 85 | 15 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | No | 40596.0925 | N/A | 0 | 0 | No | 49209 | 89805.0925 | 44902.5463 | 179610.1851 | Not At-Risk | SDAC
CA2910011 | PLAVADA COMMUNITY ASSOCIATION | 359 | 255 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 64670.3116 | Yes | 0 | 0 | No | 156003 | 220673.3116 | 110336.6558 | 441346.6231 | Potentially At-Risk | Non-DAC
CA5000082 | 4N MOBILEHOME PARK | 65 | 31 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 38838.8503 | No | 2012868.1438 | 0 | Yes | 0 | 2051706.9941 | 1025853.497 | 4103413.9882 | Potentially At-Risk | Non-DAC
CA1000056 | MEADOW LAKES CLUB | 240 | 120 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 54214.7201 | Yes | 0 | 0 | No | 181131 | 237125.6201 | 118562.81 | 474251.2402 | Not At-Risk | DAC
CA1910147 | SATIVA WATER SYSTEM | 6837 | 1643 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA | Yes | 0 | No | 827011.6967 | Yes | 0 | 0 | No | 2764909.224 | 3591920.9207 | 1795960.4603 | 7183841.8414 | Potentially At-Risk | Non-DAC
CA1510002 | BORON CSD | 2253 | 627 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 34132.2 | 34132.2 | 17066.1 | 68264.4 | Not At-Risk | SDAC
CA1310700 | NAF EL CENTRO | 972 | 386 | DISTRICT 14 - SAN DIEGO | C | T - SECONDARY RESIDENCES | N/A | 0 | No | 118529.787 | N/A | 0 | 0 | No | 453769.8 | 572299.587 | 286149.7935 | 1144599.174 | Not At-Risk | DAC
CA5000010 | TID/ LA GRANGE WATER SYSTEM | 195 | 59 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 50260.925 | Yes | 0 | 0 | Yes | 0 | 50260.925 | 25130.4625 | 100521.85 | Not At-Risk | DAC
CA2701658 | ARROYO CENTER WC | 130 | 60 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 137471.1 | 139784.97 | 69892.485 | 279569.94 | Not At-Risk | DAC
CA1900075 | BLEICH FLATS MUTUAL | 93 | 34 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 53885.3481 | Yes | 0 | 0 | Yes | 0 | 56234.8161 | 28117.4081 | 112469.6322 | Not At-Risk | DAC
CA3400103 | B & W RESORT MARINA | 100 | 37 | LPA64 - SACRAMENTO COUNTY | C | T - RECREATION AREA | No | 2349.468 | No | 54687.8221 | Yes | 0 | 0 | No | 101441.736 | 158479.0261 | 79239.513 | 316958.0522 | Not At-Risk | SDAC
CA2701906 | LAKE SAN ANTONIO PARK WS | 54 | 30 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 48693.0433 | No | 2494777.7235 | 0 | Yes | 0 | 2545784.6368 | 1272892.3184 | 5091569.2736 | Potentially At-Risk | SDAC
CA4900521 | GILL CREEK MUTUAL WATER COMPANY | 232 | 92 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 68800.9155 | Yes | 0 | 0 | Yes | 0 | 68800.9155 | 34400.4578 | 137601.831 | Not At-Risk | Non-DAC
CA4500255 | SACRAMENTO RIVER RV PARK | 382 | 156 | LPA75 - SHASTA COUNTY | C | T - OTHER TRANSIENT AREA | Yes | 0 | No | 66691.1402 | No | 2040263.4244 | 0 | No | 226361.4 | 2333315.9645 | 1166657.9823 | 4666631.9291 | Not At-Risk | SDAC
CA1700502 | ANDERSON SPRINGS CSD | 331 | 130 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | Non-DAC
CA5000067 | TULLY MOBILE ESTATES | 40 | 15 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 36642.2974 | No | 2010707.6327 | 0 | No | 36645 | 2085774.8302 | 1042887.4151 | 4171549.6603 | At-Risk | Missing
CA3600158 | LYTLE SPRINGS WC | 475 | 141 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 126037.86 | 128351.73 | 64175.865 | 256703.46 | Not At-Risk | SDAC
CA3900563 | GAYLA MANOR PWS | 146 | 54 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 45955.6814 | No | 2019868.1997 | 0 | No | 98208.6 | 2164032.4812 | 1082016.2406 | 4328064.9623 | Potentially At-Risk | Non-DAC
CA2300708 | RIDGEWOOD WATER SYSTEM | 220 | 167 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | N/A | 0 | Yes | 0 | 0 | No | 240181.8 | 241961.7 | 120980.85 | 483923.4 | Not At-Risk | SDAC
CA3910017 | SAN JOAQUIN COUNTY-MOKELUMNE ACRES | 3800 | 1151 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | No | 367003.8434 | Yes | 0 | 0 | No | 1471453.8 | 1838457.6434 | 919228.8217 | 3676915.2867 | Not At-Risk | Non-DAC
CA3200188 | GREENHORN CREEK CSD | 280 | 136 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 57729.2046 | Yes | 0 | 0 | Yes | 0 | 59509.1046 | 29754.5523 | 119018.2092 | Not At-Risk | SDAC
CA3900722 | MORADA ESTATES PWS | 158 | 88 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 47010.0268 | Yes | 0 | 0 | No | 140926.2 | 187936.2268 | 93968.1134 | 375872.4536 | At-Risk | Non-DAC
CA5200510 | RIVER RANCH MOBILE HOME PARK | 305 | 109 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 59925.7575 | No | 2033609.0502 | 0 | No | 167310.6 | 2262625.3077 | 1131312.6538 | 4525250.6154 | Not At-Risk | SDAC
CA4900687 | BROOKWOOD MOBILE HOME PARK | 400 | 202 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | Yes | 0 | No | 87779.132 | Yes | 0 | 0 | No | 369402.54 | 457181.672 | 228590.836 | 914363.344 | Not At-Risk | SDAC
CA2310004 | WILLITS, CITY OF | 6175 | 2418 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA4910023 | CALIFORNIA-AMERICAN LARKFIELD (PUC) | 7524 | 2284 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 892545.8827 | Yes | 0 | 0 | Yes | 0 | 892545.8827 | 446272.9414 | 1785091.7654 | Not At-Risk | Non-DAC
CA2010007 | CAL AM - OAKHURST | 3403 | 1032 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | Non-DAC
CA1500556 | HART FLAT BEAR MUTUAL WATER | 56 | 28 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 38048.0912 | Yes | 0 | 0 | Yes | 0 | 38048.0912 | 19024.0456 | 76096.1825 | Not At-Risk | Non-DAC
CA1210002 | BLUE LAKE, CITY OF | 1253 | 704 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA1900721 | TERRA NOVA MOBILE HOME PARK | 140 | 75 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 59273.3876 | No | 0 | 1741998.6 | No | 164462.76 | 1968084.2156 | 984042.1078 | 3936168.4312 | At-Risk | SDAC
CA1300572 | VALLEY MOBILE HOME PARK | 70 | 22 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK | N/A | 0 | No | 39278.1608 | N/A | 0 | 0 | No | 35388.6 | 74666.7608 | 37333.3804 | 149333.5217 | At-Risk | Missing
CA4200827 | SANTA YNEZ ROBLAR MOBILE HOME PARK | 25 | 19 | LPA72 - SANTA BARBARA COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 45417.0417 | No | 2491670.0443 | 0 | No | 70504.98 | 2609905.936 | 1304952.968 | 5219811.872 | Not At-Risk | DAC
CA5500149 | COLUMBIA MOBILE HOME PARK | 88 | 63 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK | No | 1779.9 | No | 40859.6789 | No | 2014855.814 | 0 | No | 109516.2 | 2167011.5929 | 1083505.7964 | 4334023.1858 | Potentially At-Risk | SDAC
CA4800753 | VINEYARD RV PARK | 365 | 360 | DISTRICT 04 - SAN FRANCISCO | C | R - MOBILE HOME PARK | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 624200.46 | 626514.33 | 313257.165 | 1253028.66 | Not At-Risk | Non-DAC
CA4910028 | SWEETWATER SPRINGS CWD - MONTE RIO | 3000 | 1197 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA4300994 | COYOTE VALLEY RV RESORT | 500 | 129 | DISTRICT 17 - SANTA CLARA | C | R - MOBILE HOME PARK | No | 2349.468 | No | 100543.4774 | No | 2575379.0621 | 0 | No | 254018.952 | 2932290.9595 | 1466145.4797 | 5864581.9189 | Not At-Risk | Non-DAC
CA1910165 | VALLEY VIEW MUTUAL WATER CO. | 4571 | 1389 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA3301018 | ANZA PINES MOBILE HOME PARK | 150 | 47 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 60419.779 | Yes | 0 | 0 | No | 118026.216 | 180795.463 | 90397.7315 | 361590.926 | Not At-Risk | SDAC
CA3610085 | SAN ANTONIO WATER COMPANY | 3371 | 1214 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 423399.853 | Yes | 0 | 0 | Yes | 0 | 423399.853 | 211699.9265 | 846799.706 | Not At-Risk | Non-DAC
CA1100404 | DEL ORO WC - BLACK BUTTE DISTRICT | 284 | 85 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2031794.2209 | 0 | Yes | 0 | 2031794.2209 | 1015897.1105 | 4063588.4418 | Potentially At-Risk | SDAC
CA3301534 | RANCHO CALIMESA MOBILE HOME PARK | 302 | 207 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA2000549 | MD 05 MOUNTAIN RANCHES | 239 | 27 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 54126.858 | Yes | 0 | 0 | Yes | 0 | 54126.858 | 27063.429 | 108253.7159 | At-Risk | DAC
CA5601105 | FILLMORE IRRIGATION CO | 353 | 236 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 83691.5241 | Yes | 0 | 0 | Yes | 0 | 83691.5241 | 41845.762 | 167383.0481 | Not At-Risk | Non-DAC
CA4900675 | ROSELAND MOBILE HOME PARK | 130 | 70 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | No | 2313.87 | No | 57278.4269 | Yes | 0 | 0 | No | 153804.3 | 213396.5969 | 106698.2985 | 426793.1939 | Not At-Risk | SDAC
CA5100112 | TIERRA BUENA MHP #1 | 50 | 17 | DISTRICT 21 - VALLEY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 37520.9186 | No | 2011571.8372 | 0 | No | 51721.8 | 2102594.4557 | 1051297.2279 | 4205188.9115 | At-Risk | Non-DAC
CA1310801 | CENTINELA STATE PRISON | 4600 | 2001 | DISTRICT 14 - SAN DIEGO | C | NT - INSTITUTION | N/A | 0 | No | 437293.534 | N/A | 0 | 0 | No | 2544419.4 | 2981712.934 | 1490856.467 | 5963425.868 | Not At-Risk | DAC
CA1500341 | SIERRA BELLA MUTUAL WATER COMPANY | 60 | 180 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 38399.5397 | Yes | 0 | 0 | Yes | 0 | 40179.4397 | 20089.7198 | 80358.8794 | Not At-Risk | Missing
CA3600222 | JUNIPER RIVIERA CWD | 441 | 250 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 92410.7205 | Yes | 0 | 0 | Yes | 0 | 94724.5905 | 47362.2953 | 189449.1811 | HR2W | SDAC
CA2700842 | BAUMANN RD WS #01 | 40 | 17 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 47111.5253 | No | 2493277.4646 | 0 | No | 67238.34 | 2609941.1999 | 1304970.5999 | 5219882.3997 | Potentially At-Risk | Non-DAC
CA4000222 | AVILA BEACH COMMUNITY SERVICES DISTRICT | 1630 | 388 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA2210905 | MCCLURE BOAT CLUB, INC. | 282 | 66 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 112029 | 112029 | 56014.5 | 224058 | Not At-Risk | SDAC
CA3610118 | APPLE VALLEY RANCHOS WATER CO - YERMO | 1033 | 316 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 159286.3405 | Yes | 0 | 0 | Yes | 0 | 159286.3405 | 79643.1702 | 318572.6809 | Not At-Risk | DAC
CA1000019 | FCSA #30/EL PORVENIR | 241 | 56 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 54302.5822 | N/A | 0 | 0 | Yes | 0 | 54302.5822 | 27151.2911 | 108605.1644 | HR2W | SDAC
CA3301863 | OLIVET UNIVERSITY | 195 | 48 | LPA63 - RIVERSIDE COUNTY | C | NT - INSTITUTION | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 79881.912 | 79881.912 | 39940.956 | 159763.824 | Not At-Risk | Missing
CA3210007 | WEST ALMANOR M.W.C. | 1394 | 500 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 155607.5988 | Yes | 0 | 0 | Yes | 0 | 155607.5988 | 77803.7994 | 311215.1976 | Not At-Risk | Non-DAC
CA2110004 | STINSON BEACH COUNTY WTR DIST | 1500 | 741 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA3710039 | PINE VALLEY MUTUAL WC | 2500 | 719 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 329821.754 | Yes | 0 | 0 | Yes | 0 | 329821.754 | 164910.877 | 659643.5079 | Not At-Risk | Non-DAC
CA5201147 | GOLDEN MEADOWS CSD | 102 | 49 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 42089.7485 | No | 2016065.7002 | 0 | No | 91926.6 | 2151861.9487 | 1075930.9743 | 4303723.8974 | Not At-Risk | Non-DAC
CA4010081 | WOODLANDS DEVELOPMENT | 2918 | 1276 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 372226.4479 | Yes | 0 | 0 | Yes | 0 | 374540.3179 | 187270.1589 | 749080.6357 | Not At-Risk | Non-DAC
CA1000260 | SANDY CREEK VILLAGE MHP | 88 | 45 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK | No | 1779.9 | No | 40859.6789 | Yes | 0 | 0 | No | 86901 | 129540.5789 | 64770.2894 | 259081.1577 | Not At-Risk | DAC
CA5400567 | TOOLEVILLE MUTUAL NON PROFIT WATER ASSOC | 340 | 77 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 63000.9314 | Yes | 0 | 0 | No | 127105.8 | 191886.6314 | 95943.3157 | 383773.2628 | At-Risk | Missing
CA3301528 | OAK HAVEN ASSOCIATION | 92 | 36 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 53770.709 | Yes | 0 | 0 | No | 99783.288 | 155903.465 | 77951.7325 | 311806.93 | Not At-Risk | Non-DAC
CA1010034 | SAN JOAQUIN, CITY OF | 4060 | 730 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | SDAC
CA1010339 | CALIFORNIA STATE UNIVERSITY FRESNO | 41000 | 159 | DISTRICT 12 - VISALIA | C | NT - SCHOOL | Yes | 0 | N/A | 0 | Yes | 0 | 0 | No | 230130.6 | 230130.6 | 115065.3 | 460261.2 | Not At-Risk | SDAC
CA0310011 | FIRST MACE MEADOW # 1 | 838 | 337 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA0707615 | DOUBLETREE RANCH WATER SYSTEM | 49 | 20 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48128.2154 | Yes | 0 | 0 | Yes | 0 | 50442.0854 | 25221.0427 | 100884.1709 | Not At-Risk | Non-DAC
CA2701036 | APPLE AVE WS #03 | 60 | 20 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49370.8368 | No | 0 | 1057208.25 | Yes | 0 | 1108892.9568 | 554446.4784 | 2217785.9135 | HR2W | DAC
CA5800820 | RIVER HIGHLANDS CSD | 200 | 84 | LPA88 - YUBA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 50700.2356 | Yes | 0 | 0 | Yes | 0 | 52480.1356 | 26240.0678 | 104960.2711 | Not At-Risk | DAC
CA3900682 | LOCKEFORD MOBILE HOME PARK WTR SYS | 100 | 43 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 41914.0242 | No | 2015892.8593 | 0 | No | 84388.2 | 2143974.9836 | 1071987.4918 | 4287949.9671 | Potentially At-Risk | DAC
CA1100405 | BLACK BUTTE MOBILE H.P. | 148 | 49 | DISTRICT 21 - VALLEY | NP/C | RESIDENTIAL AREA | Yes | 0 | No | 46131.4057 | No | 2020041.0406 | 0 | No | 91926.6 | 2158099.0463 | 1079049.5231 | 4316198.0926 | Not At-Risk | DAC
CA1900542 | LOS ANGELES, CITY OF - POWER PLANT #2 | 41 | 16 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA | N/A | 0 | No | 47924.1129 | N/A | 0 | 0 | No | 63297.432 | 111221.5449 | 55610.7725 | 222443.0899 | At-Risk | DAC
CA4300545 | SARATOGA HEIGHTS MUTUAL WATER COMPANY | 258 | 92 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA5700615 | YOLO CO HOUSING AUTHORITY-EL RIO VILLA | 432 | 113 | LPA87 - YOLO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 71084.2458 | Yes | 0 | 0 | Yes | 0 | 71084.2458 | 35542.1229 | 142168.4917 | At-Risk | SDAC
CA0410001 | CITY OF BIGGS | 1805 | 715 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 340693.8 | 340693.8 | 170346.9 | 681387.6 | Not At-Risk | DAC
CA4200531 | RANCHO MARCELINO WATER | 240 | 87 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 171770.82 | 171770.82 | 85885.41 | 343541.64 | Not At-Risk | Missing
CA1500494 | WILSON ROAD WATER COMMUNITY | 66 | 20 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 38926.7124 | No | 2012954.5643 | 0 | Yes | 0 | 2053661.1766 | 1026830.5883 | 4107322.3533 | HR2W | SDAC
CA1500535 | MANON MANOR MUTUAL WATER COMPANY | 200 | 55 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 50700.2356 | Yes | 0 | 0 | No | 99465 | 151945.1356 | 75972.5678 | 303890.2711 | Not At-Risk | Non-DAC
CA3600089 | DESERT SPRINGS MWC | 325 | 79 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | Not At-Risk | SDAC
CA0202504 | MARKLEEVILLE WATER CO. | 25 | 167 | LPA32 - ALPINE COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 240181.8 | 240181.8 | 120090.9 | 480363.6 | Not At-Risk | DAC
CA3600306 | THUNDERBIRD CWD | 997 | 302 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 155219.5798 | Yes | 0 | 0 | Yes | 0 | 157533.4498 | 78766.7249 | 315066.8996 | Potentially At-Risk | Non-DAC
CA2702405 | JENSEN MHP WS | 56 | 26 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 48918.9745 | Yes | 0 | 0 | No | 81938.22 | 133171.0645 | 66585.5322 | 266342.1289 | HR2W | Non-DAC
CA4000506 | WOODLAND PARK MUTUAL WATER CO | 534 | 162 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 102916.5189 | Yes | 0 | 0 | No | 47638.5 | 152868.8889 | 76434.4445 | 305737.7779 | Potentially At-Risk | Non-DAC
CA3010082 | SERRANO WATER DISTRICT | 5895 | 2254 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 708524.9623 | Yes | 0 | 0 | Yes | 0 | 708524.9623 | 354262.4812 | 1417049.9246 | Not At-Risk | Non-DAC
CA5800828 | COUNTRYSIDE MOBILE HOME PARK | 185 | 86 | LPA88 - YUBA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2023238.597 | 0 | No | 138413.4 | 2163431.897 | 1081715.9485 | 4326863.794 | Potentially At-Risk | SDAC
CA2010011 | MADERA CO SA1-INDIAN LAKES | 1562 | 473 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 170368.4338 | Yes | 0 | 0 | Yes | 0 | 170368.4338 | 85184.2169 | 340736.8677 | Not At-Risk | Non-DAC
CA1010023 | CITY OF ORANGE COVE | 9780 | 1705 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | SDAC
CA2702299 | POST RANCH INN WS | 286 | 58 | LPA57 - MONTEREY COUNTY | C | T - HOTEL/MOTEL | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 134204.46 | 136518.33 | 68259.165 | 273036.66 | Not At-Risk | DAC
CA3600260 | SMILEY PARK COUNTRY CLUB | 530 | 102 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 102464.6566 | Yes | 0 | 0 | Yes | 0 | 102464.6566 | 51232.3283 | 204929.3133 | Not At-Risk | Missing
CA4010010 | SAN MIGUEL COMMUNITY SERVICES DISTRICT | 2600 | 923 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 336303.3953 | Yes | 0 | 0 | Yes | 0 | 336303.3953 | 168151.6976 | 672606.7905 | Potentially At-Risk | Non-DAC
CA1210011 | REDWAY C.S.D. | 1500 | 584 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA4500022 | DEL ORO WATER CO. - HAT CREEK DISTRICT | 205 | 62 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 51139.5461 | N/A | 0 | 0 | Yes | 0 | 51139.5461 | 25569.7731 | 102279.0922 | Not At-Risk | DAC
CA5601106 | FILLMORE WEST MOBILE HOME PARK | 99 | 33 | DISTRICT 06 - SANTA BARBARA | C | R - MOBILE HOME PARK | No | 2349.468 | Yes | 0 | No | 2531852.8872 | 0 | No | 94807.944 | 2629010.2992 | 1314505.1496 | 5258020.5985 | Potentially At-Risk | Non-DAC
CA3600785 | LAKE JODIE WATER SYSTEM | 250 | 50 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 70834.2959 | Yes | 0 | 0 | Yes | 0 | 73148.1659 | 36574.0829 | 146296.3317 | Not At-Risk | SDAC
CA2100565 | GREEN GULCH FARM | 75 | 17 | DISTRICT 25 - MARIN | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 51065.3204 | Yes | 0 | 0 | No | 67238.34 | 118303.6604 | 59151.8302 | 236607.3207 | Not At-Risk | Missing
CA5610700 | NAVAL BASE VENTURA COUNTY, POINT MUGU | 1700 | 928 | DISTRICT 06 - SANTA BARBARA | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | No | 238110.4433 | Yes | 0 | 0 | No | 1579118.904 | 1817229.3473 | 908614.6737 | 3634458.6947 | Not At-Risk | SDAC
CA1610009 | KETTLEMAN CITY CSD | 1450 | 354 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 160527.8772 | Yes | 0 | 0 | Yes | 0 | 160527.8772 | 80263.9386 | 321055.7543 | At-Risk | DAC
CA1900062 | LOS ANGELES RESIDENTIAL COMMUNITY FOUNDA | 184 | 22 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 76565.016 | 76565.016 | 38282.508 | 153130.032 | At-Risk | Non-DAC
CA1900942 | ALPINE SPRINGS MOBILE HOME PARK | 175 | 53 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 63285.7575 | No | 0 | 1472915.412 | Yes | 0 | 1536201.1695 | 768100.5847 | 3072402.3389 | At-Risk | DAC
CA1910085 | MAYWOOD MUTUAL WATER CO. #2 | 7118 | 1924 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | Yes | 0 | No | 859225.2945 | Yes | 0 | 0 | Yes | 0 | 859225.2945 | 429612.6473 | 1718450.5891 | Not At-Risk | SDAC
CA3400106 | EAST WALNUT GROVE [SWS] | 300 | 166 | LPA64 - SACRAMENTO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 45054.504 | 45054.504 | 22527.252 | 90109.008 | Not At-Risk | SDAC
CA3410033 | FLORIN COUNTY WATER DISTRICT | 7831 | 2323 | DISTRICT 09 - SACRAMENTO | C | RESIDENTIAL AREA | No | 2349.468 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 2349.468 | 1174.734 | 4698.936 | Potentially At-Risk | SDAC
CA1510011 | BUTTONWILLOW CWD | 1508 | 411 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA5410513 | NPS-ASH MOUNTAIN | 2930 | 45 | DISTRICT 12 - VISALIA | C | T - RECREATION AREA | No | 1779.9 | No | 290563.8048 | Yes | 0 | 0 | Yes | 0 | 292343.7048 | 146171.8524 | 584687.4096 | Not At-Risk | Non-DAC
CA1907014 | NORTH TRAILS MUTUAL WATER COMPANY | 100 | 49 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 54687.8221 | Yes | 0 | 0 | Yes | 0 | 54687.8221 | 27343.911 | 109375.6442 | HR2W | Non-DAC
CA3910014 | SAN JOAQUIN COUNTY-RAYMUS VILLAGE | 1082 | 329 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | No | 128194.6195 | Yes | 0 | 0 | No | 442462.2 | 570656.8195 | 285328.4097 | 1141313.6389 | HR2W | Non-DAC
CA3900927 | SPRING CREEK ESTATES PWS | 90 | 36 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 41035.4031 | No | 0 | 1036289.19 | No | 75593.4 | 1152917.9931 | 576458.9965 | 2305835.9862 | Potentially At-Risk | Non-DAC
CA3900714 | SUNNYSIDE ESTATES WATER SYSTEM | 76 | 21 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 56747.4 | 56747.4 | 28373.7 | 113494.8 | At-Risk | Non-DAC
CA2702140 | WOODSIDE WA | 73 | 26 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 50839.3892 | Yes | 0 | 0 | Yes | 0 | 53153.2592 | 26576.6296 | 106306.5184 | Not At-Risk | Non-DAC
CA5000066 | MODESTO MOBILE HOME PARK | 300 | 150 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 59486.4469 | No | 0 | 2178545.25 | No | 218823 | 2456854.6969 | 1228427.3484 | 4913709.3938 | Not At-Risk | DAC
CA3900606 | A1 WINSTONS MOBILE HOME PARK | 75 | 30 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | N/A | 0 | No | 2013732.3483 | 0 | No | 68055 | 2081787.3483 | 1040893.6741 | 4163574.6965 | Not At-Risk | Missing
CA1500478 | VALLEY ESTATES POA, INC. | 386 | 117 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 67042.5886 | Yes | 0 | 0 | Yes | 0 | 67042.5886 | 33521.2943 | 134085.1773 | Not At-Risk | Missing
CA4400559 | SUMMIT MUTUAL WATER COMPANY | 152 | 54 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 59763.6696 | N/A | 0 | 0 | Yes | 0 | 59763.6696 | 29881.8348 | 119527.3392 | HR2W | Non-DAC
CA5510016 | SIERRA PARK WATER COMPANY, INC. | 300 | 347 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 59486.4469 | Yes | 0 | 0 | No | 466333.8 | 525820.2469 | 262910.1234 | 1051640.4938 | HR2W | SDAC
CA2702073 | SAN MIGUEL WS #22 | 93 | 31 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 53098.7007 | Yes | 0 | 0 | No | 90104.82 | 145517.3907 | 72758.6954 | 291034.7814 | Not At-Risk | Non-DAC
CA1000257 | MT ARARAT MOBILE HOME PARK | 43 | 36 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK | Yes | 0 | No | 36905.8838 | Yes | 0 | 0 | No | 75593.4 | 112499.2838 | 56249.6419 | 224998.5675 | Not At-Risk | SDAC
CA4901221 | GRATON MUTUAL (GREEN VALLEY HOA) | 50 | 16 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48241.181 | No | 2494349.0781 | 0 | No | 65605.02 | 2610509.1491 | 1305254.5745 | 5221018.2982 | At-Risk | Non-DAC
CA4400572 | FERN GROVE WATER CLUB | 182 | 67 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 63152.6368 | Yes | 0 | 0 | Yes | 0 | 65466.5068 | 32733.2534 | 130933.0136 | Not At-Risk | Non-DAC
CA3301283 | GLEN EDEN SUN CLUB | 495 | 407 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 99970.2817 | Yes | 0 | 0 | No | 258994.296 | 358964.5777 | 179482.2889 | 717929.1554 | At-Risk | Non-DAC
CA1210012 | RIO DELL, CITY OF | 3300 | 1290 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 1565683.8 | 1567463.7 | 783731.85 | 3134927.4 | Not At-Risk | SDAC
CA3910800 | DEUEL VOCATIONAL INSTITUTION | 3271 | 1688 | DISTRICT 10 - STOCKTON | C | NT - INSTITUTION | Yes | 0 | No | 320524.7854 | Yes | 0 | 0 | No | 2149909.8 | 2470434.5854 | 1235217.2927 | 4940869.1709 | Not At-Risk | SDAC
CA0103040 | NORRIS CANYON PROPERTY OWNERS ASSN | 50 | 19 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1200671 | BENBOW-DEL ORO W.C. | 150 | 122 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA4210022 | GOLDEN STATE WATER COMPANY - LAKE MARIE | 527 | 206 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 102125.7599 | Yes | 0 | 0 | Yes | 0 | 102125.7599 | 51062.88 | 204251.5198 | Not At-Risk | Non-DAC
CA2300606 | LAKE VIEW MUTUAL WATER CO. | 90 | 29 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 41035.4031 | Yes | 0 | 0 | Yes | 0 | 42815.3031 | 21407.6515 | 85630.6062 | Potentially At-Risk | Non-DAC
CA0800552 | NORTHCREST TRAILER CITY | 250 | 89 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK | No | 1779.9 | No | 55093.3412 | Yes | 0 | 0 | No | 142182.6 | 199055.8412 | 99527.9206 | 398111.6824 | Potentially At-Risk | DAC
CA2700534 | COLONIAL OAK WC INC | 198 | 66 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 64960.086 | Yes | 0 | 0 | No | 147271.02 | 214544.976 | 107272.488 | 429089.952 | Potentially At-Risk | Non-DAC
CA1710022 | LAKE COUNTY CSA 20 - SODA BAY | 2129 | 645 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | Non-DAC
CA3400397 | LAGUNA VILLAGE RV PARK | 32 | 28 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 46892.3607 | No | 2524580.4341 | 0 | No | 86515.704 | 2660337.9668 | 1330168.9834 | 5320675.9336 | Potentially At-Risk | DAC
CA4510013 | SHASTA C.S.D. | 1584 | 480 | DISTRICT 02 - LASSEN | C | T - RECREATION AREA | N/A | 0 | No | 172301.4003 | No | 0 | 5485075.95 | Yes | 0 | 5657377.3503 | 2828688.6752 | 11314754.7007 | Potentially At-Risk | DAC
CA4900634 | HUCKLEBERRY MUTUAL WATER COMPANY | 45 | 29 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 47676.3531 | No | 2493813.2713 | 0 | No | 86838.18 | 2628327.8045 | 1314163.9022 | 5256655.609 | At-Risk | DAC
CA2900523 | WASHINGTON WATER DISTRICT | 330 | 115 | LPA59 - NEVADA COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 34132.2 | 34132.2 | 17066.1 | 68264.4 | At-Risk | Non-DAC
CA5400523 | EL MONTE VILLAGE MHP | 100 | 47 | DISTRICT 24 - TULARE | C | R - MOBILE HOME PARK | Yes | 0 | No | 41914.0242 | No | 2015892.8593 | 0 | No | 32875.8 | 2090682.6836 | 1045341.3418 | 4181365.3671 | HR2W | SDAC
CA0707556 | SANDMOUND MUTUAL | 160 | 103 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 60667.3942 | Yes | 0 | 0 | No | 207703.86 | 268371.2542 | 134185.6271 | 536742.5084 | Not At-Risk | SDAC
CA2701898 | CLEAR RIDGE WA | 123 | 41 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 56487.6679 | No | 2502171.8566 | 0 | Yes | 0 | 2560973.3946 | 1280486.6973 | 5121946.7891 | Not At-Risk | DAC
CA2610002 | JUNE LAKE PUD VILLAGE | 2740 | 293 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 273870.0033 | Yes | 0 | 0 | No | 31619.4 | 305489.4033 | 152744.7016 | 610978.8066 | Potentially At-Risk | Missing
CA3701341 | QUIET OAKS MOBILE HOME PARK | 120 | 45 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 56980.6049 | No | 2534132.3129 | 0 | Yes | 0 | 2593462.3857 | 1296731.1929 | 5186924.7714 | HR2W | Non-DAC
CA3700918 | RANCHO SANTA TERESA MW CO. | 95 | 37 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 54114.6264 | Yes | 0 | 0 | Yes | 0 | 56464.0944 | 28232.0472 | 112928.1888 | Potentially At-Risk | Non-DAC
CA3600258 | SKY FOREST MWC | 605 | 159 | LPA66 - SAN BERNARDINO COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 2313.87 | No | 110937.0747 | Yes | 0 | 0 | Yes | 0 | 113250.9447 | 56625.4724 | 226501.8894 | Not At-Risk | DAC
CA4300573 | GREEN ACRES MUTUAL WATER | 53 | 19 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 49299.7826 | Yes | 0 | 0 | No | 71589.672 | 123238.9226 | 61619.4613 | 246477.8452 | At-Risk | Non-DAC
CA2701888 | CACHAGUA MUTUAL WS (#4) | 55 | 24 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48806.0089 | Yes | 0 | 0 | Yes | 0 | 51119.8789 | 25559.9394 | 102239.7578 | Not At-Risk | Non-DAC
CA5200555 | RIO RANCH COMMUNITY SVCS DIST | 44 | 30 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36993.7459 | No | 2011053.3145 | 0 | No | 68055 | 2117881.9604 | 1058940.9802 | 4235763.9208 | Not At-Risk | SDAC
CA2500911 | I'SOT WELL #3 & #15 | 215 | 53 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | No | 52018.1673 | Yes | 0 | 0 | No | 96952.2 | 148970.3673 | 74485.1836 | 297940.7345 | Not At-Risk | Missing
CA4500012 | CASCADE RACQUET CLUB MUTUAL WATER | 89 | 27 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 40947.541 | No | 0 | 946111.08 | No | 64285.8 | 1053124.321 | 526562.1605 | 2106248.642 | Not At-Risk | Non-DAC
CA0810003 | BERTSCH OCEAN VIEW CSD | 1600 | 696 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA5500019 | JENNESS PARK CHRISTIAN CAMP | 505 | 43 | DISTRICT 11 - MERCED | C | T - OTHER TRANSIENT AREA | Yes | 0 | No | 77498.1801 | Yes | 0 | 0 | No | 84388.2 | 161886.3801 | 80943.1901 | 323772.7602 | Not At-Risk | SDAC
CA2700773 | SUNNY MESA WATER SYSTEM | 880 | 267 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 142002.6076 | Yes | 0 | 0 | Yes | 0 | 142002.6076 | 71001.3038 | 284005.2152 | Potentially At-Risk | Non-DAC
CA4010027 | NACIMIENTO WATER COMPANY | 1836 | 653 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | Non-DAC
CA4700542 | ABRAMS LAKE MOBILE ESTATES | 135 | 2 | DISTRICT 01 - KLAMATH | C | MOBILE HOME PARK | No | 1779.9 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | SDAC
CA5200527 | HUNTER'S FISHING RESORT | 50 | 47 | LPA82 - TEHAMA COUNTY | C | T - RECREATION AREA | No | 1779.9 | No | 37520.9186 | Yes | 0 | 0 | No | 89413.8 | 128714.6186 | 64357.3093 | 257429.2371 | Not At-Risk | SDAC
CA3301502 | PARADISE VALLEY MWC | 30 | 19 | LPA63 - RIVERSIDE COUNTY | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Missing
CA4300637 | LOS RANCHOS DE UVAS WATER COMPANY | 58 | 21 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 49872.9783 | Yes | 0 | 0 | Yes | 0 | 52222.4463 | 26111.2231 | 104444.8926 | Not At-Risk | Non-DAC
CA1000069 | SHAVER LAKE HEIGHTS PROP ASSN | 345 | 201 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 282899.4 | 282899.4 | 141449.7 | 565798.8 | Not At-Risk | Non-DAC
CA3901276 | HANOT FOUNDATION INC | 38 | 15 | LPA69 - SAN JOAQUIN COUNTY | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 36466.5732 | No | 2010534.7918 | 0 | No | 49209 | 2096210.3651 | 1048105.1825 | 4192420.7301 | Not At-Risk | Non-DAC
CA2710012 | CWSC SALINAS HILLS | 8213 | 1632 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 970379.1634 | Yes | 0 | 0 | Yes | 0 | 970379.1634 | 485189.5817 | 1940758.3267 | Not At-Risk | Non-DAC
CA1900523 | WHITE FENCE FARMS MWC NO.3 | 749 | 253 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA | Yes | 0 | No | 129088.6228 | Yes | 0 | 0 | Yes | 0 | 129088.6228 | 64544.3114 | 258177.2457 | Not At-Risk | Non-DAC
CA1500493 | EL ADOBE POA, INC. | 200 | 80 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | N/A | 0 | Yes | 0 | 0 | No | 130875 | 132654.9 | 66327.45 | 265309.8 | HR2W | SDAC
CA5101009 | WILDWOOD EAST MUTUAL | 350 | 48 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 63879.5525 | Yes | 0 | 0 | No | 90670.2 | 156329.6525 | 78164.8263 | 312659.3051 | At-Risk | DAC
CA4410016 | FOREST LAKES MWC | 1067 | 326 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 163127.17 | Yes | 0 | 0 | Yes | 0 | 163127.17 | 81563.585 | 326254.34 | Not At-Risk | Non-DAC
CA0910003 | PLACERVILLE, CITY OF - MAIN | 10762 | 2795 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA5400880 | THE LAKES ASSOCIATION | 495 | 161 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 76619.559 | Yes | 0 | 0 | No | 232643.4 | 311042.859 | 155521.4295 | 622085.7179 | Potentially At-Risk | Non-DAC
CA2700634 | CHETMOORE ACRES WA | 70 | 25 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 50500.4925 | No | 2496492.3051 | 0 | No | 80304.9 | 2629611.5676 | 1314805.7838 | 5259223.1352 | Potentially At-Risk | Non-DAC
CA5400506 | NORTH KAWEAH MWC | 560 | 71 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 82330.5963 | Yes | 0 | 0 | Yes | 0 | 84110.4963 | 42055.2482 | 168220.9927 | Not At-Risk | DAC
CA3500556 | MISSION FARM R.V. PARK | 110 | 173 | DISTRICT 05 - MONTEREY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 55019.1155 | Yes | 0 | 0 | No | 322036.26 | 379369.2455 | 189684.6227 | 758738.4909 | Not At-Risk | Non-DAC
CA4400645 | HIDDEN MEADOW MUTUAL WATER CO | 45 | 18 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 47676.3531 | Yes | 0 | 0 | Yes | 0 | 49990.2231 | 24995.1116 | 99980.4463 | Not At-Risk | Non-DAC
CA3900835 | WAYSIDE MOTEL APARTMENTS WTR SYS | 70 | 25 | LPA69 - SAN JOAQUIN COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | No | 39278.1608 | No | 2013300.246 | 0 | No | 61773 | 2116131.3069 | 1058065.6534 | 4232262.6137 | Potentially At-Risk | DAC
CA2910010 | TRUCKEE-DONNER PUD - HIRSCHDALE | 85 | 26 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 40596.0925 | No | 0 | 936091.29 | Yes | 0 | 976687.3825 | 488343.6913 | 1953374.7651 | At-Risk | Non-DAC
CA5000317 | OID #51 - SUNSET OAKS #10 | 287 | 82 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 58344.2394 | Yes | 0 | 0 | No | 133387.8 | 193511.9394 | 96755.9697 | 387023.8788 | Not At-Risk | Non-DAC
CA1503226 | QVWD-WEST & EAST COMBINED WATER SYSTEM | 207 | 75 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2025139.8468 | 0 | Yes | 0 | 2025139.8468 | 1012569.9234 | 4050279.6936 | At-Risk | SDAC
CA3600012 | APPLE VALLEY VIEW MWC | 275 | 81 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 73658.4352 | Yes | 0 | 0 | Yes | 0 | 73658.4352 | 36829.2176 | 147316.8704 | HR2W | Non-DAC
CA1400045 | PRIMROSE LANE APARTMENTS | 73 | 26 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39541.7472 | Yes | 0 | 0 | No | 63029.4 | 104351.0472 | 52175.5236 | 208702.0943 | Not At-Risk | Non-DAC
CA1500560 | KRANENBURG WATER SYSTEM | 42 | 15 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36818.0217 | N/A | 0 | 0 | No | 49209 | 87806.9217 | 43903.4608 | 175613.8433 | At-Risk | Non-DAC
CA5510025 | TUD - PHOENIX LAKE PARK | 119 | 57 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 43583.4044 | No | 2017534.8478 | 0 | Yes | 0 | 2061118.2521 | 1030559.1261 | 4122236.5043 | Potentially At-Risk | Non-DAC
CA4110002 | CITY OF BRISBANE | 3197 | 1280 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1000021 | FCSA #05/WILDWOOD ISLAND | 417 | 149 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 69766.3141 | Yes | 0 | 0 | No | 217566.6 | 287332.9141 | 143666.4571 | 574665.8283 | Potentially At-Risk | DAC
CA1400007 | SIERRA HIGHLAND CSD | 600 | 215 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 85845.0809 | Yes | 0 | 0 | No | 300489 | 386334.0809 | 193167.0404 | 772668.1617 | Not At-Risk | Non-DAC
CA3901304 | ENCLAVE AT THE DELTA | 39 | 15 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 36554.4353 | No | 2010621.2123 | 0 | No | 49209 | 2096384.6476 | 1048192.3238 | 4192769.2952 | Not At-Risk | DAC
CA3310047 | CABAZON WATER DISTRICT | 2588 | 969 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 339909.9981 | Yes | 0 | 0 | Yes | 0 | 339909.9981 | 169954.9991 | 679819.9963 | Not At-Risk | DAC
CA1510013 | MCFARLAND, CITY OF | 15506 | 2849 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1395517.7414 | Yes | 0 | 0 | Yes | 0 | 1395517.7414 | 697758.8707 | 2791035.4829 | HR2W | SDAC
CA1000471 | FCSA #39 A&B | 395 | 141 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | SDAC
CA1010030 | TRANQUILLITY IRRIGATION DISTRICT | 897 | 340 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 457539 | 457539 | 228769.5 | 915078 | Potentially At-Risk | Non-DAC
CA2000608 | WILDWOOD MOBILE HOME PK INC | 100 | 68 | LPA50 - MADERA COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 41914.0242 | No | 2015892.8593 | 0 | Yes | 0 | 2057806.8836 | 1028903.4418 | 4115613.7671 | At-Risk | Non-DAC
CA1210021 | JACOBY CREEK CSD | 904 | 330 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1210015 | WILLOW CREEK C.S.D. | 1710 | 931 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | Non-DAC
CA1000265 | MARY LOU MOBILE HOME PARK | 60 | 34 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 73080.6 | 74860.5 | 37430.25 | 149721 | Not At-Risk | SDAC
CA0300053 | RANCHO DEL ORO | 44 | 24 | DISTRICT 10 - STOCKTON | C | R - MOBILE HOME PARK | No | 1779.9 | No | 36993.7459 | No | 2011053.3145 | 0 | No | 60516.6 | 2110343.5604 | 1055171.7802 | 4220687.1208 | At-Risk | DAC
CA4500314 | SHASTA CO CSA # 13 ALPINE MEADOWS | 31 | 31 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 35851.5384 | No | 2009929.8487 | 0 | Yes | 0 | 2045781.3872 | 1022890.6936 | 4091562.7743 | At-Risk | SDAC
CA3600446 | UPPER LITTLE BEAR MOUNTAIN CLUB | 25 | 36 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | Yes | 0 | 0 | No | 98271.42 | 98271.42 | 49135.71 | 196542.84 | Not At-Risk | Missing
CA2000538 | CEDAR VALLEY MUTUAL WATER CO | 137 | 67 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 114541.8 | 114541.8 | 57270.9 | 229083.6 | HR2W | SDAC
CA3205003 | GOLD MOUNTAIN CSD | 100 | 100 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 41914.0242 | Yes | 0 | 0 | Yes | 0 | 43693.9242 | 21846.9621 | 87387.8485 | Not At-Risk | DAC
CA1900913 | LILY OF THE VALLEY MOBILE VILLAGE | 495 | 182 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 99970.2817 | No | 2574836.3417 | 0 | Yes | 0 | 2674806.6234 | 1337403.3117 | 5349613.2468 | Not At-Risk | Non-DAC
CA1900055 | BLUE SKIES TRAILOR PARK | 40 | 20 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | Yes | 0 | No | 0 | 1069290.63 | Yes | 0 | 1069290.63 | 534645.315 | 2138581.26 | Potentially At-Risk | DAC
CA2410018 | SANTA NELLA COUNTY WATER DISTRICT | 1308 | 667 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 148051.4571 | Yes | 0 | 0 | Yes | 0 | 148051.4571 | 74025.7285 | 296102.9141 | Potentially At-Risk | DAC
CA4900669 | WENDELL LANE MUTUAL WATER COMPANY | 82 | 25 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 51856.0794 | No | 2497778.2413 | 0 | Yes | 0 | 2551948.1907 | 1275974.0953 | 5103896.3813 | Not At-Risk | Non-DAC
CA5602115 | SAVIERS ROAD MUTUAL WATER CO | 368 | 92 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | DAC
CA4901062 | KINNYBROOK MUTUAL WATER COMPANY | 48 | 23 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA0400123 | HUMBOLDT HIGHLANDS MUTUAL | 50 | 28 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 37520.9186 | No | 2011571.8372 | 0 | Yes | 0 | 2049092.7557 | 1024546.3779 | 4098185.5115 | Not At-Risk | Missing
CA0707577 | RIVERVIEW WATER ASSOCIATION | 230 | 89 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 68574.9844 | Yes | 0 | 0 | No | 184837.38 | 253412.3644 | 126706.1822 | 506824.7287 | Not At-Risk | SDAC
CA2710018 | SEASIDE MUNICIPAL WATER SYSTEM | 2800 | 786 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA0707588 | BIG OAK MOBILE HOME PARK WATER | 156 | 66 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 147271.02 | 147271.02 | 73635.51 | 294542.04 | Not At-Risk | SDAC
CA3301877 | BLOCK 77 WATER COMPANY | 50 | 18 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 48955.8652 | No | 0 | 1044828.522 | No | 69931.224 | 1166065.0792 | 583032.5396 | 2332130.1583 | At-Risk | Non-DAC
CA1009027 | HARRIS FARMS HEADQUARTERS | 300 | 69 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | No | 59486.4469 | N/A | 0 | 0 | No | 117054.6 | 176541.0469 | 88270.5234 | 353082.0938 | Not At-Risk | SDAC
CA1710012 | COBB AREA COUNTY WATER DISTRICT | 3308 | 1004 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 63029.4 | 63029.4 | 31514.7 | 126058.8 | Not At-Risk | Missing
CA2000526 | PIKE RANCH MUTUAL WATER CO | 74 | 20 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39629.6093 | No | 2013645.9278 | 0 | Yes | 0 | 2055055.4371 | 1027527.7185 | 4110110.8742 | HR2W | SDAC
CA2410002 | CITY OF DOS PALOS | 7452 | 2521 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | N/A | 0 | No | 687876.2811 | N/A | 0 | 0 | No | 35388.6 | 723264.8811 | 361632.4405 | 1446529.7621 | HR2W | SDAC
CA4900577 | RIO LINDO ADVENTIST ACADEMY | 358 | 54 | DISTRICT 18 - SONOMA | C | NT - SCHOOL | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 127671.18 | 129985.05 | 64992.525 | 259970.1 | Not At-Risk | Missing
CA4710012 | HAPPY CAMP C.S.D. | 1100 | 453 | DISTRICT 01 - KLAMATH | C | T - RECREATION AREA | N/A | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA1010044 | HURON, CITY OF | 9306 | 871 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 850772.6391 | N/A | 0 | 0 | Yes | 0 | 850772.6391 | 425386.3195 | 1701545.2782 | HR2W | SDAC
CA2300604 | POINT OF VIEW MUTUAL WATER CO | 56 | 30 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 38048.0912 | Yes | 0 | 0 | Yes | 0 | 39827.9912 | 19913.9956 | 79655.9825 | Not At-Risk | SDAC
CA5510024 | SONORA WATER COMPANY INC | 1055 | 110 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | DAC
CA2000775 | OAK CREEK MOBILE HOME PARK | 370 | 198 | LPA50 - MADERA COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 65636.7948 | Yes | 0 | 0 | No | 279130.2 | 344766.9948 | 172383.4974 | 689533.9896 | Not At-Risk | SDAC
CA4200731 | ALEGRIA DOMESTIC MUTUAL WATER COMPANY | 54 | 17 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 48693.0433 | Yes | 0 | 0 | Yes | 0 | 48693.0433 | 24346.5217 | 97386.0866 | Not At-Risk | Non-DAC
CA1500290 | NORTH MUROC MUTUAL WATER COMPANY | 270 | 198 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 56850.5835 | Yes | 0 | 0 | No | 279130.2 | 337760.6835 | 168880.3417 | 675521.367 | Not At-Risk | SDAC
CA2310008 | REDWOOD VALLEY COUNTY WATER DISTRICT | 5200 | 1317 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 490010.802 | N/A | 0 | 0 | Yes | 0 | 490010.802 | 245005.401 | 980021.6039 | At-Risk | DAC
CA5602108 | GARDEN ACRES MUTUAL WATER CO | 840 | 140 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2612284.0482 | 0 | Yes | 0 | 2612284.0482 | 1306142.0241 | 5224568.0964 | Not At-Risk | SDAC
CA5800821 | HERITAGE PARK | 26 | 20 | LPA88 - YUBA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 35412.2278 | No | 2009497.7465 | 0 | No | 55491 | 2102180.8744 | 1051090.4372 | 4204361.7487 | Potentially At-Risk | DAC
CA1400098 | DARWIN COMMUNITY SERVICE DISTRICT | 40 | 63 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | SDAC
CA2000530 | CRASS MUTUAL WATER COMPANY | 80 | 26 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 40156.782 | No | 2014164.4505 | 0 | Yes | 0 | 2054321.2324 | 1027160.6162 | 4108642.4649 | Potentially At-Risk | SDAC
CA3400191 | ELEVEN OAKS MOBILE HOME COMMUNITY | 262 | 136 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 73259.3625 | Yes | 0 | 0 | No | 265628.088 | 341236.9185 | 170618.4592 | 682473.837 | Not At-Risk | SDAC
CA4200891 | BOBCAT SPRINGS MUTUAL WATER COMPANY | 120 | 47 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 56148.7712 | Yes | 0 | 0 | No | 46005.18 | 102153.9512 | 51076.9756 | 204307.9024 | Potentially At-Risk | Non-DAC
CA2600547 | CROWLEY LAKE TRAILER PARK | 230 | 108 | LPA56 - MONO COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 53336.099 | Yes | 0 | 0 | No | 166054.2 | 219390.299 | 109695.1495 | 438780.5979 | Not At-Risk | Non-DAC
CA1400027 | CARTAGO MUTUAL WATER COMPANY | 132 | 40 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 44725.6119 | Yes | 0 | 0 | No | 80619 | 125344.6119 | 62672.3059 | 250689.2237 | Potentially At-Risk | SDAC
CA4300562 | ROSEVIEW HEIGHTS MUTUAL WATER COMPANY | 143 | 51 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 59617.305 | N/A | 0 | 0 | Yes | 0 | 59617.305 | 29808.6525 | 119234.6101 | Not At-Risk | Non-DAC
CA2010003 | BASS LAKE WATER COMPANY | 4527 | 1013 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 1247814.6 | 1247814.6 | 623907.3 | 2495629.2 | At-Risk | Non-DAC
CA2702521 | SANTA LUCIA PRESERVE WS | 554 | 171 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA5400816 | BEDEL MUTUAL WATER CO | 155 | 66 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 46746.4405 | Yes | 0 | 0 | No | 113285.4 | 161811.7405 | 80905.8702 | 323623.4809 | Not At-Risk | Non-DAC
CA1510054 | PINON PINES MWC | 642 | 275 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 245207.4 | 245207.4 | 122603.7 | 490414.8 | HR2W | SDAC
CA4500082 | MIDWAY MOBILEHOME PARK | 50 | 29 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 37520.9186 | No | 2011571.8372 | 0 | Yes | 0 | 2050872.6557 | 1025436.3279 | 4101745.3115 | Potentially At-Risk | DAC
CA5200012 | VISTA GRANDE WATER SYSTEM | 400 | 141 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 68272.6582 | Yes | 0 | 0 | No | 207515.4 | 277567.9582 | 138783.9791 | 555135.9164 | Not At-Risk | SDAC
CA4400850 | THE WILLOWS RESORT | 54 | 69 | LPA74 - SANTA CRUZ COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | Yes | 0 | No | 2494777.7235 | 0 | No | 152170.98 | 2646948.7035 | 1323474.3517 | 5293897.407 | At-Risk | Non-DAC
CA5200013 | WOMACK SUBDIVISION M.W.C. | 40 | 16 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36642.2974 | No | 2010707.6327 | 0 | Yes | 0 | 2049129.8302 | 1024564.9151 | 4098259.6603 | Not At-Risk | Non-DAC
CA3400401 | PLANTATION MOBILE HOME PARK | 44 | 44 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 48268.0303 | No | 0 | 1362835.926 | No | 113050.872 | 1526504.2963 | 763252.1482 | 3053008.5927 | Potentially At-Risk | SDAC
CA1500443 | CANYON MEADOWS MUTUAL WATER | 394 | 141 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 67745.4855 | Yes | 0 | 0 | Yes | 0 | 69525.3855 | 34762.6928 | 139050.7711 | HR2W | Missing
CA0707589 | BELLA VISTA WATER SYS | 93 | 33 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | No | 0 | 1214415.3 | No | 93371.46 | 1310100.63 | 655050.315 | 2620201.26 | HR2W | Non-DAC
CA5500041 | ALPINE ACRES MUTUAL WATER CO | 59 | 55 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 38311.6776 | Yes | 0 | 0 | Yes | 0 | 40091.5776 | 20045.7888 | 80183.1552 | Not At-Risk | Non-DAC
CA1710018 | LAKE COUNTY CSA 2 - SPRING VALLEY | 1386 | 479 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | DAC
CA3100019 | NORTH EDEN VALLEY | 52 | 21 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37696.6428 | Yes | 0 | 0 | Yes | 0 | 39476.5428 | 19738.2714 | 78953.0856 | Not At-Risk | Non-DAC
CA3901215 | SAN JUAN VISTA | 100 | 72 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 41914.0242 | No | 0 | 1397001.63 | No | 120823.8 | 1559739.4542 | 779869.7271 | 3119478.9085 | Potentially At-Risk | SDAC
CA5200547 | GATEWAY MOBILE HOME PARK | 75 | 32 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 39717.4714 | No | 0 | 996210.03 | No | 70567.8 | 1108275.2014 | 554137.6007 | 2216550.4028 | Not At-Risk | SDAC
CA3900586 | B&G MOBILE HOME PARK LLC WS | 50 | 22 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 37520.9186 | No | 2011571.8372 | 0 | No | 58003.8 | 2108876.4557 | 1054438.2279 | 4217752.9115 | At-Risk | DAC
CA3100041 | ALPINE MEADOWS PROPERTY OWNERS ASSO | 250 | 129 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 41670.6 | 41670.6 | 20835.3 | 83341.2 | Potentially At-Risk | Non-DAC
CA3110034 | CHRISTIAN VALLEY PARK CSD | 1800 | 627 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | No | 0 | 6957985.08 | Yes | 0 | 6957985.08 | 3478992.54 | 13915970.16 | At-Risk | Non-DAC
CA1210017 | MANILA COMMUNITY SERVICES DIST. | 750 | 362 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA2700766 | STRAWBERRY RD WS #06 | 78 | 27 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 51404.2171 | No | 2497349.5959 | 0 | No | 83571.54 | 2634639.223 | 1317319.6115 | 5269278.4459 | Potentially At-Risk | Non-DAC
CA3900724 | ELKHORN ESTATES WATER SYSTEM | 200 | 71 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 50700.2356 | Yes | 0 | 0 | No | 118311 | 169011.2356 | 84505.6178 | 338022.4711 | At-Risk | Non-DAC
CA2700589 | GLENN AVE WS #01 | 73 | 26 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 50839.3892 | No | 2496813.7891 | 0 | Yes | 0 | 2549967.0484 | 1274983.5242 | 5099934.0967 | Potentially At-Risk | Non-DAC
CA2900562 | ANANDA VILLAGE | 290 | 83 | LPA59 - NEVADA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 58607.8258 | Yes | 0 | 0 | Yes | 0 | 58607.8258 | 29303.9129 | 117215.6515 | Not At-Risk | SDAC
CA0707594 | CASA MEDANOS WATER SYSTEM | 45 | 16 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 47676.3531 | No | 0 | 1008836.85 | No | 65605.02 | 1124432.0931 | 562216.0466 | 2248864.1863 | Not At-Risk | SDAC
CA1502600 | WEGIS MUTUAL WATER COMPANY | 64 | 23 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 38750.9881 | N/A | 0 | 0 | No | 59260.2 | 98011.1882 | 49005.5941 | 196022.3763 | Potentially At-Risk | Non-DAC
CA3200189 | VALIVU ESTATES MHP | 54 | 19 | LPA62 - PLUMAS COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2011917.5189 | 0 | No | 54234.6 | 2067932.0189 | 1033966.0095 | 4135864.0379 | Potentially At-Risk | DAC
CA4300831 | MT. EDEN MUTUAL WATER COMPANY | 165 | 65 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 62139.3661 | N/A | 0 | 0 | Yes | 0 | 62139.3661 | 31069.683 | 124278.7322 | Not At-Risk | Non-DAC
CA1010020 | LATON COMMUNITY SERVICES DISTRICT | 1824 | 472 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 193388.3075 | Yes | 0 | 0 | Yes | 0 | 193388.3075 | 96694.1538 | 386776.6151 | Not At-Risk | SDAC
CA0300062 | HOPE FOUNDATION/MORIAH HEIGHTS | 299 | 21 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | No | 59398.5848 | No | 2033090.5276 | 0 | No | 56747.4 | 2149236.5123 | 1074618.2562 | 4298473.0247 | HR2W | Non-DAC
CA1110002 | CAL-WATER SERVICE CO.-HAMILTON CITY | 2607 | 639 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA2710013 | CWSC LAS LOMAS | 3387 | 621 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 425207.3022 | Yes | 0 | 0 | Yes | 0 | 425207.3022 | 212603.6511 | 850414.6044 | At-Risk | Non-DAC
CA4710002 | DUNSMUIR, CITY OF | 1923 | 1187 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | No | 202086.6567 | N/A | 0 | 0 | No | 42927 | 245013.6567 | 122506.8284 | 490027.3135 | Not At-Risk | SDAC
CA1910084 | MAYWOOD MUTUAL WATER CO. #1 | 5500 | 1163 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA5410034 | DEL ORO CALIFORNIA PINES DISTRICT | 930 | 284 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 114839.5783 | Yes | 0 | 0 | Yes | 0 | 114839.5783 | 57419.7891 | 229679.1565 | Potentially At-Risk | SDAC
CA4000803 | RANCHO SALINAS MBWC | 50 | 20 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48241.181 | Yes | 0 | 0 | Yes | 0 | 50555.051 | 25277.5255 | 101110.102 | Potentially At-Risk | Non-DAC
CA4500313 | SHASTA CO CSA # 8 PALO CEDRO | 261 | 79 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 56059.8245 | No | 0 | 1467140.16 | Yes | 0 | 1523199.9845 | 761599.9922 | 3046399.9689 | Not At-Risk | DAC
CA3901348 | FAIROAKS PWS #44 | 1172 | 355 | DISTRICT 10 - STOCKTON | C | O - WHOLESALER (SELLS WATER) | Yes | 0 | No | 136102.2097 | Yes | 0 | 0 | No | 172336.2 | 308438.4097 | 154219.2048 | 616876.8193 | Not At-Risk | Non-DAC
CA0500019 | MINERAL MOUNTAIN MUTUAL WATER | 125 | 38 | LPA35 - CALAVERAS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 78106.2 | 79886.1 | 39943.05 | 159772.2 | Not At-Risk | SDAC
CA0400013 | MERRY MOUNTAIN MUTUAL | 100 | 97 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 152233.8 | 154013.7 | 77006.85 | 308027.4 | Not At-Risk | SDAC
CA1000186 | HELM SCHOOL | 146 | 11 | DISTRICT 23 - FRESNO | C | NT - SCHOOL | Yes | 0 | No | 44507.2216 | No | 2019868.1997 | 0 | No | 44183.4 | 2108558.8213 | 1054279.4106 | 4217117.6426 | At-Risk | Non-DAC
CA2702148 | ASOLEADO MWC | 101 | 36 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 54002.4253 | Yes | 0 | 0 | Yes | 0 | 56316.2953 | 28158.1476 | 112632.5906 | Not At-Risk | Non-DAC
CA3600107 | FOREST PARK MWC | 415 | 93 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 89473.6156 | Yes | 0 | 0 | No | 191370.66 | 283158.1456 | 141579.0728 | 566316.2912 | Not At-Risk | DAC
CA2000529 | BONADELLE RANCHOS MUTUAL WATER | 50 | 23 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37520.9186 | No | 2011571.8372 | 0 | Yes | 0 | 2050872.6557 | 1025436.3279 | 4101745.3115 | At-Risk | Non-DAC
CA3301031 | BANNING HTS. MUTUAL WATER CO. | 552 | 178 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 106504.7126 | Yes | 0 | 0 | Yes | 0 | 106504.7126 | 53252.3563 | 213009.4252 | Not At-Risk | Non-DAC
CA5400641 | TEVISTON CSD | 343 | 140 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 63264.5178 | No | 2036893.0271 | 0 | Yes | 0 | 2100157.5448 | 1050078.7724 | 4200315.0897 | HR2W | SDAC
CA1300664 | RIVERFRONT MUTUAL WATER COMPANY | 15 | 42 | LPA43 - IMPERIAL COUNTY | C | O - OTHER AREA | Yes | 0 | No | 34445.7446 | Yes | 0 | 0 | No | 49209 | 83654.7446 | 41827.3723 | 167309.4892 | Potentially At-Risk | SDAC
CA5303002 | INDIAN CREEK TRAILER PARK | 36 | 35 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 74337 | 74337 | 37168.5 | 148674 | At-Risk | SDAC
CA4500027 | BIG SPRINGS MUTUAL WATER SYSTEM | 97 | 42 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2015633.598 | 0 | No | 83131.8 | 2098765.398 | 1049382.699 | 4197530.796 | Not At-Risk | DAC
CA1510007 | FRAZIER PARK PUD | 2691 | 1318 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 269564.7597 | Yes | 0 | 0 | Yes | 0 | 269564.7597 | 134782.3799 | 539129.5195 | HR2W | SDAC
CA2000533 | SUGAR PINE HOMEOWNERS ASSOC | 120 | 58 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 43671.2665 | Yes | 0 | 0 | No | 103234.2 | 146905.4665 | 73452.7332 | 293810.933 | Not At-Risk | SDAC
CA4200572 | LAS POSITAS MUTUAL WATER COMPANY | 200 | 62 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 65186.0171 | No | 0 | 1565107.95 | No | 140737.74 | 1771031.7071 | 885515.8536 | 3542063.4143 | Potentially At-Risk | Non-DAC
CA1600002 | SUNSET VISTA ESTATES MHP | 400 | 108 | LPA46 - KINGS COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 68272.6582 | No | 0 | 1757714.07 | Yes | 0 | 1827766.6282 | 913883.3141 | 3655533.2564 | Potentially At-Risk | SDAC
CA3301943 | PLANTATION ON THE LAKE PARK | 891 | 554 | DISTRICT 20 - RIVERSIDE | C | R - MOBILE HOME PARK | Yes | 0 | No | 145367.3805 | Yes | 0 | 0 | Yes | 0 | 145367.3805 | 72683.6902 | 290734.7609 | Potentially At-Risk | SDAC
CA2110008 | LAWSON S LANDING | 962 | 66 | DISTRICT 25 - MARIN | C | R - OTHER RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 147271.02 | 149584.89 | 74792.445 | 299169.78 | Not At-Risk | Non-DAC
CA3701988 | ALPINE OAKS ESTATES LLC | 125 | 68 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 57553.8005 | No | 0 | 1656381.222 | Yes | 0 | 1713935.0225 | 856967.5113 | 3427870.0451 | Potentially At-Risk | Non-DAC
CA5800805 | LAKE FRANCIS MUTUAL WATER COMPANY | 60 | 19 | LPA88 - YUBA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 38399.5397 | Yes | 0 | 0 | No | 54234.6 | 94414.0397 | 47207.0198 | 188828.0794 | At-Risk | SDAC
CA3700958 | LOS TULES MUTUAL WATER COMPANY | 140 | 100 | LPA67 - SAN DIEGO COUNTY | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 59273.3876 | Yes | 0 | 0 | Yes | 0 | 59273.3876 | 29636.6938 | 118546.7752 | Not At-Risk | SDAC
CA4400605 | CRESTWOOD HEIGHTS WATER ASSN | 126 | 45 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 56826.5647 | Yes | 0 | 0 | No | 112971.3 | 172111.7347 | 86055.8673 | 344223.4693 | Not At-Risk | Non-DAC
CA2000573 | THE VILLAGE | 40 | 21 | LPA50 - MADERA COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | No | 36642.2974 | Yes | 0 | 0 | Yes | 0 | 38422.1974 | 19211.0987 | 76844.3949 | HR2W | DAC
CA0300024 | TABEAU MOBILE HOME PARK | 25 | 22 | DISTRICT 10 - STOCKTON | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2009411.3261 | 0 | No | 58003.8 | 2069195.0261 | 1034597.513 | 4138390.0522 | Not At-Risk | Non-DAC
CA1010005 | FIREBAUGH CITY | 7619 | 1642 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 230130.6 | 230130.6 | 115065.3 | 460261.2 | At-Risk | SDAC
CA4010006 | CAYUCOS BEACH MUTUAL WATER COMPANY | 2373 | 783 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 310660.2099 | Yes | 0 | 0 | Yes | 0 | 310660.2099 | 155330.105 | 621320.4198 | Not At-Risk | DAC
CA3901081 | MOBILE VILLAS TRAILER PARK | 130 | 36 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 44549.8876 | Yes | 0 | 0 | No | 74337 | 120666.7876 | 60333.3938 | 241333.5753 | Potentially At-Risk | Non-DAC
CA3400101 | HOOD WATER MAINTENCE DIST [SWS] | 100 | 82 | LPA64 - SACRAMENTO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 53346.744 | 53346.744 | 26673.372 | 106693.488 | Not At-Risk | DAC
CA1210008 | GARBERVILLE SANITARY DISTRICT | 1500 | 442 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | SDAC
CA0300010 | DRYTOWN COUNTY WATER DISTRICT | 214 | 66 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA1100711 | BUTTE CITY COMMUNITY S.D. | 75 | 48 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39717.4714 | No | 2013732.3483 | 0 | No | 90670.2 | 2145899.9196 | 1072949.9598 | 4291799.8393 | At-Risk | DAC
CA4000771 | RANCHO NIPOMO WATER COMPANY | 65 | 44 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 49935.6646 | Yes | 0 | 0 | No | 57438.42 | 107374.0846 | 53687.0423 | 214748.1692 | Not At-Risk | Non-DAC
CA3700922 | LIVE OAK SPRINGS WATER SYSTEM | 300 | 94 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | Yes | 0 | No | 2553670.2467 | 0 | Yes | 0 | 2556019.7147 | 1278009.8573 | 5112039.4294 | At-Risk | SDAC
CA5610001 | DEMPSEY ROAD MUTUAL WATER CO | 990 | 301 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 156716.6552 | Yes | 0 | 0 | No | 539272.008 | 698338.1312 | 349169.0656 | 1396676.2623 | Not At-Risk | Non-DAC
CA3301428 | BLYTHE - MESA RANCH | 561 | 189 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 107536.4648 | Yes | 0 | 0 | Yes | 0 | 109885.9328 | 54942.9664 | 219771.8657 | Not At-Risk | SDAC
CA3810700 | PRESIDIO OF SAN FRANCISCO | 3500 | 1219 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 444460.8922 | Yes | 0 | 0 | No | 61638.984 | 506099.8762 | 253049.9381 | 1012199.7525 | Not At-Risk | Non-DAC
CA4900547 | END-O-VALLEY MUTUAL WATER COMPANY | 129 | 39 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 0 | 1286972.4 | No | 103171.38 | 1390143.78 | 695071.89 | 2780287.56 | Not At-Risk | Non-DAC
CA3910023 | OAKWOOD LAKE WATER DISTRICT-SUBDIVISION | 1304 | 391 | DISTRICT 10 - STOCKTON | C | O - WHOLESALER (SELLS WATER) | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1910046 | SUBURBAN WATER SYSTEMS-GLENDORA | 6543 | 1546 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1900301 | SHADOW ACRES MUTUAL WATER COMPANY | 431 | 162 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 92633.3769 | Yes | 0 | 0 | Yes | 0 | 94982.8449 | 47491.4224 | 189965.6897 | Not At-Risk | Non-DAC
CA2110001 | INVERNESS PUBLIC UTILITY DIST | 1445 | 516 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1300629 | JACKSON HIDE-A-WAY | 29 | 26 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Missing
CA3301171 | BRADFORD RUN RV | 100 | 59 | LPA63 - RIVERSIDE COUNTY | C | T - OTHER TRANSIENT AREA | Yes | 0 | No | 54687.8221 | No | 2531961.4313 | 0 | No | 137927.592 | 2724576.8454 | 1362288.4227 | 5449153.6908 | At-Risk | Missing
CA3301381 | CSA 51 | 350 | 77 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 83347.6067 | Yes | 0 | 0 | Yes | 0 | 83347.6067 | 41673.8033 | 166695.2133 | At-Risk | SDAC
CA2701959 | TIERRA VISTA MWC | 54 | 18 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48693.0433 | No | 0 | 1033022.55 | Yes | 0 | 1084029.4633 | 542014.7317 | 2168058.9266 | At-Risk | Non-DAC
CA1700630 | PIER 1900 HOMEOWNER S ASSOCIATION | 152 | 54 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2020386.7224 | 0 | No | 98208.6 | 2120375.2224 | 1060187.6112 | 4240750.4448 | Not At-Risk | Missing
CA0310021 | AWA - CAMANCHE VILLAGE | 2384 | 732 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA2701918 | LOMAS DEL SOL MWS | 93 | 32 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 53098.7007 | Yes | 0 | 0 | Yes | 0 | 55412.5707 | 27706.2854 | 110825.1414 | Potentially At-Risk | Non-DAC
CA1900903 | SLEEPY VALLEY WATER COMPANY | 130 | 58 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 58126.9962 | Yes | 0 | 0 | Yes | 0 | 60476.4642 | 30238.2321 | 120952.9285 | HR2W | Non-DAC
CA5200645 | SADDLEBACK MUTUAL WATER CO. | 90 | 38 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 78106.2 | 79886.1 | 39943.05 | 159772.2 | Potentially At-Risk | SDAC
CA5500119 | YOSEMITE VISTA ESTATES | 59 | 59 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2012349.6212 | 0 | Yes | 0 | 2012349.6212 | 1006174.8106 | 4024699.2423 | Potentially At-Risk | SDAC
CA5410001 | CUTLER PUD | 6200 | 1218 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 577872.9152 | Yes | 0 | 0 | No | 1543068.6 | 2120941.5152 | 1060470.7576 | 4241883.0305 | At-Risk | SDAC
CA3000618 | LIBERTY PARK WATER ASSOCIATION | 89 | 27 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 52646.8384 | No | 0 | 1141858.2 | No | 83571.54 | 1280390.4484 | 640195.2242 | 2560780.8968 | Not At-Risk | DAC
CA4910010 | SONOMA COUNTY CSA 41-FITCH MOUNTAIN | 1115 | 338 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA5402038 | PATTERSON TRACT CSD | 550 | 153 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 81451.9752 | Yes | 0 | 0 | Yes | 0 | 83231.8752 | 41615.9376 | 166463.7504 | Not At-Risk | SDAC
CA3900964 | SAHARA MOBILE COURT | 300 | 162 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 59486.4469 | No | 0 | 2298782.73 | No | 233899.8 | 2593948.8769 | 1296974.4384 | 5187897.7538 | At-Risk | SDAC
CA3610082 | SAN ANTONIO CANYON MSC | 125 | 64 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | Yes | 0 | 0 | No | 140737.74 | 140737.74 | 70368.87 | 281475.48 | Not At-Risk | Non-DAC
CA5601144 | RANCHO SESPE WORKERS IMP ASSOC | 600 | 109 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | No | 2349.468 | Yes | 0 | No | 2586233.4698 | 0 | No | 219191.544 | 2807774.4818 | 1403887.2409 | 5615548.9635 | Not At-Risk | DAC
CA1900975 | CALI LAKE RV RESORT | 99 | 47 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | Yes | 0 | No | 2531852.8872 | 0 | No | 118026.216 | 2652228.5712 | 1326114.2856 | 5304457.1425 | HR2W | Non-DAC
CA4900510 | SOUTH CLOVERDALE WATER COMPANY | 90 | 39 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 52759.804 | No | 0 | 1286972.4 | No | 103171.38 | 1445217.454 | 722608.727 | 2890434.908 | At-Risk | DAC
CA2000757 | MD 63 MEADOW SPRINGS RANCH | 300 | 85 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 59486.4469 | Yes | 0 | 0 | Yes | 0 | 59486.4469 | 29743.2234 | 118972.8938 | Potentially At-Risk | SDAC
CA4210021 | GOLDEN STATE WATER COMPANY - TANGLEWOOD | 1962 | 455 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 264231.3589 | Yes | 0 | 0 | Yes | 0 | 264231.3589 | 132115.6795 | 528462.7178 | Not At-Risk | Non-DAC
CA3301535 | RANCHO CARRILLO MWC | 210 | 74 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 67298.1273 | Yes | 0 | 0 | Yes | 0 | 67298.1273 | 33649.0636 | 134596.2546 | At-Risk | Non-DAC
CA3901303 | ACAMPO WATER SYSTEM | 150 | 70 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 46307.1299 | Yes | 0 | 0 | No | 118311 | 164618.1299 | 82309.0649 | 329236.2598 | Not At-Risk | Non-DAC
CA1900843 | CALIFORNIAN MOBILE HOME PARK | 372 | 133 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 85869.6677 | No | 0 | 2451399.732 | No | 260652.744 | 2800271.6117 | 1400135.8059 | 5600543.2234 | At-Risk | Missing
CA2300832 | HILLS RANCH MUTUAL WATER COMPANY | 77 | 48 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39893.1956 | Yes | 0 | 0 | Yes | 0 | 41673.0956 | 20836.5478 | 83346.1912 | Not At-Risk | DAC
CA5410050 | ALPAUGH COMMUNITY SERVICES DISTRICT | 1026 | 394 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 123274.3411 | Yes | 0 | 0 | Yes | 0 | 123274.3411 | 61637.1706 | 246548.6823 | At-Risk | SDAC
CA2800526 | BERRYESSA ESTATES (LBRID) | 476 | 187 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | DAC
CA4600012 | ALLEGHANY COUNTY W.D. | 80 | 57 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA2800527 | LINDA FALLS TERRACE MUTUAL | 35 | 17 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | No | 2492741.6578 | 0 | No | 41105.22 | 2536160.7478 | 1268080.3739 | 5072321.4957 | Not At-Risk | Non-DAC
CA5000218 | COUNTRY VILLA APTS | 60 | 23 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 38399.5397 | No | 2012436.0416 | 0 | No | 59260.2 | 2111875.6813 | 1055937.8406 | 4223751.3626 | HR2W | SDAC
CA2701278 | RANCHO CHAPARRAL MWC | 58 | 20 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 49144.9056 | No | 2495206.3689 | 0 | Yes | 0 | 2544351.2745 | 1272175.6372 | 5088702.549 | Potentially At-Risk | DAC
CA3400122 | EL DORADO WEST MHP | 172 | 128 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 62941.84 | No | 0 | 2390244.462 | No | 252360.504 | 2707896.274 | 1353948.137 | 5415792.5481 | Not At-Risk | SDAC
CA2701034 | APPLE AVE WS #02 | 75 | 18 | LPA57 - MONTEREY COUNTY | C | T - SECONDARY RESIDENCES | No | 2313.87 | No | 51065.3204 | No | 0 | 1033022.55 | Yes | 0 | 1086401.7404 | 543200.8702 | 2172803.4807 | Potentially At-Risk | DAC
CA3410026 | CALIFORNIA STATE FAIR | 650 | 269 | DISTRICT 09 - SACRAMENTO | C | O - OTHER AREA | No | 2349.468 | No | 117739.3481 | Yes | 0 | 0 | No | 486201.672 | 606290.4881 | 303145.2441 | 1212580.9763 | Not At-Risk | SDAC
CA1400037 | FOOTHILL MOBILE HOME PARK | 60 | 48 | DISTRICT 13 - SAN BERNARDINO | C | R - MOBILE HOME PARK | No | 1779.9 | No | 38399.5397 | Yes | 0 | 0 | No | 90670.2 | 130849.6397 | 65424.8198 | 261699.2794 | HR2W | SDAC
CA4300551 | HAPPY ACRES MWC | 220 | 79 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 68444.5187 | No | 2544986.7205 | 0 | Yes | 0 | 2613431.2392 | 1306715.6196 | 5226862.4785 | Not At-Risk | Non-DAC
CA1000298 | WOODWARD BLUFFS MHP | 300 | 172 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK | No | 1779.9 | No | 59486.4469 | No | 0 | 2398980.63 | No | 246463.8 | 2706710.7769 | 1353355.3884 | 5413421.5538 | Potentially At-Risk | Non-DAC
CA5610006 | YERBA BUENA WATER COMPANY | 690 | 245 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 122324.9137 | Yes | 0 | 0 | Yes | 0 | 122324.9137 | 61162.4568 | 244649.8273 | Not At-Risk | Non-DAC
CA4200802 | OAK TRAIL RANCH | 105 | 31 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 54454.2876 | Yes | 0 | 0 | Yes | 0 | 54454.2876 | 27227.1438 | 108908.5752 | Not At-Risk | Non-DAC
CA2910016 | DONNER SUMMIT PUBLIC UTILITY DISTRICT | 310 | 352 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 60365.068 | N/A | 0 | 0 | Yes | 0 | 60365.068 | 30182.534 | 120730.136 | Potentially At-Risk | Non-DAC
CA3400181 | LAGUNA DEL SOL INC | 470 | 112 | LPA64 - SACRAMENTO COUNTY | C | T - RECREATION AREA | No | 2349.468 | No | 97104.3033 | Yes | 0 | 0 | No | 225825.336 | 325279.1073 | 162639.5536 | 650558.2145 | Not At-Risk | Non-DAC
CA1900803 | EL DORADO MUTUAL WATER CO. | 660 | 237 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 118885.7395 | Yes | 0 | 0 | Yes | 0 | 121235.2075 | 60617.6038 | 242470.4151 | Not At-Risk | Non-DAC
CA1410009 | INYO COUNTY PWD - LONE PINE | 1835 | 503 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA0400081 | FEATHER RIDGE ESTATES WATER CO | 37 | 32 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36378.7111 | Yes | 0 | 0 | No | 70567.8 | 108726.4111 | 54363.2055 | 217452.8222 | HR2W | SDAC
CA3000825 | SOUTH MIDWAY CITY MUTUAL WATER CO. | 825 | 56 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 135789.501 | Yes | 0 | 0 | No | 130937.82 | 266727.321 | 133363.6605 | 533454.6421 | Not At-Risk | Missing
CA2410003 | CITY OF GUSTINE | 5855 | 1913 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 547560.4862 | Yes | 0 | 0 | Yes | 0 | 547560.4862 | 273780.2431 | 1095120.9723 | Potentially At-Risk | DAC
CA3110048 | PLACER CSA - SHERIDAN | 726 | 196 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 96915.7071 | Yes | 0 | 0 | No | 276617.4 | 375313.0071 | 187656.5036 | 750626.0143 | Not At-Risk | DAC
CA4600018 | SIERRAVILLE P.U.D. | 200 | 111 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA5601119 | SIETE ROBLES MUTUAL WATER CO | 323 | 95 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 80252.3499 | Yes | 0 | 0 | Yes | 0 | 82601.8179 | 41300.909 | 165203.6358 | Not At-Risk | Non-DAC
CA5200526 | HIDDEN HARBOR MARINA & RVP | 70 | 70 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 39278.1608 | No | 2013300.246 | 0 | No | 118311 | 2172669.3069 | 1086334.6534 | 4345338.6137 | Not At-Risk | Missing
CA3500912 | COMSTOCK MUTUAL WATER COMPANY | 100 | 33 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2499707.1456 | 0 | Yes | 0 | 2499707.1456 | 1249853.5728 | 4999414.2912 | Not At-Risk | Non-DAC
CA2700535 | JOST POST WA | 60 | 20 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49370.8368 | No | 2495420.6916 | 0 | No | 72138.3 | 2619243.6983 | 1309621.8492 | 5238487.3967 | Not At-Risk | Non-DAC
CA1500542 | WILLOW SPRINGS MOBILE HOME PARK | 275 | 104 | DISTRICT 19 - TEHACHAPI | C | R - MOBILE HOME PARK | No | 1779.9 | No | 57289.8941 | No | 2031016.4369 | 0 | No | 161028.6 | 2251114.831 | 1125557.4155 | 4502229.662 | Not At-Risk | SDAC
CA2700656 | MORO COJO MWA | 67 | 19 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 50161.5958 | Yes | 0 | 0 | Yes | 0 | 52475.4658 | 26237.7329 | 104950.9315 | Not At-Risk | Non-DAC
CA5400544 | ALLENSWORTH CSD | 521 | 164 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 78903.9739 | Yes | 0 | 0 | Yes | 0 | 78903.9739 | 39451.987 | 157807.9478 | HR2W | SDAC
CA1700589 | BLUE LAKES MOBILE HOME PARK | 32 | 24 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2010016.2692 | 0 | Yes | 0 | 2011796.1692 | 1005898.0846 | 4023592.3384 | At-Risk | DAC
CA2700503 | ASSISI MWC | 126 | 42 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 56826.5647 | No | 2502493.3407 | 0 | No | 106438.02 | 2668071.7953 | 1334035.8977 | 5336143.5906 | Not At-Risk | Missing
CA3110035 | WEIMAR WATER COMPANY | 1500 | 568 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA2000561 | MD 08 NORTH FORK WATER SYSTEM | 264 | 75 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 56323.4108 | No | 2030065.812 | 0 | Yes | 0 | 2086389.2229 | 1043194.6114 | 4172778.4457 | HR2W | SDAC
CA3710707 | USN SAN CLEMENTE ISLAND | 670 | 267 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | No | 227483.784 | 227483.784 | 113741.892 | 454967.568 | Not At-Risk | Missing
CA2010010 | MADERA VALLEY WATER COMPANY | 6372 | 1944 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 592985.1987 | Yes | 0 | 0 | No | 2406215.4 | 2999200.5987 | 1499600.2994 | 5998401.1975 | Not At-Risk | Non-DAC
CA1310003 | GSWC-CALIPATRIA | 4335 | 1164 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 414010.074 | N/A | 0 | 0 | Yes | 0 | 414010.074 | 207005.037 | 828020.1479 | At-Risk | SDAC
CA4300909 | LICK OBSERVATORY-UCSC | 284 | 32 | DISTRICT 17 - SANTA CLARA | C | NT - INSTITUTION | N/A | 0 | Yes | 0 | Yes | 0 | 0 | No | 93149.496 | 93149.496 | 46574.748 | 186298.992 | Not At-Risk | Non-DAC
CA5510006 | MI WUK VILLAGE MUT WTR CO | 1737 | 770 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 185744.3037 | Yes | 0 | 0 | Yes | 0 | 185744.3037 | 92872.1518 | 371488.6073 | Not At-Risk | Non-DAC
CA1910060 | LA PUENTE VALLEY CWD | 8108 | 2457 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | Yes | 0 | No | 972718.0414 | Yes | 0 | 0 | Yes | 0 | 972718.0414 | 486359.0207 | 1945436.0829 | Not At-Risk | Non-DAC
CA5010031 | CITY OF MODESTO - WALNUT MANOR | 175 | 53 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | No | 48503.6827 | No | 0 | 1206625.62 | No | 37901.4 | 1293030.7027 | 646515.3514 | 2586061.4054 | Not At-Risk | Non-DAC
CA4700503 | CALLAHAN WATER DISTRICT | 70 | 34 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 73080.6 | 73080.6 | 36540.3 | 146161.2 | Potentially At-Risk | SDAC
CA1010013 | HUME LAKE CHRISTIAN CAMPS, INC | 2649 | 388 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 517846.2 | 517846.2 | 258923.1 | 1035692.4 | Not At-Risk | Missing
CA0300037 | JACKSON VALLEY IRRIGATION DISTRICT | 3553 | 331 | DISTRICT 10 - STOCKTON | C | R - MOBILE HOME PARK | N/A | 0 | N/A | 0 | Yes | 0 | 0 | No | 270335.4 | 270335.4 | 135167.7 | 540670.8 | Not At-Risk | DAC
CA0600012 | COLUSA CO. SERVICE AREA #1-CENTURY RANCH | 246 | 88 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 54741.8928 | Yes | 0 | 0 | Yes | 0 | 56521.7928 | 28260.8964 | 113043.5855 | Not At-Risk | SDAC
CA1800516 | LITTLE VALLEY CSD | 70 | 44 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39278.1608 | No | 2013300.246 | 0 | Yes | 0 | 2054358.3069 | 1027179.1534 | 4108716.6137 | Not At-Risk | DAC
CA4700531 | TENNANT C.S.D. | 94 | 102 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 158515.8 | 160295.7 | 80147.85 | 320591.4 | Potentially At-Risk | SDAC
CA4100539 | KINGS MOUNTAIN PARK MUTUAL | 66 | 23 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 50790.0914 | Yes | 0 | 0 | Yes | 0 | 50790.0914 | 25395.0457 | 101580.1828 | Not At-Risk | Non-DAC
CA4200560 | SISQUOC | 133 | 76 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 57617.3237 | Yes | 0 | 0 | Yes | 0 | 57617.3237 | 28808.6618 | 115234.6473 | Not At-Risk | Non-DAC
CA3110022 | MCKINNEY WATER DISTRICT | 853 | 253 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 348232.2 | 348232.2 | 174116.1 | 696464.4 | Not At-Risk | Non-DAC
CA4400625 | VISTA ROBLES ASSOCIATION | 50 | 19 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 41105.22 | 43419.09 | 21709.545 | 86838.18 | Not At-Risk | DAC
CA5400542 | DUCOR CSD | 535 | 166 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 80134.0435 | Yes | 0 | 0 | No | 238925.4 | 319059.4435 | 159529.7218 | 638118.887 | Not At-Risk | SDAC
CA1700674 | WALNUT COVE MOBILE ESTATES | 200 | 60 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 50700.2356 | No | 2024534.9037 | 0 | No | 105747 | 2180982.1392 | 1090491.0696 | 4361964.2785 | Not At-Risk | SDAC
CA4700626 | COVE MOBILE VILLA | 105 | 47 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK | No | 1779.9 | No | 42353.3348 | No | 2016324.9616 | 0 | No | 89413.8 | 2149871.9963 | 1074935.9982 | 4299743.9927 | At-Risk | Non-DAC
CA4710008 | MT. SHASTA, CITY OF | 3642 | 1841 | DISTRICT 01 - KLAMATH | C | T - RECREATION AREA | Yes | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | DAC
CA4600017 | R.R. LEWIS SMALL WC | 324 | 120 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | No | 61595.1376 | Yes | 0 | 0 | Yes | 0 | 61595.1376 | 30797.5688 | 123190.2752 | Not At-Risk | SDAC
CA0400001 | YOUTH WITH A MISSION-SPRINGS OF LIVING W | 150 | 52 | LPA34 - BUTTE COUNTY | C | NT - INSTITUTION | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 95695.8 | 97475.7 | 48737.85 | 194951.4 | Not At-Risk | Non-DAC
CA4600019 | SIERRA CO. W.W.D #1 CALPINE | 225 | 135 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 52896.7884 | Yes | 0 | 0 | Yes | 0 | 52896.7884 | 26448.3942 | 105793.5768 | Not At-Risk | Non-DAC
CA5410026 | POPLAR COMM SERVICE DIST | 2200 | 597 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 226424.4621 | Yes | 0 | 0 | Yes | 0 | 228204.3621 | 114102.1811 | 456408.7242 | Not At-Risk | SDAC
CA0310018 | FIRST MACE MEADOWS UNIT NO. 2 | 200 | 82 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA4910007 | SEA RANCH WATER COMPANY,THE (PUC) | 6151 | 1872 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1502056 | CLARK STREET COMMUNITY WELL | 90 | 20 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 41035.4031 | No | 2015028.6549 | 0 | No | 55491 | 2111555.058 | 1055777.529 | 4223110.116 | At-Risk | SDAC
CA4710003 | FORT JONES, TOWN OF | 675 | 362 | DISTRICT 01 - KLAMATH | C | T - RECREATION AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA1700508 | GLENHAVEN MUTUAL WATER COMPANY | 300 | 131 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 194951.4 | 194951.4 | 97475.7 | 389902.8 | Not At-Risk | SDAC
CA1000359 | FCSA #32/CANTUA CREEK | 476 | 79 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 74950.1788 | N/A | 0 | 0 | Yes | 0 | 74950.1788 | 37475.0894 | 149900.3576 | HR2W | SDAC
CA4710001 | DORRIS, CITY OF | 887 | 420 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 545487 | 545487 | 272743.5 | 1090974 | Not At-Risk | SDAC
CA1910218 | LA HABRA HEIGHTS CWD | 5459 | 2006 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA | Yes | 0 | No | 669038.9641 | Yes | 0 | 0 | Yes | 0 | 669038.9641 | 334519.4821 | 1338077.9283 | Not At-Risk | Non-DAC
CA3500911 | CREEKBRIDGE MUTUAL WATER COMPANY | 69 | 22 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | No | 2496385.1437 | 0 | Yes | 0 | 2498699.0137 | 1249349.5069 | 4997398.0275 | At-Risk | Non-DAC
CA4700872 | MONTE SHASTA M.W.C. | 150 | 46 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | No | 46307.1299 | Yes | 0 | 0 | No | 31619.4 | 77926.5299 | 38963.2649 | 155853.0598 | Not At-Risk | SDAC
CA5200503 | MINERAL COUNTY WATER DISTRICT | 624 | 189 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA4500028 | SHASTA CSA - CRAGVIEW, #23 | 218 | 66 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | No | 52281.7536 | N/A | 0 | 0 | Yes | 0 | 52281.7536 | 26140.8768 | 104563.5072 | At-Risk | SDAC
CA5200521 | ANTELOPE CREEK MHP | 175 | 60 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 48503.6827 | No | 2022374.3926 | 0 | No | 105747 | 2178404.9753 | 1089202.4877 | 4356809.9506 | Not At-Risk | SDAC
CA1909006 | WEST VALLEY COUNTY WATER DISTRICT | 766 | 237 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA | Yes | 0 | No | 131037.4882 | Yes | 0 | 0 | Yes | 0 | 131037.4882 | 65518.7441 | 262074.9764 | Not At-Risk | DAC
CA1000229 | GREEN ACRES MOBILE HOME ESTATE | 350 | 113 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK | Yes | 0 | Yes | 0 | No | 0 | 1807813.02 | No | 172336.2 | 1980149.22 | 990074.61 | 3960298.44 | Potentially At-Risk | SDAC
CA2700738 | SAN MIGUEL WS #01 | 100 | 34 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 53889.4597 | Yes | 0 | 0 | No | 95004.78 | 151208.1097 | 75604.0549 | 302416.2194 | At-Risk | Non-DAC
CA5400553 | DEL ORO TRAVER DISTRICT | 660 | 199 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 91116.8077 | Yes | 0 | 0 | Yes | 0 | 91116.8077 | 45558.4038 | 182233.6153 | HR2W | SDAC
CA4900552 | MICHELE MUTUAL WATER COMPANY | 170 | 62 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 61797.0499 | Yes | 0 | 0 | No | 140737.74 | 202534.7899 | 101267.395 | 405069.5798 | Not At-Risk | Non-DAC
CA2300646 | BELLA SHORES MOBILE HOME PARK | 80 | 60 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2014164.4505 | 0 | No | 105747 | 2121691.3505 | 1060845.6752 | 4243382.7009 | At-Risk | SDAC
CA0310004 | PLYMOUTH, CITY OF | 1060 | 520 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | No | 1779.9 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | HR2W | Non-DAC
CA3610017 | HAVASU WC | 361 | 224 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 83373.4746 | N/A | 0 | 0 | Yes | 0 | 83373.4746 | 41686.7373 | 166746.9492 | HR2W | SDAC
CA2000506 | SIERRA LINDA MUTUAL WATER CO | 200 | 89 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 50700.2356 | Yes | 0 | 0 | No | 142182.6 | 192882.8356 | 96441.4178 | 385765.6711 | HR2W | DAC
CA2410007 | PLANADA CSD | 4500 | 1097 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 58003.8 | 58003.8 | 29001.9 | 116007.6 | Potentially At-Risk | SDAC
CA3610009 | BIGHORN - DESERT VIEW WATER AGENCY | 3689 | 1708 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 459322.9056 | Yes | 0 | 0 | Yes | 0 | 459322.9056 | 229661.4528 | 918645.8112 | Not At-Risk | SDAC
CA4500235 | WOODRIDGE MUTUAL WATER CO | 187 | 71 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | SDAC
CA5403217 | OKIEVILLE HIGHLAND ACRES MWC | 300 | 72 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 59486.4469 | No | 2033176.948 | 0 | Yes | 0 | 2094443.2949 | 1047221.6474 | 4188886.5898 | At-Risk | Missing
CA1210024 | WESTHAVEN C.S.D. | 490 | 226 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA | Yes | 0 | No | 76180.2484 | Yes | 0 | 0 | Yes | 0 | 76180.2484 | 38090.1242 | 152360.4968 | Potentially At-Risk | DAC
CA2702007 | VIERRA ESTATES WS | 164 | 48 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 61119.2565 | Yes | 0 | 0 | Yes | 0 | 61119.2565 | 30559.6282 | 122238.5129 | Not At-Risk | Non-DAC
CA2410011 | LE GRAND COMM SERVICES DIST | 1700 | 474 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 182493.4055 | Yes | 0 | 0 | Yes | 0 | 182493.4055 | 91246.7027 | 364986.811 | At-Risk | SDAC
CA1010021 | MENDOTA, CITY OF | 11104 | 2300 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1008748.7188 | Yes | 0 | 0 | Yes | 0 | 1008748.7188 | 504374.3594 | 2017497.4375 | Not At-Risk | SDAC
CA4900795 | STONEGATE MOBILE HOME PARK | 100 | 75 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | No | 2313.87 | No | 53889.4597 | No | 2499707.1456 | 0 | No | 161970.9 | 2717881.3753 | 1358940.6876 | 5435762.7506 | At-Risk | Non-DAC
CA3500823 | BEST ROAD MWC | 133 | 48 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 57617.3237 | Yes | 0 | 0 | Yes | 0 | 59931.1937 | 29965.5968 | 119862.3873 | HR2W | Non-DAC
CA3900661 | MAPACHE TRAILER PARK | 275 | 99 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 57289.8941 | No | 2031016.4369 | 0 | No | 154746.6 | 2244832.831 | 1122416.4155 | 4489665.662 | Potentially At-Risk | Missing
CA0900300 | KYBURZ MUTUAL WATER COMPANY | 150 | 118 | LPA39 - EL DORADO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 59537.7384 | Yes | 0 | 0 | No | 232203.66 | 294055.2684 | 147027.6342 | 588110.5369 | Potentially At-Risk | Missing
CA1410008 | INYO COUNTY PWD - INDEPENDENCE | 669 | 336 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA3601045 | BEAR VALLEY MHP | 150 | 98 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 59537.7384 | Yes | 0 | 0 | No | 150537.66 | 212389.2684 | 106194.6342 | 424778.5369 | Not At-Risk | SDAC
CA4400582 | PINE TREE LANE MUTUAL WATER CO | 80 | 36 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 51630.1482 | No | 0 | 1250693.85 | No | 96638.1 | 1401275.9682 | 700637.9841 | 2802551.9365 | Not At-Risk | Non-DAC
CA3600308 | FREEDOM ACRES THE RESORT | 500 | 100 | LPA66 - SAN BERNARDINO COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 2313.87 | No | 99075.6894 | Yes | 0 | 0 | No | 202803.9 | 304193.4594 | 152096.7297 | 608386.9188 | Not At-Risk | Non-DAC
CA5510026 | PHOENIX LAKE ESTATES CC MWC | 988 | 355 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA2410700 | CASTLE AIRPORT | 1650 | 134 | DISTRICT 11 - MERCED | C | NT - INDUSTRIAL/AGRICULTURAL | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 36645 | 36645 | 18322.5 | 73290 | At-Risk | SDAC
CA3410032 | FOLSOM STATE PRISON | 5422 | 2790 | DISTRICT 09 - SACRAMENTO | C | NT - INSTITUTION | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 4667149.08 | 4667149.08 | 2333574.54 | 9334298.16 | Not At-Risk | SDAC
CA3610060 | BDVWA - GOAT MOUNTAIN ID | 1300 | 602 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 189448.1488 | Yes | 0 | 0 | Yes | 0 | 189448.1488 | 94724.0744 | 378896.2976 | Not At-Risk | SDAC
CA3610028 | MARYGOLD MWC | 3055 | 926 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 387702.7315 | Yes | 0 | 0 | Yes | 0 | 387702.7315 | 193851.3658 | 775405.4631 | Not At-Risk | SDAC
CA5810004 | CITY OF WHEATLAND | 3456 | 1219 | DISTRICT 21 - VALLEY | C | O - OTHER AREA | Yes | 0 | No | 336779.2764 | Yes | 0 | 0 | Yes | 0 | 336779.2764 | 168389.6382 | 673558.5528 | Not At-Risk | Non-DAC
CA1700518 | LOCH LOMOND MUTUAL WATER CO | 588 | 238 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA3010071 | JOINT REGIONAL WATER SUPPLY SYSTEM | 0 | 42 | DISTRICT 08 - SANTA ANA | C | O - WHOLESALER (SELLS WATER) | N/A | 0 | N/A | 0 | Yes | 0 | 0 | No | 42738.54 | 42738.54 | 21369.27 | 85477.08 | Not At-Risk | Missing
CA2600532 | LUNDY MUTUAL WATER COMPANY | 70 | 32 | LPA56 - MONO COUNTY | C | NT - INDUSTRIAL/AGRICULTURAL | No | 1779.9 | No | 39278.1608 | No | 2013300.246 | 0 | No | 70567.8 | 2124926.1069 | 1062463.0534 | 4249852.2137 | Not At-Risk | Missing
CA0510005 | CCWD - WEST POINT | 988 | 584 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA1400072 | NORTH LONE PINE MUTUAL WATER COMPANY | 70 | 33 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 39278.1608 | Yes | 0 | 0 | No | 71824.2 | 111102.3608 | 55551.1804 | 222204.7217 | Not At-Risk | SDAC
CA4400665 | MEADOWRIDGE MUTUAL WATER CO | 42 | 18 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 47337.4564 | Yes | 0 | 0 | No | 68871.66 | 118522.9864 | 59261.4932 | 237045.9728 | At-Risk | Non-DAC
CA0707519 | DUTCH SLOUGH WATER WORKS | 49 | 58 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48128.2154 | No | 2494241.9167 | 0 | No | 119504.58 | 2664188.5822 | 1332094.2911 | 5328377.1644 | Not At-Risk | Non-DAC
CA2410012 | HILMAR COUNTY WATER DISTRICT | 5416 | 1649 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 508989.0184 | Yes | 0 | 0 | Yes | 0 | 508989.0184 | 254494.5092 | 1017978.0369 | Not At-Risk | DAC
CA5200562 | SKY VIEW COUNTY WATER | 412 | 85 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 69327.0036 | No | 2042856.0377 | 0 | Yes | 0 | 2113962.9412 | 1056981.4706 | 4227925.8825 | At-Risk | SDAC
CA3901172 | PAR COUNTRY ESTATES CSA-16 | 120 | 54 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 43671.2665 | Yes | 0 | 0 | No | 94439.4 | 138110.6665 | 69055.3332 | 276221.333 | Potentially At-Risk | Non-DAC
CA4300581 | VELLADAO MOBILE HOME PARK | 75 | 27 | DISTRICT 17 - SANTA CLARA | C | R - MOBILE HOME PARK | No | 2349.468 | No | 51821.8436 | No | 0 | 1154908.008 | Yes | 0 | 1209079.3196 | 604539.6598 | 2418158.6393 | Potentially At-Risk | DAC
CA5400631 | LINNELL FARM LABOR CENTER | 694 | 195 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 94104.1195 | Yes | 0 | 0 | No | 275361 | 369465.1195 | 184732.5598 | 738930.239 | At-Risk | SDAC
CA3700897 | GUATAY MUTUAL BENEFIT CORPORATION | 100 | 35 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | Non-DAC
CA2010005 | YOSEMITE SPRING PARK UTIL CO | 6224 | 1902 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 579981.606 | Yes | 0 | 0 | Yes | 0 | 579981.606 | 289990.803 | 1159963.2119 | HR2W | Non-DAC
CA5400792 | WOODVILLE FARM LABOR CENTER | 650 | 177 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 90238.1865 | Yes | 0 | 0 | No | 252745.8 | 342983.9865 | 171491.9933 | 685967.9731 | HR2W | SDAC
CA2702055 | VIERRA KNOLLS MWC | 66 | 22 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 50048.6302 | No | 2496063.6597 | 0 | No | 75404.94 | 2623831.0999 | 1311915.5499 | 5247662.1998 | Potentially At-Risk | Non-DAC
CA5401038 | AKIN WATER CO | 86 | 26 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | N/A | 0 | No | 40683.9546 | N/A | 0 | 0 | No | 63029.4 | 103713.3546 | 51856.6773 | 207426.7093 | At-Risk | SDAC
CA1500599 | CHOCTAW VALLEY MUTUAL WATER CO. | 44 | 18 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36993.7459 | No | 2011053.3145 | 0 | Yes | 0 | 2049826.9604 | 1024913.4802 | 4099653.9208 | Not At-Risk | Non-DAC
CA1500553 | RANCHOS DEL RIO | 62 | 24 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 38575.2639 | Yes | 0 | 0 | No | 60516.6 | 100871.7639 | 50435.882 | 201743.5278 | Not At-Risk | DAC
CA1502622 | GOSFORD ROAD WATER COMPANY | 50 | 15 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37520.9186 | Yes | 0 | 0 | Yes | 0 | 39300.8186 | 19650.4093 | 78601.6371 | At-Risk | Non-DAC
CA3110049 | TAHOE PARK WATER CO - SKYLAND/NIELSEN | 50 | 92 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 37520.9186 | Yes | 0 | 0 | No | 142182.6 | 179703.5186 | 89851.7593 | 359407.0371 | Not At-Risk | Missing
CA3110047 | TALMONT RESORT IMPROVEMENT DISTRICT | 300 | 346 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 59486.4469 | Yes | 0 | 0 | Yes | 0 | 59486.4469 | 29743.2234 | 118972.8938 | Not At-Risk | Non-DAC
CA1000018 | EASTON ESTATES WATER COMPANY | 302 | 108 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 59662.1711 | Yes | 0 | 0 | No | 164797.8 | 224459.9711 | 112229.9856 | 448919.9422 | Potentially At-Risk | SDAC
CA1805007 | HERLONG PUBLIC UTILITY DISTRICT | 2114 | 297 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 40414.2 | 40414.2 | 20207.1 | 80828.4 | Not At-Risk | DAC
CA1700580 | TWIN CREEKS MOBILE AND RV VILLAGE | 50 | 17 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2011571.8372 | 0 | Yes | 0 | 2011571.8372 | 1005785.9186 | 4023143.6743 | HR2W | Missing
CA1700536 | SUNRISE SHORE MUTUAL WATER COMPANY | 83 | 42 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 40420.3683 | No | 2014423.7118 | 0 | No | 83131.8 | 2139755.7801 | 1069877.8901 | 4279511.5602 | At-Risk | Non-DAC
CA4500254 | ANDERSON PARK VILLAGE | 112 | 45 | LPA75 - SHASTA COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 0 | 1126467.3 | No | 86901 | 1215148.2 | 607574.1 | 2430296.4 | Not At-Risk | SDAC
CA0800861 | RESERVATION RANCH | 50 | 20 | DISTRICT 01 - KLAMATH | C | NT - INDUSTRIAL/AGRICULTURAL | No | 1779.9 | Yes | 0 | No | 2011571.8372 | 0 | No | 55491 | 2068842.7372 | 1034421.3686 | 4137685.4743 | At-Risk | DAC
CA1400518 | VAN LOON WATER ASSOCIATION | 25 | 15 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 35324.3657 | Yes | 0 | 0 | No | 49209 | 86313.2657 | 43156.6329 | 172626.5315 | Not At-Risk | SDAC
CA1000063 | NEW AUBERRY WATER ASSOCIATION | 120 | 35 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 43671.2665 | Yes | 0 | 0 | No | 74337 | 118008.2665 | 59004.1332 | 236016.533 | HR2W | SDAC
CA3600388 | DESERT VIEW MOBILE PARK | 130 | 28 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | N/A | 0 | Yes | 0 | 0 | No | 85204.86 | 87518.73 | 43759.365 | 175037.46 | HR2W | SDAC
CA4710007 | MONTAGUE, CITY OF | 1495 | 536 | DISTRICT 01 - KLAMATH | C | T - RECREATION AREA | N/A | 0 | No | 164481.6723 | Yes | 0 | 0 | Yes | 0 | 164481.6723 | 82240.8361 | 328963.3445 | Not At-Risk | SDAC
CA1900767 | GOLDEN VALLEY MUNICIPAL WATER DISTRICT | 70 | 18 | LPA49 - LA COUNTY | C | T - OTHER TRANSIENT AREA | Yes | 0 | No | 51248.6479 | No | 2528705.109 | 0 | Yes | 0 | 2579953.757 | 1289976.8785 | 5159907.5139 | Potentially At-Risk | DAC
CA1510046 | LOST HILLS UTILITY DISTRICT | 2412 | 443 | DISTRICT 12 - VISALIA | C | O - WHOLESALER (SELLS WATER) | Yes | 0 | No | 245051.2301 | Yes | 0 | 0 | Yes | 0 | 245051.2301 | 122525.6151 | 490102.4603 | Not At-Risk | SDAC
CA3400179 | MC CLELLAN MHP | 700 | 199 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 123471.3051 | Yes | 0 | 0 | No | 370110.312 | 495931.0851 | 247965.5425 | 991862.1701 | Not At-Risk | SDAC
CA0500068 | DUNROVIN MOBILE HOME VILLAGE | 99 | 42 | LPA35 - CALAVERAS COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 41826.1621 | Yes | 0 | 0 | No | 83131.8 | 126737.8621 | 63368.9311 | 253475.7242 | Not At-Risk | SDAC
CA1500401 | METTLER COUNTY WATER DISTRICT | 157 | 43 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | Missing
CA5301008 | PINE COVE RV PARK | 223 | 81 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 132131.4 | 132131.4 | 66065.7 | 264262.8 | Not At-Risk | SDAC
CA1000405 | PIEDRA PARK ASSOCIATION | 25 | 15 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK | No | 1779.9 | No | 35324.3657 | No | 2009411.3261 | 0 | No | 49209 | 2095724.5918 | 1047862.2959 | 4191449.1836 | Potentially At-Risk | SDAC
CA3301247 | ELMS MOBILE PARK | 100 | 47 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 54687.8221 | No | 0 | 1399529.088 | No | 118026.216 | 1574592.5941 | 787296.297 | 3149185.1882 | Potentially At-Risk | SDAC
CA3900720 | SHADED TERRACE PWS | 161 | 72 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 47273.6131 | No | 2021164.5064 | 0 | No | 120823.8 | 2189261.9195 | 1094630.9598 | 4378523.839 | Potentially At-Risk | Non-DAC
CA5500092 | PONDEROSA MOBILE HOME PARK | 52 | 58 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK | No | 1779.9 | No | 37696.6428 | Yes | 0 | 0 | No | 103234.2 | 142710.7428 | 71355.3714 | 285421.4856 | Not At-Risk | Non-DAC
CA3600157 | LUCERNE VISTA MWC | 160 | 57 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 60667.3942 | Yes | 0 | 0 | Yes | 0 | 60667.3942 | 30333.6971 | 121334.7884 | Not At-Risk | SDAC
CA5400682 | PLAINVIEW MWC - CENTRAL WATER | 138 | 42 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 45252.7845 | No | 2019176.8362 | 0 | No | 83131.8 | 2147561.4207 | 1073780.7104 | 4295122.8414 | HR2W | SDAC
CA1502645 | MEADOWS OF THE KERN MUTUAL WATER COMPANY | 32 | 16 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 35939.4005 | Yes | 0 | 0 | Yes | 0 | 37719.3005 | 18859.6503 | 75438.601 | Potentially At-Risk | DAC
CA5500116 | PEPPERMINT CREEK MHP | 280 | 101 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK | N/A | 0 | No | 57729.2046 | N/A | 0 | 0 | Yes | 0 | 57729.2046 | 28864.6023 | 115458.4092 | Potentially At-Risk | DAC
CA4900573 | WILSHIRE HEIGHTS MUTUAL WATER COMPANY | 100 | 41 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2499707.1456 | 0 | Yes | 0 | 2499707.1456 | 1249853.5728 | 4999414.2912 | Potentially At-Risk | Non-DAC
CA3900561 | LODI LAKE MOBILE HOME PARK | 104 | 52 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 42265.4727 | No | 0 | 1196605.83 | No | 95695.8 | 1334567.1027 | 667283.5513 | 2669134.2054 | Not At-Risk | Non-DAC
CA3400192 | TUNNEL TRAILER PARK | 44 | 21 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 48268.0303 | No | 2525882.963 | 0 | No | 74906.568 | 2651407.0294 | 1325703.5147 | 5302814.0587 | Potentially At-Risk | SDAC
CA1910163 | VALENCIA HEIGHTS WATER CO. | 7775 | 1680 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA4900785 | NOEL HEIGHTS-CAL WATER SERVICE (PUC) | 137 | 50 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 58069.186 | No | 2503672.1155 | 0 | Yes | 0 | 2564055.1715 | 1282027.5857 | 5128110.343 | Not At-Risk | DAC
CA4700803 | SHADOW MOUNTAIN MHP | 100 | 73 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK | No | 1779.9 | No | 41914.0242 | Yes | 0 | 0 | No | 122080.2 | 165774.1242 | 82887.0621 | 331548.2485 | Not At-Risk | DAC
CA5510004 | PINECREST PERMITTEES ASSN | 1253 | 390 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | No | 1779.9 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | SDAC
CA1200544 | REDCREST WATER WORKS | 100 | 35 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 74337 | 74337 | 37168.5 | 148674 | Not At-Risk | SDAC
CA2300514 | ELK COUNTY WATER DISTRICT | 380 | 99 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 66515.4159 | No | 2040090.5835 | 0 | Yes | 0 | 2108385.8994 | 1054192.9497 | 4216771.7988 | Not At-Risk | SDAC
CA3610047 | GOLDEN STATE WATER CO - WRIGHTWOOD | 4440 | 2777 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 544160.0518 | Yes | 0 | 0 | Yes | 0 | 544160.0518 | 272080.0259 | 1088320.1037 | Not At-Risk | Non-DAC
CA4500023 | HAT CREEK HIGHLANDS MUTUAL WATER CO | 88 | 44 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | No | 40859.6789 | N/A | 0 | 0 | No | 85644.6 | 126504.2789 | 63252.1394 | 253008.5577 | Potentially At-Risk | SDAC
CA2010008 | MADERA CO MD10A-MADERA RANCHOS | 3172 | 944 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 311826.4362 | Yes | 0 | 0 | No | 1193789.4 | 1505615.8362 | 752807.9181 | 3011231.6725 | HR2W | Non-DAC
CA2000605 | WHISPERING PINES MHP | 36 | 30 | LPA50 - MADERA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 36290.849 | Yes | 0 | 0 | Yes | 0 | 38070.749 | 19035.3745 | 76141.498 | Not At-Risk | SDAC
CA5410008 | OROSI PUBLIC UTILITY DISTRICT | 8770 | 1579 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 803678.5464 | Yes | 0 | 0 | Yes | 0 | 803678.5464 | 401839.2732 | 1607357.0928 | Not At-Risk | SDAC
CA4900600 | RINCON VALLEY MOBILE ESTATES | 460 | 230 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | Not At-Risk | DAC
CA4900832 | LEISURE MOBILE HOME PARK | 410 | 186 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 41105.22 | 41105.22 | 20552.61 | 82210.44 | Not At-Risk | Non-DAC
CA3700923 | LAKE MORENA OAK SHORES MWC | 670 | 197 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 120032.1309 | Yes | 0 | 0 | Yes | 0 | 120032.1309 | 60016.0655 | 240064.2618 | At-Risk | DAC
CA4400624 | RANCHO CORRALITOS | 60 | 31 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49370.8368 | Yes | 0 | 0 | No | 42738.54 | 94423.2468 | 47211.6234 | 188846.4935 | Not At-Risk | Non-DAC
CA5500053 | LEISURE PINES MUTUAL WATER CO | 340 | 103 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 63000.9314 | Yes | 0 | 0 | No | 159772.2 | 224553.0314 | 112276.5157 | 449106.0628 | Not At-Risk | Non-DAC
CA4910029 | CAMP MEEKER WATER SYSTEM | 1171 | 356 | DISTRICT 18 - SONOMA | C | O - WHOLESALER (SELLS WATER) | Yes | 0 | No | 174875.5897 | No | 2614476.9512 | 0 | Yes | 0 | 2789352.5409 | 1394676.2704 | 5578705.0818 | Not At-Risk | DAC
CA4900611 | RAINS CREEK WATER DISTRICT | 208 | 63 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2511280.5714 | 0 | Yes | 0 | 2511280.5714 | 1255640.2857 | 5022561.1427 | Not At-Risk | Non-DAC
CA2701705 | TASSAJARA SPRINGS WS | 150 | 70 | LPA57 - MONTEREY COUNTY | C | NT - INSTITUTION | N/A | 0 | N/A | 0 | Yes | 0 | 0 | No | 153804.3 | 153804.3 | 76902.15 | 307608.6 | Not At-Risk | Non-DAC
CA1907028 | SPV WATER COMPANY | 211 | 73 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 67412.7664 | Yes | 0 | 0 | Yes | 0 | 67412.7664 | 33706.3832 | 134825.5329 | At-Risk | Non-DAC
CA1010001 | BAKMAN WATER COMPANY | 16756 | 2608 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1505345.383 | Yes | 0 | 0 | No | 147208.2 | 1652553.583 | 826276.7915 | 3305107.1661 | At-Risk | SDAC
CA3301511 | PINYON CREST HOA | 104 | 90 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 55146.3786 | Yes | 0 | 0 | Yes | 0 | 57495.8466 | 28747.9233 | 114991.6933 | Not At-Risk | DAC
CA0310019 | AWA LA MEL HEIGHTS #3 | 188 | 55 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | No | 49645.8902 | Yes | 0 | 0 | Yes | 0 | 49645.8902 | 24822.9451 | 99291.7804 | Not At-Risk | SDAC
CA5400529 | SHADY GROVE MHP, LLC | 95 | 42 | DISTRICT 24 - TULARE | C | R - MOBILE HOME PARK | No | 1779.9 | No | 41474.7137 | No | 0 | 1096407.93 | No | 83131.8 | 1222794.3437 | 611397.1718 | 2445588.6873 | Potentially At-Risk | SDAC
CA2701503 | MESA DEL TORO MWC | 90 | 35 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | Not At-Risk | Non-DAC
CA2710851 | SALINAS VALLEY STATE PRISON | 2489 | 2208 | DISTRICT 05 - MONTEREY | C | NT - INSTITUTION | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 3645842.46 | 3645842.46 | 1822921.23 | 7291684.92 | At-Risk | DAC
CA5601104 | CASITAS MUTUAL WATER COMPANY | 238 | 85 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 70508.0232 | Yes | 0 | 0 | Yes | 0 | 70508.0232 | 35254.0116 | 141016.0463 | Not At-Risk | Non-DAC
CA1009078 | HARRIS FEEDING COMPANY | 225 | 30 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | No | 52896.7884 | N/A | 0 | 0 | No | 55491 | 108387.7884 | 54193.8942 | 216775.5768 | Potentially At-Risk | SDAC
CA3901031 | 132 INVESTMENTS WATER SYSTEM | 100 | 93 | LPA69 - SAN JOAQUIN COUNTY | C | T - RESTAURANT | No | 1779.9 | No | 41914.0242 | No | 2015892.8593 | 0 | No | 147208.2 | 2206794.9836 | 1103397.4918 | 4413589.9671 | At-Risk | DAC
CA2810013 | BERRYESSA HIGHLANDS | 938 | 248 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | Non-DAC
CA4300924 | PARKWAY LAKES RV PARK | 250 | 121 | DISTRICT 17 - SANTA CLARA | C | R - MOBILE HOME PARK | No | 2349.468 | No | 71883.6928 | No | 2548243.0429 | 0 | No | 240751.368 | 2863227.5717 | 1431613.7858 | 5726455.1434 | Not At-Risk | Non-DAC
CA2702520 | ARROYO SECO ESTATES MWS | 70 | 27 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 50500.4925 | Yes | 0 | 0 | No | 47638.5 | 98138.9925 | 49069.4962 | 196277.985 | Not At-Risk | SDAC
CA2300591 | PINE MOUNTAIN MUTUAL WATER CO. | 310 | 124 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA5400819 | MOUNTAIN VIEW MHP | 44 | 24 | DISTRICT 24 - TULARE | C | R - MOBILE HOME PARK | No | 1779.9 | No | 36993.7459 | No | 2011053.3145 | 0 | No | 60516.6 | 2110343.5604 | 1055171.7802 | 4220687.1208 | Potentially At-Risk | SDAC
CA1700592 | KONOCTI SHORES | 99 | 99 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 154746.6 | 156526.5 | 78263.25 | 313053 | Not At-Risk | DAC
CA4500089 | PINE RIDGE PARK ESTATES | 44 | 27 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | N/A | 0 | No | 2011053.3145 | 0 | No | 64285.8 | 2077119.0145 | 1038559.5073 | 4154238.029 | Potentially At-Risk | SDAC
CA5000071 | TWIN CYPRESS MOBILE HOME PARK | 112 | 45 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2016929.9047 | 0 | No | 86901 | 2105610.8047 | 1052805.4023 | 4211221.6093 | Not At-Risk | Non-DAC
CA3100038 | HEATHER GLEN COMMUNITY SERVICE DIST | 250 | 101 | LPA61 - PLACER COUNTY | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | No | 55093.3412 | N/A | 0 | 0 | Yes | 0 | 55093.3412 | 27546.6706 | 110186.6824 | Potentially At-Risk | DAC
CA2702094 | BLACKIE RD WS #18 | 60 | 21 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 49370.8368 | No | 2495420.6916 | 0 | Yes | 0 | 2544791.5283 | 1272395.7642 | 5089583.0567 | Potentially At-Risk | DAC
CA1610006 | STRATFORD PUD | 1277 | 364 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 32875.8 | 32875.8 | 16437.9 | 65751.6 | Not At-Risk | SDAC
CA4200881 | OAK TRAIL ESTATES | 210 | 63 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 66315.6729 | Yes | 0 | 0 | Yes | 0 | 66315.6729 | 33157.8364 | 132631.3458 | Not At-Risk | Non-DAC
CA5800924 | CAMPTONVILLE COMMUNITY SERV DIST | 180 | 85 | LPA88 - YUBA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 48942.9933 | Yes | 0 | 0 | No | 32875.8 | 83598.6933 | 41799.3466 | 167197.3866 | Not At-Risk | DAC
CA5200556 | MAYWOOD MOBILE HOME PARK | 140 | 50 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 45428.5088 | No | 2019349.6771 | 0 | No | 93183 | 2159741.0858 | 1079870.5429 | 4319482.1717 | Potentially At-Risk | DAC
CA0706004 | OAKLEY MUTUAL WATER COMPANY | 170 | 50 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 61797.0499 | Yes | 0 | 0 | No | 121137.9 | 185248.8199 | 92624.41 | 370497.6398 | HR2W | Non-DAC
CA5304501 | SALYER MUTUAL WC (FORMERLY RIVERVIEW AC) | 231 | 70 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA3110015 | FULTON WATER COMPANY | 500 | 923 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 77058.8695 | Yes | 0 | 0 | No | 1190020.2 | 1267079.0695 | 633539.5348 | 2534158.1391 | Not At-Risk | DAC
CA3700934 | PAUMA VALLEY WATER COMPANY | 193 | 101 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 65349.2619 | Yes | 0 | 0 | Yes | 0 | 65349.2619 | 32674.631 | 130698.5239 | HR2W | DAC
CA3910002 | SAN JOAQUIN COUNTY - COLONIAL HEIGHTS | 1953 | 558 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 727665 | 727665 | 363832.5 | 1455330 | Not At-Risk | Non-DAC
CA4200618 | MIDLAND SCHOOL | 300 | 48 | LPA72 - SANTA BARBARA COUNTY | C | NT - SCHOOL | Yes | 0 | No | 76482.5746 | Yes | 0 | 0 | No | 117871.26 | 194353.8346 | 97176.9173 | 388707.6691 | Not At-Risk | Non-DAC
CA2710850 | CORRECTIONAL TRAINING FACILITY - SOLEDAD | 5500 | 2769 | DISTRICT 05 - MONTEREY | C | NT - INSTITUTION | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 4562134.98 | 4562134.98 | 2281067.49 | 9124269.96 | Not At-Risk | DAC
CA5410004 | FARMERSVILLE, CITY OF | 11327 | 2736 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1028341.97 | Yes | 0 | 0 | Yes | 0 | 1028341.97 | 514170.985 | 2056683.9401 | Not At-Risk | SDAC
CA1206004 | PALMER CREEK CSD | 320 | 132 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2034905.3569 | 0 | Yes | 0 | 2034905.3569 | 1017452.6784 | 4069810.7138 | Not At-Risk | SDAC
CA2701254 | CARMEL RIVIERA MWC | 584 | 177 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 108564.7976 | Yes | 0 | 0 | Yes | 0 | 110878.6676 | 55439.3338 | 221757.3353 | Not At-Risk | Non-DAC
CA3600094 | DOGWOOD BLUE JAY CYN IMP | 160 | 81 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 171770.82 | 171770.82 | 85885.41 | 343541.64 | Not At-Risk | SDAC
CA2100519 | ESTERO MUTUAL | 186 | 145 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 63604.4991 | Yes | 0 | 0 | Yes | 0 | 65918.3691 | 32959.1846 | 131836.7382 | Not At-Risk | Non-DAC
CA4300546 | SIERRA ROAD IMPROVEMENT ASSOCIATION INC | 280 | 50 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 75322.867 | N/A | 0 | 0 | Yes | 0 | 75322.867 | 37661.4335 | 150645.734 | Not At-Risk | Non-DAC
CA3210005 | GRAEAGLE WATER COMPANY | 737 | 935 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 251489.4 | 251489.4 | 125744.7 | 502978.8 | Not At-Risk | DAC
CA3700422 | LAGUNA MOUNTIAN MUTUAL WATER CO. | 100 | 28 | LPA67 - SAN DIEGO COUNTY | C | T - SECONDARY RESIDENCES | No | 2349.468 | No | 54687.8221 | No | 2531961.4313 | 0 | No | 86515.704 | 2675514.4254 | 1337757.2127 | 5351028.8508 | Not At-Risk | Non-DAC
CA3200155 | FRCCSD HOT SPRINGS | 25 | 17 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2009411.3261 | 0 | No | 49209 | 2060400.2261 | 1030200.113 | 4120800.4522 | Potentially At-Risk | SDAC
CA2700691 | PESANTE RD WS #06 | 48 | 16 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48015.2499 | No | 2494134.7554 | 0 | No | 65605.02 | 2610068.8953 | 1305034.4476 | 5220137.7905 | Not At-Risk | Non-DAC
CA5410011 | SPRINGVILLE PUD | 1500 | 390 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 164920.9828 | N/A | 0 | 0 | Yes | 0 | 164920.9828 | 82460.4914 | 329841.9656 | Not At-Risk | SDAC
CA3400296 | SAC CITY MOBILE HOME COMMUNITY LP | 350 | 164 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 83347.6067 | Yes | 0 | 0 | No | 312064.632 | 397761.7067 | 198880.8533 | 795523.4133 | Not At-Risk | SDAC
CA5304109 | BURNT RANCH ESTATES | 115 | 35 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | No | 43231.9559 | N/A | 0 | 0 | Yes | 0 | 43231.9559 | 21615.978 | 86463.9119 | Not At-Risk | DAC
CA0707613 | WILLOW MOBILE HOME PARK | 350 | 172 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | No | 2526497.483 | 0 | No | 320402.94 | 2849214.293 | 1424607.1465 | 5698428.586 | Not At-Risk | SDAC
CA5500115 | SUGAR PINE RV RESORT | 244 | 87 | DISTRICT 11 - MERCED | C | T - OTHER TRANSIENT AREA | No | 1779.9 | No | 54566.1685 | No | 0 | 1547298.48 | No | 139669.8 | 1743314.3485 | 871657.1743 | 3486628.6971 | Potentially At-Risk | Non-DAC
CA5400732 | PIERPOINT SPRINGS WATER CO. | 35 | 84 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36202.9869 | Yes | 0 | 0 | No | 135900.6 | 173883.4869 | 86941.7434 | 347766.9737 | Not At-Risk | SDAC
CA5500060 | MI WUK HEIGHTS MWC | 352 | 158 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 64055.2768 | Yes | 0 | 0 | No | 228874.2 | 292929.4768 | 146464.7384 | 585858.9535 | Not At-Risk | Non-DAC
CA1900155 | WILSONA GARDENS MUTUAL | 74 | 39 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 51707.2045 | Yes | 0 | 0 | Yes | 0 | 54056.6725 | 27028.3362 | 108113.345 | Not At-Risk | SDAC
CA3110018 | TAHOE PARK WATER COMPANY | 750 | 445 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2072066.1475 | 0 | No | 540461.4 | 2612527.5475 | 1306263.7738 | 5225055.095 | Not At-Risk | Non-DAC
CA3700041 | BARRETT LAKE MH AND RV LLC | 150 | 58 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 60419.779 | Yes | 0 | 0 | Yes | 0 | 62769.247 | 31384.6235 | 125538.494 | Not At-Risk | Non-DAC
CA4400723 | MISSION SPRINGS CONFERENCE CENTER | 1310 | 141 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 190577.8045 | Yes | 0 | 0 | No | 148904.34 | 341796.0145 | 170898.0073 | 683592.0291 | Not At-Risk | Non-DAC
CA3301775 | HIGH VALLEYS WATER DISTRICT | 762 | 231 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA | N/A | 0 | No | 130578.9316 | N/A | 0 | 0 | Yes | 0 | 130578.9316 | 65289.4658 | 261157.8633 | Not At-Risk | Non-DAC
CA3600372 | PALMS RIVER RESORT | 127 | 205 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 56939.5302 | Yes | 0 | 0 | No | 126037.86 | 182977.3902 | 91488.6951 | 365954.7805 | Not At-Risk | SDAC
CA1000267 | KINGS CANYON MOBILE HOME PARK | 120 | 26 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK | No | 1779.9 | No | 43671.2665 | Yes | 0 | 0 | No | 63029.4 | 108480.5665 | 54240.2832 | 216961.133 | Not At-Risk | Non-DAC
CA5010026 | WATERFORD - HICKMAN | 597 | 180 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | Non-DAC
CA2000828 | SHADY OAKS MOBILE HOME PARK LLC | 27 | 21 | LPA50 - MADERA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 35500.09 | Yes | 0 | 0 | No | 56747.4 | 94027.39 | 47013.695 | 188054.7799 | HR2W | SDAC
CA3301800 | STONEWOOD CANYON ESTATES | 40 | 26 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 47809.4738 | No | 2525448.7867 | 0 | No | 83198.808 | 2658806.5365 | 1329403.2683 | 5317613.073 | Not At-Risk | Non-DAC
CA2702256 | NORTH SHORE ESTATES WS | 60 | 33 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 49370.8368 | Yes | 0 | 0 | Yes | 0 | 51684.7068 | 25842.3534 | 103369.4135 | Not At-Risk | SDAC
CA5000015 | OID #22 - WILLIAMS TRACT | 150 | 53 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 46307.1299 | No | 0 | 1206625.62 | No | 96952.2 | 1351664.8499 | 675832.4249 | 2703329.6998 | Not At-Risk | Non-DAC
CA1900100 | METTLER VALLEY MUTUAL | 135 | 98 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 58700.1919 | Yes | 0 | 0 | No | 55005.192 | 116054.8519 | 58027.426 | 232109.7039 | HR2W | DAC
CA2701670 | LANGLEY/VALLE PACIFICO WS | 81 | 31 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 51743.1138 | No | 2497671.0799 | 0 | Yes | 0 | 2549414.1937 | 1274707.0969 | 5098828.3875 | At-Risk | Non-DAC
CA3610110 | ARROWBEAR PARK CWD | 1856 | 955 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 252257.0081 | Yes | 0 | 0 | Yes | 0 | 252257.0081 | 126128.504 | 504514.0161 | Potentially At-Risk | DAC
CA2700799 | VISTA DEL TORO WS | 92 | 28 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 52985.7351 | Yes | 0 | 0 | Yes | 0 | 55299.6051 | 27649.8026 | 110599.2103 | Potentially At-Risk | Non-DAC
CA4200807 | WOODSTOCK RANCH | 350 | 117 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 82130.8533 | Yes | 0 | 0 | No | 41105.22 | 123236.0733 | 61618.0366 | 246472.1466 | Potentially At-Risk | Non-DAC
CA5200551 | WOODSON BRIDGE MHP | 158 | 104 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 47010.0268 | No | 2020905.2451 | 0 | No | 161028.6 | 2230723.7718 | 1115361.8859 | 4461447.5437 | Not At-Risk | DAC
CA2000589 | MAMMOTH POOL MOBILE HOME PARK | 60 | 32 | LPA50 - MADERA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 38399.5397 | No | 2012436.0416 | 0 | Yes | 0 | 2052615.4813 | 1026307.7406 | 4105230.9626 | At-Risk | SDAC
CA2000511 | MD 85 VALETA | 45 | 20 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 37081.608 | No | 2011139.735 | 0 | No | 55491 | 2103712.3429 | 1051856.1715 | 4207424.6859 | At-Risk | DAC
CA1700561 | BLUE LAKES IMPROVEMENT CLUB | 80 | 41 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2014164.4505 | 0 | No | 68055 | 2082219.4505 | 1041109.7252 | 4164438.9009 | Not At-Risk | DAC
CA1502320 | LERDO SHERIFF S FACILITY | 2800 | 110 | DISTRICT 12 - VISALIA | C | NT - INSTITUTION | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 168567 | 168567 | 84283.5 | 337134 | Not At-Risk | Non-DAC
CA2310010 | HOPLAND PUBLIC UTILITY DISTRICT | 1076 | 329 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA3900607 | COUNTRY SQUIRE MOBILE ESTATES & WATER SY | 64 | 49 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 38750.9881 | No | 2012781.7234 | 0 | No | 91926.6 | 2145239.2115 | 1072619.6058 | 4290478.4231 | Potentially At-Risk | SDAC
CA1900936 | AQUA J. MUTUAL WATER COMPANY | 165 | 48 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 62139.3661 | No | 0 | 1411760.142 | Yes | 0 | 1476248.9761 | 738124.488 | 2952497.9522 | Potentially At-Risk | SDAC
CA5400744 | EAST THREE RIVERS MUTUAL WATER CORP | 40 | 15 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 36642.2974 | No | 2010707.6327 | 0 | No | 49209 | 2098338.8302 | 1049169.4151 | 4196677.6603 | Not At-Risk | SDAC
CA2400209 | SAN LUIS HILLS | 300 | 65 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | SDAC
CA1100616 | ELK CREEK COMMUNITY S.D. | 159 | 90 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 47097.8889 | N/A | 0 | 0 | Yes | 0 | 47097.8889 | 23548.9445 | 94195.7778 | At-Risk | DAC
CA5400824 | SULTANA CSD | 866 | 249 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 109216.403 | Yes | 0 | 0 | No | 343206.6 | 452423.003 | 226211.5015 | 904846.006 | At-Risk | SDAC
CA5402048 | DEL ORO RIVER ISLAND SERV TERR #2 | 99 | 27 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 41826.1621 | Yes | 0 | 0 | Yes | 0 | 41826.1621 | 20913.0811 | 83652.3242 | At-Risk | DAC
CA0900112 | CANDLELIGHT VILLAGE MUTUAL WATER CO. | 32 | 32 | LPA39 - EL DORADO COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 70504.98 | 70504.98 | 35252.49 | 141009.96 | Not At-Risk | DAC
CA3100058 | DUTCH FLAT MUTUAL | 350 | 104 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | DAC
CA1400002 | STARLITE COMMUNITY SERVICE DISTRICT | 231 | 71 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA4000815 | LAS VENTANAS RANCH | 108 | 33 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 54793.1843 | Yes | 0 | 0 | Yes | 0 | 57107.0543 | 28553.5272 | 114214.1086 | HR2W | Missing
CA1410006 | BIG PINE CSD | 792 | 304 | DISTRICT 13 - SAN BERNARDINO | C | R - MUNICIPALITY | N/A | 0 | No | 102714.6066 | Yes | 0 | 0 | Yes | 0 | 102714.6066 | 51357.3033 | 205429.2132 | Not At-Risk | DAC
CA3610030 | MARIANA RANCHOS CWD | 1459 | 442 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 207409.6751 | Yes | 0 | 0 | Yes | 0 | 207409.6751 | 103704.8375 | 414819.3502 | Not At-Risk | SDAC
CA2700687 | PESANTE RD WS #02 | 120 | 40 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 56148.7712 | No | 2501850.3726 | 0 | No | 104804.7 | 2665117.7138 | 1332558.8569 | 5330235.4276 | Potentially At-Risk | Non-DAC
CA5510023 | SONORA MEADOWS MUTUAL WTR CO | 1123 | 448 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 131796.9661 | Yes | 0 | 0 | Yes | 0 | 131796.9661 | 65898.4831 | 263593.9322 | Not At-Risk | Non-DAC
CA2700728 | SAN ARDO WD | 575 | 161 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 107548.1075 | Yes | 0 | 0 | Yes | 0 | 107548.1075 | 53774.0537 | 215096.215 | Not At-Risk | DAC
CA2300717 | CREEKSIDE CABINS & RV RESORT | 124 | 55 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK,PRINC. RES. | No | 1779.9 | Yes | 0 | No | 2017966.95 | 0 | No | 99465 | 2119211.85 | 1059605.925 | 4238423.7 | Potentially At-Risk | SDAC
CA1000426 | RIVERBEND MOBILE HOME & RV PARK | 400 | 49 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK | No | 1779.9 | No | 68272.6582 | Yes | 0 | 0 | No | 91926.6 | 161979.1582 | 80989.5791 | 323958.3164 | Not At-Risk | DAC
CA3400155 | SEQUOIA WATER ASSOC | 54 | 18 | LPA64 - SACRAMENTO COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 49414.4217 | No | 2526968.4038 | 0 | No | 69931.224 | 2648663.5175 | 1324331.7588 | 5297327.035 | Not At-Risk | SDAC
CA3400138 | LOCKE WATER WORKS CO [SWS] | 80 | 44 | LPA64 - SACRAMENTO COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 52395.0393 | No | 2529790.5498 | 0 | No | 113050.872 | 2697585.9291 | 1348792.9646 | 5395171.8582 | HR2W | SDAC
CA1200518 | RIVERSIDE CSD | 293 | 101 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | SDAC
CA3303087 | SAN JOSE COMMUNITY WATER SYSTEM | 71 | 15 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 51363.2871 | No | 2528813.6531 | 0 | No | 64955.88 | 2647482.2882 | 1323741.1441 | 5294964.5763 | At-Risk | Missing
CA1510025 | STALLION SPRINGS CSD | 4441 | 1375 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA1410505 | NPS - DEATH VALLEY, FURNACE CREEK | 150 | 150 | DISTRICT 13 - SAN BERNARDINO | C | T - RECREATION AREA | No | 1779.9 | No | 46307.1299 | Yes | 0 | 0 | Yes | 0 | 48087.0299 | 24043.5149 | 96174.0598 | Not At-Risk | SDAC
CA1910023 | AVERYDALE MWC | 964 | 297 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | Yes | 0 | No | 153736.0376 | Yes | 0 | 0 | Yes | 0 | 153736.0376 | 76868.0188 | 307472.0751 | Not At-Risk | DAC
CA2701633 | PARADISE RD WS #21 | 48 | 16 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48015.2499 | No | 2494134.7554 | 0 | No | 65605.02 | 2610068.8953 | 1305034.4476 | 5220137.7905 | At-Risk | DAC
CA1500364 | KERNVALE MUTUAL WATER CO | 75 | 32 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 70567.8 | 70567.8 | 35283.9 | 141135.6 | Potentially At-Risk | Missing
CA5200560 | MIRA MONTE WATER CO. | 142 | 41 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 45604.233 | No | 2019522.518 | 0 | Yes | 0 | 2066906.6509 | 1033453.3255 | 4133813.3019 | Not At-Risk | Non-DAC
CA3901092 | SAN JOAQUIN WATER WORKS #2 | 293 | 94 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 58871.4121 | Yes | 0 | 0 | Yes | 0 | 58871.4121 | 29435.706 | 117742.8242 | Not At-Risk | DAC
CA3600386 | FOOTHILL ESTATES MHP | 135 | 33 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 57843.2548 | No | 2503457.7928 | 0 | No | 93371.46 | 2656986.3776 | 1328493.1888 | 5313972.7553 | At-Risk | SDAC
CA2310012 | IRISH BEACH WATER DISTRICT | 560 | 204 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 82330.5963 | Yes | 0 | 0 | Yes | 0 | 82330.5963 | 41165.2982 | 164661.1927 | Not At-Risk | DAC
CA3510006 | MISSION OAKS MOBILE HOME PARK | 550 | 238 | DISTRICT 05 - MONTEREY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 104723.9681 | Yes | 0 | 0 | Yes | 0 | 107037.8381 | 53518.9191 | 214075.6762 | Not At-Risk | Non-DAC
CA3500510 | MCMAHON ROAD MUTUAL WATER COMPANY | 102 | 32 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 54115.3909 | No | 2499921.4683 | 0 | Yes | 0 | 2556350.7291 | 1278175.3646 | 5112701.4583 | Potentially At-Risk | Non-DAC
CA2701068 | IVERSON & JACKS APTS WS | 150 | 31 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 59537.7384 | Yes | 0 | 0 | Yes | 0 | 61851.6084 | 30925.8042 | 123703.2169 | At-Risk | SDAC
CA5400550 | SEVILLE WATER COMPANY | 691 | 90 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 93840.5332 | Yes | 0 | 0 | No | 143439 | 239059.4332 | 119529.7166 | 478118.8664 | At-Risk | DAC
CA2800521 | CIRCLE OAKS WATER DISTRICT | 500 | 190 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA4300771 | NEW AVENUE MUTUAL WATER COMPANY | 302 | 113 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 77844.928 | Yes | 0 | 0 | Yes | 0 | 77844.928 | 38922.464 | 155689.856 | Not At-Risk | Non-DAC
CA4900793 | VINEHILL VISTAS MUTUAL WATER COMPANY | 42 | 29 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 47337.4564 | Yes | 0 | 0 | No | 86838.18 | 136489.5064 | 68244.7532 | 272979.0128 | Not At-Risk | Non-DAC
CA4200714 | SAN AUGUSTINE MUTUAL WATER COMPANY | 43 | 23 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 47450.422 | Yes | 0 | 0 | Yes | 0 | 47450.422 | 23725.211 | 94900.844 | Potentially At-Risk | Non-DAC
CA3303035 | THERMAL PARK | 73 | 22 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 51592.5654 | No | 0 | 1093752.738 | No | 76565.016 | 1224259.7874 | 612129.8937 | 2448519.5747 | Potentially At-Risk | SDAC
CA4200733 | MONTECITO SEA MEADOWS | 70 | 28 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 85204.86 | 85204.86 | 42602.43 | 170409.72 | Not At-Risk | Non-DAC
CA4900512 | HAPPY ACRES MUTUAL BENEFIT WATER SYSTEM | 260 | 79 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | No | 2516852.9615 | 0 | Yes | 0 | 2519166.8315 | 1259583.4158 | 5038333.6631 | Potentially At-Risk | Non-DAC
CA0707585 | MORAGA HEIGHTS MUTUAL WATER | 60 | 20 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | No | 2495420.6916 | 0 | Yes | 0 | 2497734.5616 | 1248867.2808 | 4995469.1232 | Not At-Risk | Non-DAC
CA3910024 | SAN JOAQUIN COUNTY - WILKINSON MANOR | 903 | 258 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | No | 112467.3012 | Yes | 0 | 0 | No | 272848.2 | 385315.5012 | 192657.7506 | 770631.0024 | Not At-Risk | Non-DAC
CA5403212 | MONSON WATER SYSTEM | 140 | 32 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 45428.5088 | No | 2019349.6771 | 0 | No | 70567.8 | 2137125.8858 | 1068562.9429 | 4274251.7717 | Potentially At-Risk | DAC
CA1900130 | DEL RIO MUTUAL | 700 | 250 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 123471.3051 | No | 0 | 3882433.05 | No | 318698.424 | 4324602.7791 | 2162301.3895 | 8649205.5581 | Potentially At-Risk | DAC
CA4500290 | PINE GROVE MOBILEHOME PARK | 53 | 19 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 37784.5049 | No | 2011831.0985 | 0 | No | 54234.6 | 2103850.2034 | 1051925.1017 | 4207700.4068 | Not At-Risk | SDAC
CA1502653 | BELLA VISTA MUTUAL WATER COMPANY | 150 | 46 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 46307.1299 | Yes | 0 | 0 | No | 88157.4 | 136244.4299 | 68122.2149 | 272488.8598 | At-Risk | SDAC
CA3900512 | MORADA ACRES WATER SYSTEM | 105 | 32 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 42353.3348 | No | 2016324.9616 | 0 | No | 70567.8 | 2129246.0963 | 1064623.0482 | 4258492.1927 | Potentially At-Risk | Non-DAC
CA2700733 | SAN JUAN RD WS #01 | 49 | 15 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48128.2154 | No | 2494241.9167 | 0 | No | 63971.7 | 2608655.7022 | 1304327.8511 | 5217311.4044 | Not At-Risk | Non-DAC
CA1700584 | WESTWIND MOBILE HOME PARK | 104 | 38 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK | N/A | 0 | No | 42265.4727 | N/A | 0 | 0 | Yes | 0 | 42265.4727 | 21132.7363 | 84530.9454 | Potentially At-Risk | Non-DAC
CA3901159 | WILKINSON MANOR A-ZONE PWS | 100 | 38 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | N/A | 0 | 0 | No | 78106.2 | 78106.2 | 39053.1 | 156212.4 | Potentially At-Risk | Non-DAC
CA1400006 | PINE CREEK VILLAGE | 350 | 89 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 63879.5525 | Yes | 0 | 0 | No | 142182.6 | 206062.1525 | 103031.0763 | 412124.3051 | HR2W | Non-DAC
CA2701956 | PIONEER PLACE MWS | 66 | 22 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 50048.6302 | Yes | 0 | 0 | Yes | 0 | 52362.5002 | 26181.2501 | 104725.0004 | Not At-Risk | Non-DAC
CA1000295 | KINGS PARK APARTMENTS | 120 | 41 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | No | 1779.9 | N/A | 0 | No | 2017621.2682 | 0 | No | 81875.4 | 2101276.5682 | 1050638.2841 | 4202553.1364 | At-Risk | Non-DAC
CA1500483 | ALLEN ROAD MUTUAL WATER SYSTEM | 195 | 59 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 50260.925 | Yes | 0 | 0 | No | 104490.6 | 156531.425 | 78265.7125 | 313062.85 | Not At-Risk | Non-DAC
CA5400735 | RODRIGUEZ LABOR CAMP | 110 | 35 | DISTRICT 24 - TULARE | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | No | 42792.6454 | No | 2016757.0638 | 0 | No | 74337 | 2135666.6091 | 1067833.3046 | 4271333.2183 | HR2W | SDAC
CA1700702 | INNISFREE WATER COMPANY | 56 | 17 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 38048.0912 | No | 2012090.3598 | 0 | Yes | 0 | 2051918.3511 | 1025959.1755 | 4103836.7021 | At-Risk | SDAC
CA4000741 | H2O, INC | 60 | 25 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 49370.8368 | Yes | 0 | 0 | Yes | 0 | 49370.8368 | 24685.4184 | 98741.6735 | Not At-Risk | Non-DAC
CA5000014 | OID #46 - SUNSET OAKS | 269 | 79 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 56762.7214 | Yes | 0 | 0 | No | 129618.6 | 188161.2214 | 94080.6107 | 376322.4427 | Not At-Risk | Non-DAC
CA5410039 | PLAINVIEW MUTUAL WATER COMPANY | 617 | 187 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 87338.7368 | No | 2060572.2286 | 0 | No | 265309.8 | 2413220.7653 | 1206610.3827 | 4826441.5307 | HR2W | SDAC
CA2701063 | RIVER RD WS #25 | 65 | 19 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 2313.87 | N/A | 0 | No | 2495956.4983 | 0 | Yes | 0 | 2498270.3683 | 1249135.1842 | 4996540.7367 | HR2W | DAC
CA1400109 | SIERRA NORTH COMMUNITY SERVICE DISTRICT | 45 | 16 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37081.608 | No | 2011139.735 | 0 | No | 50465.4 | 2100466.6429 | 1050233.3215 | 4200933.2859 | HR2W | Non-DAC
CA1900849 | LLANO DEL RIO WATER COMPANY | 510 | 186 | LPA49 - LA COUNTY | C | O - WHOLESALER (SELLS WATER) | Yes | 0 | No | 101689.8688 | Yes | 0 | 0 | No | 41737.608 | 143427.4768 | 71713.7384 | 286854.9536 | Not At-Risk | DAC
CA0500027 | LILI VALLEY WATER CO. | 99 | 70 | LPA35 - CALAVERAS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 41826.1621 | Yes | 0 | 0 | No | 118311 | 161917.0621 | 80958.5311 | 323834.1242 | Not At-Risk | SDAC
CA1000627 | ZONNEVELD DAIRY - CERINI | 48 | 17 | DISTRICT 23 - FRESNO | C | NT - OTHER NON-TRANSIENT AREA | No | 1779.9 | No | 37345.1943 | No | 2011398.9963 | 0 | No | 51721.8 | 2102245.8906 | 1051122.9453 | 4204491.7812 | At-Risk | SDAC
CA1700609 | LAZY S MOBILE RANCH | 73 | 24 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 60516.6 | 60516.6 | 30258.3 | 121033.2 | HR2W | SDAC
CA3900907 | BEL AIR MOBILE ESTATE | 150 | 116 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | No | 46307.1299 | Yes | 0 | 0 | No | 176105.4 | 222412.5299 | 111206.2649 | 444825.0598 | Not At-Risk | SDAC
CA4400755 | MONTEREY BAY ACADEMY | 400 | 78 | LPA74 - SANTA CRUZ COUNTY | C | NT - SCHOOL | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 81938.22 | 84252.09 | 42126.045 | 168504.18 | At-Risk | Non-DAC
CA2610004 | JUNE LAKE PUD - DOWN CANYON | 2810 | 389 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | N/A | 0 | No | 280020.3512 | Yes | 0 | 0 | No | 31619.4 | 311639.7512 | 155819.8756 | 623279.5024 | Not At-Risk | Missing
CA0707553 | RIVERVIEW MOBILE HOMES | 216 | 45 | LPA37 - CONTRA COSTA COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 66993.4663 | No | 0 | 1359529.5 | No | 112971.3 | 1541808.1363 | 770904.0682 | 3083616.2727 | Not At-Risk | Non-DAC
CA3600086 | DAGGETT COMM SVCS DIST | 795 | 196 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 132400.5338 | Yes | 0 | 0 | Yes | 0 | 132400.5338 | 66200.2669 | 264801.0676 | HR2W | SDAC
CA5400660 | LAKE SUCCESS MOBILE LODGE | 80 | 19 | DISTRICT 24 - TULARE | C | R - MOBILE HOME PARK | Yes | 0 | Yes | 0 | No | 2014164.4505 | 0 | No | 31619.4 | 2045783.8505 | 1022891.9252 | 4091567.7009 | At-Risk | DAC
CA2210925 | YOSEMITE TERRACE ESTATES | 130 | 53 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK | No | 1779.9 | No | 44549.8876 | No | 2018485.4726 | 0 | No | 95695.8 | 2160511.0603 | 1080255.5301 | 4321022.1205 | HR2W | SDAC
CA5400903 | TRACT 92 CSD | 500 | 93 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 147208.2 | 148988.1 | 74494.05 | 297976.2 | Potentially At-Risk | SDAC
CA4900508 | CAZADERO WATER COMPANY, INC. (PUC) | 250 | 157 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | DAC
CA2700629 | MANZANITA HILLS WA | 75 | 31 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 51065.3204 | Yes | 0 | 0 | No | 90104.82 | 143484.0104 | 71742.0052 | 286968.0207 | Not At-Risk | Non-DAC
CA4300856 | SPRING VALLEY HEIGHTS ASSOCIATION INC | 63 | 19 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA0910015 | TAHOE KEYS WATER COMPANY | 1420 | 1566 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 2549884.74 | 2549884.74 | 1274942.37 | 5099769.48 | HR2W | Non-DAC
CA1900154 | TIERRA BONITA MUTUAL WATER | 75 | 32 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 51821.8436 | No | 2529247.8294 | 0 | No | 55005.192 | 2638424.333 | 1319212.1665 | 5276848.6661 | Potentially At-Risk | SDAC
CA3400121 | EL DORADO MOBILE HOME PARK | 256 | 128 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 72571.5277 | Yes | 0 | 0 | No | 252360.504 | 327281.4997 | 163640.7498 | 654562.9993 | Not At-Risk | SDAC
CA5400934 | PONDEROSA CSD | 340 | 146 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 75593.4 | 75593.4 | 37796.7 | 151186.8 | Not At-Risk | SDAC
CA2700837 | BLACKIE RD WS #05 | 62 | 16 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 49596.7679 | No | 2495635.0143 | 0 | Yes | 0 | 2545231.7822 | 1272615.8911 | 5090463.5644 | Not At-Risk | DAC
CA1400025 | VALLEY VISTA MUTUAL WATER COMPANY | 70 | 25 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39278.1608 | No | 2013300.246 | 0 | No | 61773 | 2116131.3069 | 1058065.6534 | 4232262.6137 | Not At-Risk | Non-DAC
CA2000521 | BROADVIEW TERRACE MUTUAL WATER COMPANY | 498 | 178 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | No | 1779.9 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | SDAC
CA4300740 | MOUNTAIN SPRINGS MUTUAL WATER COMPANY | 37 | 18 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 47465.5564 | Yes | 0 | 0 | Yes | 0 | 49815.0244 | 24907.5122 | 99630.0488 | Not At-Risk | Non-DAC
CA1010052 | SIERRA CEDARS CSD | 850 | 229 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 107810.6092 | Yes | 0 | 0 | Yes | 0 | 107810.6092 | 53905.3046 | 215621.2184 | Not At-Risk | Non-DAC
CA5403113 | SOUTH FORK ESTATES MUTUAL WATER CO | 92 | 39 | DISTRICT 24 - TULARE | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | No | 41211.1273 | Yes | 0 | 0 | Yes | 0 | 42991.0273 | 21495.5137 | 85982.0546 | Not At-Risk | SDAC
CA3700962 | OAKVALE PARK | 100 | 70 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | Yes | 0 | Yes | 0 | 0 | No | 56663.64 | 59013.108 | 29506.554 | 118026.216 | At-Risk | Non-DAC
CA5610008 | PLEASANT VALLEY MUTUAL WATER CO | 5000 | 1630 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 616419.5997 | Yes | 0 | 0 | No | 2743349.4 | 3359768.9997 | 1679884.4998 | 6719537.9993 | Not At-Risk | Non-DAC
CA0510017 | CCWD - COPPER COVE | 4416 | 2664 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA3900558 | RANCHO SAN JOAQUIN WATER SYS | 141 | 52 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 45516.3709 | Yes | 0 | 0 | No | 95695.8 | 141212.1709 | 70606.0854 | 282424.3417 | At-Risk | SDAC
CA1009120 | RAU DAIRY | 105 | 43 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 42353.3348 | No | 2016324.9616 | 0 | No | 84388.2 | 2143066.4963 | 1071533.2482 | 4286132.9927 | At-Risk | DAC
CA4400528 | LAUREL COMMUNITY LEAGUE | 64 | 23 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | Non-DAC
CA5410024 | RICHGROVE COMMUNITY SERVICES DISTRICT | 1617 | 524 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 175200.8501 | Yes | 0 | 0 | Yes | 0 | 175200.8501 | 87600.425 | 350401.7002 | HR2W | SDAC
CA0707601 | RUSSOS MOBILE PARK | 110 | 20 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 55019.1155 | No | 2500778.7591 | 0 | No | 72138.3 | 2630250.0445 | 1315125.0223 | 5260500.0891 | Not At-Risk | SDAC
CA1502383 | NORD ROAD WATER ASSOCIATION | 32 | 16 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 35939.4005 | N/A | 0 | 0 | No | 50465.4 | 88184.7005 | 44092.3503 | 176369.401 | At-Risk | Non-DAC
CA1710013 | CALLAYOMI COUNTY WATER DISTRICT | 1481 | 449 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 163251.6027 | Yes | 0 | 0 | Yes | 0 | 163251.6027 | 81625.8013 | 326503.2053 | Not At-Risk | SDAC
CA1400511 | MEADOW LAKE APARTMENTS | 22 | 16 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 35060.7794 | No | 2009152.0648 | 0 | No | 50465.4 | 2094678.2441 | 1047339.1221 | 4189356.4883 | At-Risk | Non-DAC
CA5200502 | LAS FLORES WATER WORKS | 191 | 63 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 49909.4765 | No | 2023757.1197 | 0 | Yes | 0 | 2075446.4962 | 1037723.2481 | 4150892.9924 | Not At-Risk | SDAC
CA1500424 | LANDS OF PROMISE MWC | 174 | 63 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 48415.8206 | Yes | 0 | 0 | Yes | 0 | 48415.8206 | 24207.9103 | 96831.6412 | HR2W | Missing
CA1009111 | SCE/BIG CREEK POWERHOUSE #1 | 126 | 76 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA | N/A | 0 | No | 44198.4392 | N/A | 0 | 0 | No | 125849.4 | 170047.8392 | 85023.9196 | 340095.6783 | Potentially At-Risk | Non-DAC
CA1400036 | KEELER COMMUNITY SERVICE DISTRICT | 66 | 83 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 38926.7124 | No | 2012954.5643 | 0 | No | 133387.8 | 2185269.0766 | 1092634.5383 | 4370538.1533 | HR2W | SDAC
CA1200707 | MIRANDA C.S.D. | 600 | 149 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | SDAC
CA4200918 | LOS PRIETOS COMPLEX | 845 | 39 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 138048.8125 | Yes | 0 | 0 | No | 103171.38 | 243534.0625 | 121767.0313 | 487068.125 | At-Risk | DAC
CA3100014 | BAKER RANCH WATER CORP | 150 | 31 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 46307.1299 | Yes | 0 | 0 | Yes | 0 | 46307.1299 | 23153.5649 | 92614.2598 | At-Risk | SDAC
CA3600397 | MOSS MOBILE MANOR | 290 | 43 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 75352.9188 | No | 2520067.802 | 0 | No | 109704.66 | 2707439.2509 | 1353719.6254 | 5414878.5017 | At-Risk | SDAC
CA4700630 | SHASTA VIEW HEIGHTS OWNERS ASSOCIATION | 50 | 24 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37520.9186 | Yes | 0 | 0 | Yes | 0 | 39300.8186 | 19650.4093 | 78601.6371 | Not At-Risk | DAC
CA3701793 | TWIN LAKES RESORT | 200 | 145 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | SDAC
CA5310003 | TRINITY CENTER M.W.C. . | 729 | 330 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | No | 97179.2935 | N/A | 0 | 0 | Yes | 0 | 97179.2935 | 48589.6467 | 194358.587 | Potentially At-Risk | DAC
CA2810014 | SPANISH FLAT WATER DISTRICT | 230 | 97 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 68574.9844 | N/A | 0 | 0 | Yes | 0 | 68574.9844 | 34287.4922 | 137149.9687 | Potentially At-Risk | DAC
CA0400042 | FOREST VILLAGE LLC | 34 | 21 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2010189.1101 | 0 | No | 56747.4 | 2068716.4101 | 1034358.205 | 4137432.8201 | Not At-Risk | Missing
CA2600733 | COLD WATER CANYON MWC | 90 | 45 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 41035.4031 | Yes | 0 | 0 | No | 86901 | 129716.3031 | 64858.1515 | 259432.6062 | Not At-Risk | Missing
CA4000507 | GARDEN FARMS C.W.D. | 240 | 107 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 69704.6401 | Yes | 0 | 0 | Yes | 0 | 72018.5101 | 36009.2551 | 144037.0202 | Not At-Risk | DAC
CA5200548 | LASSEN VIEW WATER DISTRICT | 85 | 30 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 40596.0925 | No | 0 | 976170.45 | Yes | 0 | 1018546.4425 | 509273.2213 | 2037092.8851 | Not At-Risk | SDAC
CA3301937 | MESQUITE MUTUAL WATER CO. | 42 | 16 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 48038.7521 | N/A | 0 | 0 | Yes | 0 | 48038.7521 | 24019.376 | 96077.5041 | Not At-Risk | Non-DAC
CA4300567 | BURCHELL ROAD WATER ASSOCIATION | 132 | 27 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 58356.2745 | Yes | 0 | 0 | Yes | 0 | 60705.7425 | 30352.8713 | 121411.485 | Not At-Risk | Non-DAC
CA4900674 | PINE HILL TERRACE MOBILE HOME PARK | 27 | 23 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | No | 2313.87 | No | 45642.9728 | No | 2491884.367 | 0 | No | 77038.26 | 2616879.4698 | 1308439.7349 | 5233758.9397 | Not At-Risk | Non-DAC
CA3900762 | RIVERSIDE MOBILE HOME PARK | 55 | 58 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 37960.2291 | Yes | 0 | 0 | No | 103234.2 | 142974.3291 | 71487.1646 | 285948.6583 | Not At-Risk | DAC
CA3500581 | RANCHO SAN JOAQUIN MWC | 96 | 30 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | No | 2313.87 | N/A | 0 | No | 2499278.5002 | 0 | Yes | 0 | 2501592.3702 | 1250796.1851 | 5003184.7404 | Potentially At-Risk | Non-DAC
CA3900702 | CORRAL HOLLOW PWS | 98 | 44 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 41738.3 | Yes | 0 | 0 | No | 85644.6 | 127382.9 | 63691.45 | 254765.8 | At-Risk | Non-DAC
CA2310013 | POINT ARENA WATER WORKS | 472 | 234 | DISTRICT 03 - MENDOCINO | C | O - OTHER AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 68055 | 69834.9 | 34917.45 | 139669.8 | Not At-Risk | SDAC
CA3700905 | PINE HILLS MUTUAL WATER COMPANY | 760 | 230 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA5601120 | SISAR MUTUAL WATER CO | 340 | 106 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA5000080 | COUNTRY WESTERN MOBILE HOME PARK | 90 | 55 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 41035.4031 | No | 2015028.6549 | 0 | No | 99465 | 2157308.958 | 1078654.479 | 4314617.916 | At-Risk | SDAC
CA5602132 | WATERS ROAD DOMESTIC USERS GROUP | 25 | 16 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 46089.8867 | N/A | 0 | 0 | Yes | 0 | 46089.8867 | 23044.9434 | 92179.7734 | Not At-Risk | Non-DAC
CA3601015 | IRONWOOD CAMP | 1000 | 74 | LPA66 - SAN BERNARDINO COUNTY | C | T - SUMMER CAMP | No | 2313.87 | No | 155558.4765 | Yes | 0 | 0 | No | 137471.1 | 295343.4465 | 147671.7233 | 590686.893 | HR2W | DAC
CA5000013 | OID #45 | 144 | 51 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 45779.9572 | Yes | 0 | 0 | No | 94439.4 | 141999.2572 | 70999.6286 | 283998.5144 | Not At-Risk | Non-DAC
CA2700787 | VEGA RD WS #01 | 438 | 125 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1910006 | SO. CAL. EDISON CO.-SANTA CATALINA | 4096 | 1886 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA | Yes | 0 | No | 512785.8187 | Yes | 0 | 0 | Yes | 0 | 512785.8187 | 256392.9093 | 1025571.6373 | Not At-Risk | Non-DAC
CA4500054 | BALLS FERRY FISHING RESORT | 204 | 75 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2024880.5854 | 0 | No | 124593 | 2151253.4854 | 1075626.7427 | 4302506.9709 | Not At-Risk | DAC
CA1900868 | RIVERS END TRAILER PARK | 35 | 45 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | Yes | 0 | No | 2524906.0663 | 0 | No | 114709.32 | 2641964.8543 | 1320982.4272 | 5283929.7087 | Potentially At-Risk | Non-DAC
CA2600538 | LOWER ROCK CREEK MUTUAL WATER CO. | 300 | 107 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1610007 | HOME GARDEN CSD | 1750 | 467 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 186886.5111 | Yes | 0 | 0 | No | 617101.8 | 803988.3111 | 401994.1556 | 1607976.6223 | At-Risk | SDAC
CA2700686 | GARLEN COURT WS | 65 | 17 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49935.6646 | No | 2495956.4983 | 0 | Yes | 0 | 2548206.033 | 1274103.0165 | 5096412.0659 | Potentially At-Risk | Non-DAC
CA2701589 | SUNNY ACRES MWS | 45 | 15 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 47676.3531 | No | 2493813.2713 | 0 | Yes | 0 | 2543803.4945 | 1271901.7472 | 5087606.989 | Potentially At-Risk | SDAC
CA2000800 | MARQUEZ RENTAL | 50 | 20 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 37520.9186 | No | 2011571.8372 | 0 | Yes | 0 | 2049092.7557 | 1024546.3779 | 4098185.5115 | At-Risk | SDAC
CA2710007 | GONZALES, CITY OF | 8549 | 1955 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | DAC
CA5410021 | EARLIMART PUD | 8800 | 1545 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 806314.4098 | Yes | 0 | 0 | No | 1942603.8 | 2748918.2098 | 1374459.1049 | 5497836.4195 | HR2W | SDAC
CA3600400 | APPLE VALLEY VILLAGE MHE | 180 | 93 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 62926.7057 | No | 0 | 1939986.3 | No | 191370.66 | 2196597.5357 | 1098298.7678 | 4393195.0713 | Not At-Risk | SDAC
CA3600297 | GORDON ACRES WATER CO | 200 | 66 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 65186.0171 | Yes | 0 | 0 | No | 49271.82 | 116771.7071 | 58385.8536 | 233543.4143 | HR2W | SDAC
CA5602117 | STRICKLAND ACRES | 429 | 128 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 92404.0986 | Yes | 0 | 0 | Yes | 0 | 92404.0986 | 46202.0493 | 184808.1972 | At-Risk | SDAC
CA1910158 | STERLING MUTUAL WATER COMPANY | 548 | 201 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 106046.156 | Yes | 0 | 0 | No | 373427.208 | 479473.364 | 239736.682 | 958946.7281 | Potentially At-Risk | Non-DAC
CA4300542 | SAN MARTIN COUNTY WATER DISTRICT | 618 | 185 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 114070.8957 | No | 2588187.2631 | 0 | No | 43396.056 | 2745654.2149 | 1372827.1074 | 5491308.4297 | Not At-Risk | Non-DAC
CA4200579 | ROSARIO PARK | 38 | 19 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2493063.1419 | 0 | No | 70504.98 | 2563568.1219 | 1281784.0609 | 5127136.2438 | Potentially At-Risk | SDAC
CA2700970 | ROYAL SIERRA ESTATES WS | 36 | 19 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | Not At-Risk | SDAC
CA1500296 | FULLER ACRES MUTUAL WATER COMPANY | 545 | 165 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 81012.6646 | Yes | 0 | 0 | No | 237669 | 320461.5646 | 160230.7823 | 640923.1293 | HR2W | SDAC
CA1500344 | SOUTH KERN MUTUAL WATER COMPANY | 32 | 15 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 35939.4005 | No | 0 | 825873.6 | No | 49209 | 912801.9005 | 456400.9503 | 1825603.801 | HR2W | Non-DAC
CA3700071 | HEAVENLY OAKS | 300 | 102 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 2349.468 | 1174.734 | 4698.936 | Not At-Risk | Non-DAC
CA1000407 | GEORGE COX WATER SYSTEM | 40 | 20 | DISTRICT 23 - FRESNO | NP/C | RESIDENTIAL AREA | Yes | 0 | No | 36642.2974 | Yes | 0 | 0 | No | 55491 | 92133.2974 | 46066.6487 | 184266.5949 | Not At-Risk | Non-DAC
CA4200633 | LINGATE MUTUAL WATER COMPANY | 55 | 20 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 0 | 1057208.25 | No | 42738.54 | 1099946.79 | 549973.395 | 2199893.58 | Not At-Risk | Non-DAC
CA3901337 | MORADA ESTATES N PWS #46 | 180 | 129 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 48942.9933 | Yes | 0 | 0 | Yes | 0 | 48942.9933 | 24471.4966 | 97885.9866 | Not At-Risk | Non-DAC
CA1500252 | KERN VALLEY MUTUAL WATER COMPANY | 47 | 47 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37257.3322 | Yes | 0 | 0 | Yes | 0 | 39037.2322 | 19518.6161 | 78074.4644 | HR2W | SDAC
CA5301001 | BUCKTAIL MUTUAL WATER COMPANY | 61 | 42 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 38487.4018 | Yes | 0 | 0 | No | 83131.8 | 123399.1018 | 61699.5509 | 246798.2036 | Not At-Risk | SDAC
CA1502670 | FAIRVIEW WATER COMPANY, LLC | 240 | 72 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 54214.7201 | No | 2027991.7214 | 0 | Yes | 0 | 2082206.4415 | 1041103.2207 | 4164412.883 | At-Risk | DAC
CA4710013 | LAKE SHASTINA C.S.D | 2400 | 1286 | DISTRICT 01 - KLAMATH | C | T - RECREATION AREA | Yes | 0 | No | 243996.8848 | Yes | 0 | 0 | Yes | 0 | 243996.8848 | 121998.4424 | 487993.7696 | Not At-Risk | DAC
CA2701040 | MCCOY RD WS #05 | 72 | 24 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 2313.87 | No | 50726.4236 | No | 2496706.6278 | 0 | Yes | 0 | 2549746.9214 | 1274873.4607 | 5099493.8429 | HR2W | SDAC
CA5400655 | CENTRAL MUTUAL WATER CO | 119 | 41 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 43583.4044 | No | 0 | 1086388.14 | No | 81875.4 | 1213626.8444 | 606813.4222 | 2427253.6888 | At-Risk | SDAC
CA1500578 | LONG CANYON WATER COMPANY CORP. | 122 | 64 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | No | 43846.9907 | Yes | 0 | 0 | No | 96952.2 | 140799.1907 | 70399.5954 | 281598.3814 | Not At-Risk | Missing
CA5403043 | YETTEM WATER SYSTEM | 350 | 66 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 63879.5525 | Yes | 0 | 0 | No | 113285.4 | 178944.8525 | 89472.4263 | 357889.7051 | At-Risk | SDAC
CA5500086 | SONORA ESTATES MOBILE HOME PARK | 231 | 87 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK | Yes | 0 | No | 53423.9611 | Yes | 0 | 0 | Yes | 0 | 53423.9611 | 26711.9805 | 106847.9221 | Potentially At-Risk | SDAC
CA1206002 | PALOMINO ESTATES WATER COMPANY | 64 | 19 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | No | 38750.9881 | N/A | 0 | 0 | No | 54234.6 | 92985.5881 | 46492.7941 | 185971.1763 | Not At-Risk | SDAC
CA3900504 | CLEMENTS WATER WORKS #43 | 120 | 79 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA1500442 | SUNSET APARTMENTS WS | 37 | 20 | DISTRICT 19 - TEHACHAPI | C | R - OTHER RESIDENTIAL AREA | Yes | 0 | No | 36378.7111 | No | 2010448.3714 | 0 | No | 55491 | 2102318.0825 | 1051159.0412 | 4204636.165 | HR2W | Missing
CA3400156 | SOUTHWEST TRACT W M D [SWS] | 150 | 33 | LPA64 - SACRAMENTO COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 43396.056 | 43396.056 | 21698.028 | 86792.112 | Not At-Risk | SDAC
CA4200678 | SANTA ANITA MUTUAL WATER COMPANY | 38 | 19 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 46885.5941 | Yes | 0 | 0 | Yes | 0 | 46885.5941 | 23442.7971 | 93771.1882 | Not At-Risk | Non-DAC
CA3900523 | MORADA MANOR WATER SYSTEM | 109 | 34 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 42704.7832 | No | 2016670.6433 | 0 | No | 73080.6 | 2132456.0266 | 1066228.0133 | 4264912.0531 | At-Risk | Non-DAC
CA4400585 | RIDGEVIEW ESTATES MWC | 45 | 18 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | Yes | 0 | No | 0 | 1033022.55 | Yes | 0 | 1035336.42 | 517668.21 | 2070672.84 | Potentially At-Risk | Non-DAC
CA4400557 | ST FRANCIS TRACT WATER SYSTEM | 118 | 29 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 55922.8401 | No | 2501636.0499 | 0 | No | 86838.18 | 2646710.9399 | 1323355.47 | 5293421.8799 | Potentially At-Risk | SDAC
CA2800593 | R RANCH AT THE LAKE | 28 | 16 | LPA58 - NAPA COUNTY | C | T - RECREATION AREA | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 65605.02 | 67918.89 | 33959.445 | 135837.78 | Not At-Risk | Non-DAC
CA1502164 | LLANAS CAMP FOUR WATER SYSTEM | 54 | 55 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 37872.367 | No | 0 | 1226665.2 | No | 99465 | 1365782.467 | 682891.2335 | 2731564.934 | HR2W | SDAC
CA1200687 | RIVERBEND MOBILE HOME PARK | 60 | 28 | DISTRICT 01 - KLAMATH | C | T - OTHER TRANSIENT AREA | No | 1779.9 | No | 38399.5397 | No | 2012436.0416 | 0 | No | 65542.2 | 2118157.6813 | 1059078.8406 | 4236315.3626 | At-Risk | SDAC
CA2400128 | COUNTRY CLUB COUNTY WD | 64 | 23 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 38750.9881 | Yes | 0 | 0 | No | 59260.2 | 98011.1882 | 49005.5941 | 196022.3763 | Not At-Risk | Non-DAC
CA3000519 | HYNES ESTATES MUTUAL WATER CO. | 139 | 42 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 58295.1171 | Yes | 0 | 0 | No | 108071.34 | 168680.3271 | 84340.1636 | 337360.6542 | Not At-Risk | SDAC
CA3200510 | IVCSD CRESCENT MILLS | 258 | 78 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 55796.2381 | Yes | 0 | 0 | Yes | 0 | 57576.1381 | 28788.0691 | 115152.2763 | Not At-Risk | SDAC
CA0610001 | ARBUCKLE PUBLIC UTILITY DISTRICT | 2778 | 1024 | DISTRICT 21 - VALLEY | C | O - OTHER AREA | Yes | 0 | No | 277208.7636 | Yes | 0 | 0 | No | 1286763 | 1563971.7636 | 781985.8818 | 3127943.5272 | Not At-Risk | Non-DAC
CA1500413 | TEJON RANCH MAIN HEADQUARTERS | 132 | 33 | DISTRICT 19 - TEHACHAPI | C | T - OTHER TRANSIENT AREA | Yes | 0 | No | 44725.6119 | No | 2018658.3135 | 0 | No | 54234.6 | 2117618.5254 | 1058809.2627 | 4235237.0508 | At-Risk | Missing
CA1503270 | LAKE ISABELLA COMMUNITY SERVICES DIST | 500 | 129 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA1700595 | CAL 20 VILLAGE AND MEADOW POINTE PARK | 175 | 93 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 32875.8 | 34655.7 | 17327.85 | 69311.4 | HR2W | SDAC
CA5301101 | TREASURE CREEK WOODS MWC | 131 | 32 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 70567.8 | 70567.8 | 35283.9 | 141135.6 | Not At-Risk | DAC
CA3600301 | STRAWBERRY LODGE MWC | 640 | 137 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 114890.8698 | Yes | 0 | 0 | No | 259970.1 | 377174.8398 | 188587.4199 | 754349.6796 | Not At-Risk | DAC
CA0707575 | FRANKS MARINA | 185 | 66 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 63491.5335 | No | 2508815.8603 | 0 | No | 147271.02 | 2721892.2838 | 1360946.1419 | 5443784.5677 | Not At-Risk | SDAC
CA3110019 | SQUAW VALLEY MWC | 500 | 271 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 77058.8695 | Yes | 0 | 0 | Yes | 0 | 77058.8695 | 38529.4348 | 154117.7391 | Not At-Risk | Non-DAC
CA5410036 | LSID-STRATHMORE SYSTEM | 500 | 161 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 77058.8695 | N/A | 0 | 0 | Yes | 0 | 77058.8695 | 38529.4348 | 154117.7391 | Not At-Risk | SDAC
CA0800603 | BUTTE COURT MOBILE HOME PARK | 67 | 23 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK | No | 1779.9 | No | 39014.5745 | No | 2013040.9847 | 0 | No | 59260.2 | 2113095.6592 | 1056547.8296 | 4226191.3184 | Not At-Risk | SDAC
CA1910159 | TRACT 180 MUTUAL WATER CO. | 14000 | 1184 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA | Yes | 0 | No | 1648171.8442 | Yes | 0 | 0 | Yes | 0 | 1648171.8442 | 824085.9221 | 3296343.6884 | At-Risk | SDAC
CA3200150 | HAMILTON BRANCH MWC | 250 | 113 | LPA62 - PLUMAS COUNTY | C | RESIDENTIAL AREA | Yes | 0 | No | 55093.3412 | Yes | 0 | 0 | No | 60516.6 | 115609.9412 | 57804.9706 | 231219.8824 | Not At-Risk | DAC
CA0900308 | QUINTETTE SERVICE CORP WATER | 79 | 52 | LPA39 - EL DORADO COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 51517.1827 | N/A | 0 | 0 | No | 44371.86 | 95889.0427 | 47944.5213 | 191778.0853 | Not At-Risk | SDAC
CA0510019 | CCWD - WALLACE | 340 | 110 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | DAC
CA1800529 | SUSAN HILLS ESTATES WC | 316 | 98 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 60892.2407 | Yes | 0 | 0 | Yes | 0 | 62672.1407 | 31336.0703 | 125344.2814 | Not At-Risk | Non-DAC
CA2610005 | LEE VINING PUBLIC UTILITY | 672 | 68 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | Yes | 0 | 0 | No | 115798.2 | 115798.2 | 57899.1 | 231596.4 | Not At-Risk | Missing
CA2300837 | YOKAYO TRIBE OF INDIANS | 75 | 23 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 39717.4714 | No | 2013732.3483 | 0 | Yes | 0 | 2055229.7196 | 1027614.8598 | 4110459.4393 | Not At-Risk | Non-DAC
CA2800531 | MOORE'S RESORT | 70 | 20 | LPA58 - NAPA COUNTY | C | R - OTHER RESIDENTIAL AREA | No | 2313.87 | No | 50500.4925 | No | 0 | 1057208.25 | Yes | 0 | 1110022.6125 | 555011.3062 | 2220045.225 | At-Risk | Non-DAC
CA4000501 | HALCYON WATER SYSTEM | 105 | 46 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 54454.2876 | No | 0 | 1371622.35 | No | 114604.62 | 1542995.1276 | 771497.5638 | 3085990.2552 | At-Risk | DAC
CA4000523 | S & T MUTUAL WATER COMPANY | 591 | 179 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 109355.5567 | Yes | 0 | 0 | Yes | 0 | 109355.5567 | 54677.7783 | 218711.1133 | At-Risk | Non-DAC
CA4900943 | ALLIANCE REDWOODS CONFERENCE GROUNDS | 418 | 73 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 89812.5123 | Yes | 0 | 0 | No | 158704.26 | 250830.6423 | 125415.3212 | 501661.2846 | Not At-Risk | DAC
CA5400504 | PORTERVILLE MOBILE VILLAGE | 154 | 62 | DISTRICT 24 - TULARE | C | R - MOBILE HOME PARK | Yes | 0 | No | 46658.5783 | No | 2020559.5633 | 0 | No | 108259.8 | 2175477.9416 | 1087738.9708 | 4350955.8832 | Not At-Risk | SDAC
CA5400805 | SOULTS MUTUAL WATER CO | 120 | 36 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 75593.4 | 75593.4 | 37796.7 | 151186.8 | Potentially At-Risk | SDAC
CA4610001 | CITY OF LOYALTON | 856 | 360 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 108337.7819 | Yes | 0 | 0 | No | 475128.6 | 583466.3819 | 291733.1909 | 1166932.7637 | At-Risk | SDAC
CA2810009 | BERRYESSA PINES WATER SYSTEM | 261 | 78 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 72076.9172 | N/A | 0 | 0 | Yes | 0 | 72076.9172 | 36038.4586 | 144153.8343 | At-Risk | DAC
CA5200546 | ANTELOPE-HOMEWOOD MHP | 140 | 24 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 45428.5088 | No | 2019349.6771 | 0 | Yes | 0 | 2066558.0858 | 1033279.0429 | 4133116.1717 | At-Risk | SDAC
CA0707574 | SANTIAGO ISLAND VILLAGE | 400 | 211 | DISTRICT 04 - SAN FRANCISCO | C | R - MOBILE HOME PARK | No | 2313.87 | No | 87779.132 | No | 0 | 3366942.6 | No | 384102.42 | 3841138.022 | 1920569.011 | 7682276.044 | At-Risk | SDAC
CA5400881 | SUNRISE MUTUAL WATER CO. | 80 | 39 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 40156.782 | Yes | 0 | 0 | No | 79362.6 | 121299.282 | 60649.641 | 242598.5639 | Not At-Risk | SDAC
CA2000729 | MADERA CO SA16 SUMNER HILL-WATER SYSTEM | 135 | 41 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | N/A | 0 | No | 44989.1982 | N/A | 0 | 0 | Yes | 0 | 44989.1982 | 22494.5991 | 89978.3964 | HR2W | Non-DAC
CA0600013 | COLUSA CO. WWD #2 - PRINCETON | 382 | 120 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 66691.1402 | Yes | 0 | 0 | No | 181131 | 249602.0402 | 124801.0201 | 499204.0803 | Not At-Risk | DAC
CA1000247 | SHERWOOD FOREST MHP | 75 | 48 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK | Yes | 0 | No | 39717.4714 | No | 2013732.3483 | 0 | No | 90670.2 | 2144120.0196 | 1072060.0098 | 4288240.0393 | At-Risk | DAC
CA1000238 | CAMDEN TRAILER PARK | 75 | 26 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2013732.3483 | 0 | No | 63029.4 | 2078541.6483 | 1039270.8241 | 4157083.2965 | At-Risk | SDAC
CA4010005 | OCEANO COMM SERVICES DIST. | 7487 | 2203 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | No | 888366.1565 | Yes | 0 | 0 | Yes | 0 | 888366.1565 | 444183.0782 | 1776732.313 | Not At-Risk | Non-DAC
CA3200148 | FEATHER RIVER RV & MHP | 700 | 21 | LPA62 - PLUMAS COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 94631.2922 | Yes | 0 | 0 | No | 56747.4 | 153158.5922 | 76579.2961 | 306317.1844 | Not At-Risk | DAC
CA3900505 | FARMINGTON WATER COMPANY | 270 | 78 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 56850.5835 | Yes | 0 | 0 | Yes | 0 | 58630.4835 | 29315.2417 | 117260.967 | Not At-Risk | Non-DAC
CA4400763 | BUENA VISTA MIGRANT CENTER | 455 | 140 | LPA74 - SANTA CRUZ COUNTY | C | NT - INDUSTRIAL/AGRICULTURAL | No | 2313.87 | No | 93992.2386 | No | 2537749.4247 | 0 | Yes | 0 | 2634055.5333 | 1317027.7667 | 5268111.0666 | At-Risk | DAC
CA0707603 | CLAYTON PALMS WATER | 287 | 198 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA5602111 | NYELAND ACRES MUTUAL WATER CO | 915 | 183 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2620424.854 | 0 | Yes | 0 | 2620424.854 | 1310212.427 | 5240849.7079 | Not At-Risk | Non-DAC
CA2701553 | POND-DEROSA OAKS WC | 216 | 75 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 66993.4663 | No | 2512137.8621 | 0 | No | 42738.54 | 2624183.7385 | 1312091.8692 | 5248367.477 | Not At-Risk | Non-DAC
CA5710005 | CITY OF WINTERS | 7417 | 2221 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 684801.1071 | Yes | 0 | 0 | Yes | 0 | 684801.1071 | 342400.5536 | 1369602.2142 | Not At-Risk | Non-DAC
CA0610003 | MAXWELL PUBLIC UTILITY DISTRICT | 1175 | 393 | DISTRICT 21 - VALLEY | C | O - OTHER AREA | Yes | 0 | No | 136365.796 | Yes | 0 | 0 | No | 524128.2 | 660493.996 | 330246.998 | 1320987.992 | Not At-Risk | DAC
CA3500825 | UNION HEIGHTS MWC | 98 | 29 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 53663.5286 | Yes | 0 | 0 | Yes | 0 | 53663.5286 | 26831.7643 | 107327.0571 | Not At-Risk | Non-DAC
CA1400059 | BROOKSIDE MOBILE HOME PARK | 126 | 45 | DISTRICT 13 - SAN BERNARDINO | C | R - MOBILE HOME PARK | No | 1779.9 | No | 44198.4392 | Yes | 0 | 0 | No | 86901 | 132879.3392 | 66439.6696 | 265758.6783 | Not At-Risk | Non-DAC
CA1200538 | MYERS FLAT M.W.S. INC. | 400 | 101 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 68272.6582 | Yes | 0 | 0 | Yes | 0 | 70052.5582 | 35026.2791 | 140105.1164 | Potentially At-Risk | SDAC
CA2210921 | WHISPERING PINES APARTMENTS | 74 | 28 | DISTRICT 11 - MERCED | C | R - OTHER RESIDENTIAL AREA | No | 1779.9 | No | 39629.6093 | Yes | 0 | 0 | No | 65542.2 | 106951.7093 | 53475.8546 | 213903.4186 | Potentially At-Risk | SDAC
CA0707597 | SANDY POINT MOBILE HOME PARK | 67 | 24 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 50161.5958 | No | 2496170.821 | 0 | No | 78671.58 | 2627317.8668 | 1313658.9334 | 5254635.7336 | Potentially At-Risk | Non-DAC
CA4910022 | CANON MANOR WATER SYSTEM | 795 | 241 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | Non-DAC
CA4400754 | MONTE VISTA CHRISTIAN SCHOOL | 1083 | 43 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 164934.6192 | Yes | 0 | 0 | No | 109704.66 | 276953.1492 | 138476.5746 | 553906.2984 | Not At-Risk | Missing
CA1800524 | LASSEN MOBILE HOME PARK | 62 | 30 | DISTRICT 02 - LASSEN | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | No | 2012608.8825 | 0 | No | 68055 | 2082443.7825 | 1041221.8912 | 4164887.565 | Not At-Risk | DAC
CA5400647 | YOKOHL MUTUAL WATER CO | 95 | 32 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 41474.7137 | Yes | 0 | 0 | No | 70567.8 | 113822.4137 | 56911.2068 | 227644.8273 | At-Risk | Non-DAC
CA3610021 | FALLSVALE SERVICE COMPANY | 995 | 492 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA | Yes | 0 | No | 154993.6486 | Yes | 0 | 0 | No | 843065.34 | 998058.9886 | 499029.4943 | 1996117.9773 | Not At-Risk | DAC
CA1910246 | LAND PROJECTS MUTUAL WATER CO. | 1500 | 544 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA | Yes | 0 | No | 215182.6157 | Yes | 0 | 0 | Yes | 0 | 215182.6157 | 107591.3078 | 430365.2314 | HR2W | Non-DAC
CA0706005 | FARRAR PARK PROPERTY OWNERS | 140 | 70 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 58408.0827 | No | 0 | 1661850.75 | No | 153804.3 | 1874063.1327 | 937031.5663 | 3748126.2654 | Not At-Risk | SDAC
CA1500544 | ENOS LANE PUBLIC UTILITY DISTRICT | 365 | 89 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 65197.4842 | Yes | 0 | 0 | No | 140926.2 | 207903.5842 | 103951.7921 | 415807.1685 | At-Risk | DAC
CA1500455 | WILLIAM FISHER MEMORIAL WATER COMPANY | 56 | 16 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 38048.0912 | No | 2012090.3598 | 0 | No | 50465.4 | 2102383.7511 | 1051191.8755 | 4204767.5021 | HR2W | SDAC
CA3400172 | TOKAY PARK WATER CO | 525 | 198 | LPA64 - SACRAMENTO COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 103409.4559 | No | 2578092.664 | 0 | No | 365134.968 | 3048986.5558 | 1524493.2779 | 6097973.1117 | Not At-Risk | SDAC
CA4200885 | CHALK HILL ESTATES HOA | 38 | 15 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 46885.5941 | Yes | 0 | 0 | No | 63971.7 | 110857.2941 | 55428.6471 | 221714.5882 | Not At-Risk | Missing
CA5200657 | NORCAL WATER WORKS | 45 | 17 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | No | 37081.608 | No | 2011139.735 | 0 | Yes | 0 | 2050001.2429 | 1025000.6215 | 4100002.4859 | At-Risk | SDAC
CA5301201 | SEYMOUR'S MUTUAL WATER SYSTEM | 29 | 27 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | N/A | 0 | No | 35675.8142 | N/A | 0 | 0 | No | 64285.8 | 99961.6142 | 49980.8071 | 199923.2284 | Not At-Risk | SDAC
CA3700291 | OCOTILLO OASIS, LLC | 100 | 55 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 54687.8221 | Yes | 0 | 0 | Yes | 0 | 57037.2901 | 28518.645 | 114074.5802 | At-Risk | SDAC
CA0500091 | RITE OF PASSAGE/SIERRA RIDGE | 150 | 13 | LPA35 - CALAVERAS COUNTY | C | NT - SCHOOL | No | 1779.9 | N/A | 0 | Yes | 0 | 0 | No | 46696.2 | 48476.1 | 24238.05 | 96952.2 | Not At-Risk | SDAC
CA2700662 | MURPHY HILL WS #01 | 65 | 29 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | N/A | 0 | No | 49935.6646 | N/A | 0 | 0 | Yes | 0 | 49935.6646 | 24967.8323 | 99871.3292 | Not At-Risk | Non-DAC
CA4500102 | NORTH REDDING RV VILLAGE | 78 | 100 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 156003 | 157782.9 | 78891.45 | 315565.8 | Not At-Risk | SDAC
CA3910009 | SAN JOAQUIN COUNTY - THORNTON | 1033 | 292 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | Yes | 0 | No | 123889.3759 | Yes | 0 | 0 | Yes | 0 | 123889.3759 | 61944.688 | 247778.7518 | At-Risk | SDAC
CA3901216 | SANTOS RANCH PWS #5-CSA #35 | 250 | 97 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | No | 55093.3412 | Yes | 0 | 0 | No | 150977.4 | 206070.7412 | 103035.3706 | 412141.4824 | Not At-Risk | Non-DAC
CA5200535 | LIVE OAK ACRES MWC INC. | 80 | 40 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 40156.782 | No | 0 | 1076368.35 | No | 80619 | 1198924.032 | 599462.016 | 2397848.0639 | Potentially At-Risk | SDAC
CA4100503 | BUTANO CANYON MUTUAL | 150 | 94 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | N/A | 0 | No | 60419.779 | N/A | 0 | 0 | Yes | 0 | 60419.779 | 30209.8895 | 120839.558 | Not At-Risk | Non-DAC
CA2700606 | HIDDEN VIEWS MHP WS | 75 | 31 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 51065.3204 | Yes | 0 | 0 | Yes | 0 | 53379.1904 | 26689.5952 | 106758.3807 | Not At-Risk | DAC
CA4900720 | MOBILE HOME ESTATES | 210 | 150 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK | No | 2313.87 | No | 66315.6729 | No | 0 | 2629278.75 | No | 284469.9 | 2982378.1929 | 1491189.0964 | 5964756.3858 | HR2W | Missing
CA5400728 | GRIER MUTUAL WATER COMPANY | 94 | 99 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 154746.6 | 156526.5 | 78263.25 | 313053 | Not At-Risk | SDAC
CA0510003 | ANGELS, CITY OF | 3836 | 1887 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | DAC
CA4900620 | AUSTIN ACRES MUTUAL WATER COMPANY | 67 | 24 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 2496170.821 | 0 | No | 78671.58 | 2574842.401 | 1287421.2005 | 5149684.8021 | Potentially At-Risk | DAC
CA2010800 | CENTRAL CA WOMENS FACILITY | 2374 | 656 | DISTRICT 11 - MERCED | C | NT - INSTITUTION | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 854561.4 | 854561.4 | 427280.7 | 1709122.8 | At-Risk | Non-DAC
CA3910803 | CDCR CALIFORNIA HEALTH CARE FACILITY | 8455 | 81 | DISTRICT 10 - STOCKTON | C | NT - INSTITUTION | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 132131.4 | 132131.4 | 66065.7 | 264262.8 | Not At-Risk | Missing
CA0800700 | LAS PALMAS MOBILE HOME PARK | 120 | 60 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK | No | 1779.9 | No | 43671.2665 | Yes | 0 | 0 | No | 105747 | 151198.1665 | 75599.0832 | 302396.333 | Potentially At-Risk | SDAC
CA3701184 | BUTTERFIELD RANCH | 350 | 75 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK | No | 2349.468 | No | 83347.6067 | No | 2559097.4505 | 0 | Yes | 0 | 2644794.5252 | 1322397.2626 | 5289589.0504 | At-Risk | SDAC
CA5601134 | ELKINS RANCH | 150 | 43 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | No | 101441.736 | 101441.736 | 50720.868 | 202883.472 | Not At-Risk | Non-DAC
CA3701780 | RICHARDSON BEARDSLEY PARK INC. | 28 | 20 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 2349.468 | 1174.734 | 4698.936 | At-Risk | SDAC
CA3600385 | BROOKSIDE MHP | 65 | 19 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | N/A | 0 | No | 0 | 1045115.4 | Yes | 0 | 1047429.27 | 523714.635 | 2094858.54 | Potentially At-Risk | DAC
CA1500231 | VICTORY MUTUAL WATER COMPANY | 849 | 173 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 107722.7471 | Yes | 0 | 0 | No | 247720.2 | 357222.8471 | 178611.4235 | 714445.6942 | HR2W | SDAC
CA5200600 | GURNSEY AVENUE MUTUAL WATER SYSTEM | 25 | 15 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 35324.3657 | No | 2009411.3261 | 0 | No | 49209 | 2095724.5918 | 1047862.2959 | 4191449.1836 | HR2W | Missing
CA0400078 | FOREST KNOLLS MUTUAL WATER CO | 46 | 21 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | Yes | 0 | No | 2011226.1554 | 0 | No | 56747.4 | 2069753.4554 | 1034876.7277 | 4139506.9108 | Not At-Risk | Missing
CA1500324 | WONDER ACRES WATER SYSTEM | 89 | 33 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | N/A | 0 | N/A | 0 | N/A | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Potentially At-Risk | SDAC
CA5410020 | WOODLAKE, CITY OF | 7950 | 1957 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | N/A | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | At-Risk | SDAC
CA4600009 | SIERRA CSA #5, SIERRA BROOKS | 515 | 219 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | Yes | 0 | No | 78376.8012 | Yes | 0 | 0 | Yes | 0 | 78376.8012 | 39188.4006 | 156753.6025 | Not At-Risk | Non-DAC
CA2210906 | MARIPOSA PINES MUTUAL | 284 | 87 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA | Yes | 0 | No | 58080.6531 | Yes | 0 | 0 | No | 139669.8 | 197750.4531 | 98875.2265 | 395500.9061 | Not At-Risk | SDAC
CA4400611 | JARVIS MUTUAL WATER SYSTEM | 125 | 38 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | No | 0 | 1274879.55 | Yes | 0 | 1274879.55 | 637439.775 | 2549759.1 | Not At-Risk | Non-DAC
CA2700624 | LEAFWOOD COMMUNITY WA | 66 | 23 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 50048.6302 | No | 2496063.6597 | 0 | Yes | 0 | 2548426.1599 | 1274213.0799 | 5096852.3198 | At-Risk | Non-DAC
CA1502608 | OWENS PEAK WEST | 79 | 24 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 40068.9198 | No | 2014078.03 | 0 | Yes | 0 | 2055926.8499 | 1027963.4249 | 4111853.6997 | Not At-Risk | Non-DAC
CA3500575 | SPRINGWOOD ESTATES MWC | 50 | 15 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 48241.181 | No | 2494349.0781 | 0 | Yes | 0 | 2544904.1291 | 1272452.0645 | 5089808.2582 | Not At-Risk | Non-DAC
CA4300996 | VALLEY VIEW RANCHES | 45 | 16 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 48382.6695 | No | 2525991.5071 | 0 | No | 66614.328 | 2643337.9726 | 1321668.9863 | 5286675.9452 | At-Risk | Non-DAC
CA0707608 | MARINA MOBILE MANOR | 75 | 24 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 51065.3204 | No | 2497028.1118 | 0 | No | 78671.58 | 2629078.8822 | 1314539.4411 | 5258157.7644 | Not At-Risk | Non-DAC
CA2702328 | VENTANA BIG SUR INN WS | 193 | 26 | LPA57 - MONTEREY COUNTY | C | T - HOTEL/MOTEL | No | 2313.87 | No | 64395.2581 | Yes | 0 | 0 | No | 81938.22 | 148647.3481 | 74323.6741 | 297294.6962 | Not At-Risk | DAC
CA5400718 | WILLIAMS MUTUAL WATER CO | 180 | 50 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA | Yes | 0 | No | 48942.9933 | No | 2022806.4948 | 0 | No | 93183 | 2164932.4881 | 1082466.244 | 4329864.9762 | At-Risk | SDAC
CA0707523 | FLAMINGO MOBILE MANOR | 200 | 62 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 65186.0171 | No | 2510423.2806 | 0 | No | 140737.74 | 2718660.9077 | 1359330.4538 | 5437321.8154 | Not At-Risk | SDAC
CA4510007 | COTTONWOOD COUNTY WATER DIST. | 3316 | 1226 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 324478.5805 | Yes | 0 | 0 | Yes | 0 | 326258.4805 | 163129.2403 | 652516.9611 | Not At-Risk | DAC
CA0103041 | TRAILER HAVEN MOBILE HOME PARK | 459 | 191 | DISTRICT 04 - SAN FRANCISCO | C | R - MOBILE HOME PARK | No | 2313.87 | No | 94444.1009 | Yes | 0 | 0 | No | 351436.02 | 448193.9909 | 224096.9954 | 896387.9817 | Not At-Risk | DAC
CA0400007 | BUTTE CREEK ESTATES MUTUAL WATER CO | 399 | 168 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 68184.7961 | Yes | 0 | 0 | No | 241438.2 | 311402.8961 | 155701.448 | 622805.7922 | Not At-Risk | DAC
CA2701820 | CORDA RD WS | 60 | 19 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49370.8368 | No | 2495420.6916 | 0 | No | 70504.98 | 2617610.3783 | 1308805.1892 | 5235220.7567 | HR2W | SDAC
CA4200612 | MEADOWLARK RANCHES MUTUAL WATER COMPANY | 150 | 45 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | Not At-Risk | SDAC
CA1510052 | NORTH EDWARDS WD | 944 | 217 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA | Yes | 0 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 0 | 0 | 0 | HR2W | SDAC
CA5400602 | EAGLE'S NEST RESORT | 279 | 78 | DISTRICT 24 - TULARE | C | T - RECREATION AREA | No | 1779.9 | No | 57641.3425 | No | 2031362.1187 | 0 | No | 128362.2 | 2219145.5612 | 1109572.7806 | 4438291.1224 | At-Risk | DAC
CA3301011 | STONE CREEK WATER CO. | 134 | 50 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA | No | 2349.468 | No | 58585.5528 | Yes | 0 | 0 | Yes | 0 | 60935.0208 | 30467.5104 | 121870.0416 | Not At-Risk | DAC
CA2510001 | CITY OF ALTURAS | 2537 | 1470 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | Yes | 0 | No | 256033.9943 | Yes | 0 | 0 | Yes | 0 | 256033.9943 | 128016.9971 | 512067.9886 | Not At-Risk | SDAC
CA4200814 | JONATA HOMEOWNERS ASSOCIATION | 45 | 16 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 47676.3531 | No | 2493813.2713 | 0 | Yes | 0 | 2543803.4945 | 1271901.7472 | 5087606.989 | HR2W | Missing
CA2701701 | BRADLEY-LOCKWOOD RD WS | 39 | 16 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 46998.5597 | Yes | 0 | 0 | No | 65605.02 | 114917.4497 | 57458.7248 | 229834.8994 | Not At-Risk | SDAC
CA2701687 | VALLEY OAKS MHP WS | 120 | 46 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK | No | 2313.87 | No | 56148.7712 | No | 2501850.3726 | 0 | No | 114604.62 | 2674917.6338 | 1337458.8169 | 5349835.2676 | Potentially At-Risk | SDAC
CA4600056 | SIERRA CITY WATER WORKS, INC. | 250 | 89 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA | N/A | 0 | No | 55093.3412 | N/A | 0 | 0 | Yes | 0 | 55093.3412 | 27546.6706 | 110186.6824 | Not At-Risk | Non-DAC
CA4000834 | ANZA VINEYARD ESTATES MUTUAL WATER CO | 60 | 16 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA | No | 2313.87 | No | 49370.8368 | Yes | 0 | 0 | No | 65605.02 | 117289.7268 | 58644.8634 | 234579.4535 | Not At-Risk | Missing
CA2500801 | NEWELL COUNTY WATER DISTRICT | 300 | 310 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA | No | 1779.9 | No | 59486.4469 | Yes | 0 | 0 | Yes | 0 | 61266.3469 | 30633.1734 | 122532.6938 | Not At-Risk | SDAC
CA0500091 | RITE OF PASSAGE/SIERRA RIDGE | 150 | 13 | LPA35 - CALAVERAS COUNTY | C | NT - SCHOOL | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 46696.2 | 48476.1 | 24238.05 | 96952.2 | Not At-Risk | SDAC
CA1000186 | HELM SCHOOL | 146 | 11 | DISTRICT 23 - FRESNO | C | NT - SCHOOL | Yes | 0 | No | 44507.2216 | No | 2019868.1997 | 0 | No | 44183.4 | 2108558.8213 | 1054279.4106 | 4217117.6426 | At-Risk | Non-DAC
CA1010339 | CALIFORNIA STATE UNIVERSITY FRESNO | 41000 | 159 | DISTRICT 12 - VISALIA | C | NT - SCHOOL | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 230130.6 | 230130.6 | 115065.3 | 460261.2 | Not At-Risk | SDAC
CA1910022 | CALIF STATE POLYTECHNICAL UNIV - POMONA | 35586 | 148 | DISTRICT 22 - ANGELES | C | NT - SCHOOL | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 190997.928 | 190997.928 | 95498.964 | 381995.856 | Not At-Risk | Non-DAC
CA2810012 | PACIFIC UNION COLLEGE | 2360 | 313 | DISTRICT 03 - MENDOCINO | C | NT - SCHOOL | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 362869.26 | 362869.26 | 181434.63 | 725738.52 | Not At-Risk | Non-DAC
CA2900546 | SIERRA FRIENDS CENTER | 125 | 13 | LPA59 - NEVADA COUNTY | C | NT - SCHOOL | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Potentially At-Risk | DAC
CA4200618 | MIDLAND SCHOOL | 300 | 48 | LPA72 - SANTA BARBARA COUNTY | C | NT - SCHOOL | Yes | 0 | No | 76482.5746 | Yes | 0 | 0 | No | 117871.26 | 194353.8346 | 97176.9173 | 388707.6691 | Not At-Risk | Non-DAC
CA4400755 | MONTEREY BAY ACADEMY | 400 | 78 | LPA74 - SANTA CRUZ COUNTY | C | NT - SCHOOL | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 81938.22 | 84252.09 | 42126.045 | 168504.18 | At-Risk | Non-DAC
CA4900577 | RIO LINDO ADVENTIST ACADEMY | 358 | 54 | DISTRICT 18 - SONOMA | C | NT - SCHOOL | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | No | 127671.18 | 129985.05 | 64992.525 | 259970.1 | Not At-Risk | Missing
CA4910027 | SONOMA STATE UNIVERSITY | 10986 | 93 | DISTRICT 18 - SONOMA | C | NT - SCHOOL | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 145637.7 | 145637.7 | 72818.85 | 291275.4 | Not At-Risk | Non-DAC
CA5710009 | UC - DAVIS | 48828 | 686 | DISTRICT 09 - SACRAMENTO | C | NT - SCHOOL | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 534179.4 | 534179.4 | 267089.7 | 1068358.8 | Not At-Risk | SDAC
CA0105009 | MOUNTAIN HOUSE SCHOOL | 50 | 1 | DISTRICT 04 - SAN FRANCISCO | NTNC | NT - SCHOOL | N/A | 0 | No | 47239.8041 | N/A | 0 | 0 | No | 41105.22 | 88345.0241 | 44172.512 | 176690.0481 | At-Risk | Missing
CA0202501 | DIAMOND VALLEY SCHOOL | 100 | 5 | LPA32 - ALPINE COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 40592.9518 | No | 2015892.8593 | 0 | No | 36645 | 2094910.7112 | 1047455.3556 | 4189821.4223 | Not At-Risk | Missing
CA0400060 | HONCUT ELEMENTARY SCHOOL | 25 | 3 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 34210.9903 | Yes | 0 | 0 | No | 34132.2 | 70123.0903 | 35061.5452 | 140246.1806 | HR2W | Missing
CA0400062 | RICHVALE ELEMENTARY SCHOOL | 63 | 4 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 37444.5175 | No | 2012695.3029 | 0 | Yes | 0 | 2051919.7204 | 1025959.8602 | 4103839.4408 | Not At-Risk | Missing
CA0400063 | MANZANITA ELEMENTARY SCHOOL | 295 | 3 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 57186.0518 | No | 2032744.8458 | 0 | No | 34132.2 | 2125842.9976 | 1062921.4988 | 4251685.9952 | HR2W | Missing
CA0400064 | CONCOW ELEMENTARY SCHOOL | 115 | 11 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 41869.3441 | No | 2017189.166 | 0 | No | 44183.4 | 2105021.8101 | 1052510.9051 | 4210043.6202 | Not At-Risk | Missing
CA0400065 | SPRING VALLEY SCHOOL | 70 | 1 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL | Yes | 0 | Yes | 0 | No | 2013300.246 | 0 | Yes | 0 | 2013300.246 | 1006650.123 | 4026600.4921 | HR2W | Missing
CA0400067 | FEATHER RIVER SCHOOL | 25 | 2 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 34210.9903 | No | 2009411.3261 | 0 | No | 32875.8 | 2078278.0164 | 1039139.0082 | 4156556.0328 | HR2W | Missing
CA0400068 | BERRY CREEK SCHOOL | 95 | 6 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 40167.4877 | No | 2015460.7571 | 0 | No | 37901.4 | 2093529.6448 | 1046764.8224 | 4187059.2897 | Potentially At-Risk | Missing
CA0400073 | NORD COUNTRY SCHOOL | 66 | 5 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 37699.7959 | No | 2012954.5643 | 0 | No | 36645 | 2089079.2602 | 1044539.6301 | 4178158.5204 | Not At-Risk | Missing
CA0400079 | FOREST RANCH CHARTER SCHOOL | 146 | 4 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2019868.1997 | 0 | No | 35388.6 | 2057036.6997 | 1028518.3499 | 4114073.3995 | Not At-Risk | Missing
CA0500085 | TOYON MIDDLE SCHOOL | 200 | 6 | LPA35 - CALAVERAS COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 49102.2339 | Yes | 0 | 0 | No | 37901.4 | 88783.5339 | 44391.7669 | 177567.0677 | Not At-Risk | Missing
CA0706028 | KNIGHTSEN ELEMENTARY SCHOOL | 350 | 4 | LPA37 - CONTRA COSTA COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 80426.004 | No | 2526497.483 | 0 | No | 46005.18 | 2655242.537 | 1327621.2685 | 5310485.074 | Not At-Risk | Missing
CA0706029 | EXCELSIOR MIDDLE SCHOOL | 600 | 2 | LPA37 - CONTRA COSTA COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 108081.1706 | No | 2553287.8205 | 0 | No | 42738.54 | 2706421.401 | 1353210.7005 | 5412842.8021 | Not At-Risk | Missing
CA0707620 | CANYON SCHOOL | 200 | 1 | LPA37 - CONTRA COSTA COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | Yes | 0 | No | 2510423.2806 | 0 | No | 41105.22 | 2553842.3706 | 1276921.1853 | 5107684.7411 | At-Risk | Missing
CA0800647 | REDWOOD MAINT. & OPER. | 421 | 1 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2043633.8217 | 0 | No | 31619.4 | 2077033.1217 | 1038516.5608 | 4154066.2433 | Not At-Risk | Missing
CA0800649 | MARGARET KEATING MAIN. & OPER. | 135 | 1 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2018917.5749 | 0 | No | 31619.4 | 2052316.8749 | 1026158.4374 | 4104633.7497 | Not At-Risk | Missing
CA0900111 | PIONEER ELEMENTARY SCHOOL | 250 | 19 | LPA39 - EL DORADO COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 69363.9373 | Yes | 0 | 0 | No | 70504.98 | 142182.7873 | 71091.3937 | 284365.5747 | Not At-Risk | Missing
CA0900210 | MILLERS HILL SCHOOL | 120 | 7 | LPA39 - EL DORADO COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | Not At-Risk | Missing
CA0900304 | SILVERFORK SCHOOL | 25 | 2 | LPA39 - EL DORADO COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 44474.2874 | No | 2491670.0443 | 0 | No | 41105.22 | 2579563.4217 | 1289781.7109 | 5159126.8435 | Not At-Risk | Missing
CA0900309 | MOUNTAIN CREEK SCHOOL | 125 | 8 | LPA39 - EL DORADO COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 55536.354 | Yes | 0 | 0 | No | 52538.46 | 110388.684 | 55194.342 | 220777.3681 | Potentially At-Risk | Missing
CA0900410 | LATROBE ELEMENTARY SCHOOL | 65 | 5 | LPA39 - EL DORADO COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | Yes | 0 | No | 2495956.4983 | 0 | No | 47638.5 | 2545908.8683 | 1272954.4342 | 5091817.7367 | Not At-Risk | Missing
CA1000104 | CENTERVILLE SCHOOL | 375 | 11 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | No | 1779.9 | No | 63993.4774 | No | 2039658.4813 | 0 | No | 44183.4 | 2149615.2587 | 1074807.6293 | 4299230.5174 | Not At-Risk | Missing
CA1000105 | MADISON ELEMENTARY SCHOOL | 900 | 8 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | No | 1779.9 | No | 108667.2081 | No | 0 | 755735.07 | No | 40414.2 | 906596.3781 | 453298.189 | 1813192.7562 | Not At-Risk | Missing
CA1000111 | PINE RIDGE SCHOOL | 100 | 13 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | No | 1779.9 | No | 40592.9518 | No | 2015892.8593 | 0 | No | 45439.8 | 2103705.5112 | 1051852.7556 | 4207411.0223 | At-Risk | Missing
CA1000180 | ALTA ELEMENTARY SCHOOL | 384 | 1 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | Yes | 0 | No | 64759.3128 | No | 2040436.2652 | 0 | Yes | 0 | 2105195.5781 | 1052597.789 | 4210391.1561 | HR2W | Missing
CA1000181 | ALVINA SCHOOL | 240 | 8 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | Yes | 0 | No | 52505.9467 | No | 2027991.7214 | 0 | No | 40414.2 | 2120911.8681 | 1060455.934 | 4241823.7362 | At-Risk | Missing
CA1000182 | BURREL UNION ELEMENTARY SCHOOL | 178 | 2 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | No | 1779.9 | No | 47230.1918 | No | 2022633.6539 | 0 | No | 32875.8 | 2104519.5457 | 1052259.7729 | 4209039.0915 | Potentially At-Risk | Missing
CA1000184 | DUNLAP K-8 SCHOOL | 408 | 1 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | Yes | 0 | No | 66801.5405 | No | 2042510.3559 | 0 | Yes | 0 | 2109311.8964 | 1054655.9482 | 4218623.7928 | Not At-Risk | Missing
CA1000185 | GREAT WESTERN ELEMENTARY SCHOOL | 411 | 1 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | Yes | 0 | No | 67056.8189 | No | 2042769.6172 | 0 | Yes | 0 | 2109826.4362 | 1054913.2181 | 4219652.8723 | Not At-Risk | Missing
CA1000187 | INDIANOLA SCHOOL | 511 | 10 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2051411.6616 | 0 | No | 42927 | 2096118.5616 | 1048059.2808 | 4192237.1231 | HR2W | Missing
CA1000189 | LATON HIGH SCHOOL | 210 | 2 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | Yes | 0 | No | 49953.1621 | Yes | 0 | 0 | Yes | 0 | 49953.1621 | 24976.581 | 99906.3241 | Not At-Risk | Missing
CA1000190 | LONE STAR SCHOOL | 436 | 6 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | No | 1779.9 | No | 69184.1395 | No | 2044930.1283 | 0 | No | 37901.4 | 2153795.5678 | 1076897.7839 | 4307591.1355 | Potentially At-Risk | Missing
CA1000192 | MONROE SCHOOL | 200 | 3 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | No | 1779.9 | No | 49102.2339 | No | 2024534.9037 | 0 | No | 34132.2 | 2109549.2375 | 1054774.6188 | 4219098.4751 | Not At-Risk | Missing
CA1000193 | NAVELENCIA SCHOOL | 330 | 1 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | Yes | 0 | No | 60164.3005 | No | 2035769.5613 | 0 | Yes | 0 | 2095933.8618 | 1047966.9309 | 4191867.7236 | Not At-Risk | Missing
CA1000194 | PACIFIC UNION ELEMENTARY SCHOOL | 490 | 1 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | No | 1779.9 | No | 73779.1518 | No | 2049596.8322 | 0 | No | 31619.4 | 2156775.284 | 1078387.642 | 4313550.568 | Not At-Risk | Missing
CA1000196 | RIVERVIEW SCHOOL | 469 | 1 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | Yes | 0 | No | 71992.2025 | No | 2047782.0029 | 0 | Yes | 0 | 2119774.2055 | 1059887.1027 | 4239548.4109 | HR2W | Missing
CA1000198 | TERRY SCHOOL | 236 | 25 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | Yes | 0 | No | 52165.5754 | No | 2027646.0396 | 0 | No | 61773 | 2141584.615 | 1070792.3075 | 4283169.2301 | Not At-Risk | Missing
CA1000201 | SUN EMPIRE SCHOOL | 780 | 10 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | Yes | 0 | No | 98456.0696 | No | 2074658.7608 | 0 | Yes | 0 | 2173114.8305 | 1086557.4152 | 4346229.6609 | Potentially At-Risk | Missing
CA1000204 | AMERICAN UNION SCHOOL | 250 | 33 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | No | 1779.9 | No | 53356.8749 | No | 2028855.9258 | 0 | No | 71824.2 | 2155816.9007 | 1077908.4504 | 4311633.8014 | HR2W | Missing
CA1000206 | HOUGHTON-KEARNEY SCHOOL | 310 | 4 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2034041.1524 | 0 | No | 35388.6 | 2071209.6524 | 1035604.8262 | 4142419.3049 | HR2W | Missing
CA1000208 | ROOSEVELT ELEMENTARY SCHOOL | 370 | 12 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2039226.379 | 0 | No | 45439.8 | 2086446.079 | 1043223.0395 | 4172892.1581 | Not At-Risk | Missing
CA1000217 | CENTRAL HIGH SCHOOL WEST | 1127 | 10 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2104646.6547 | 0 | No | 42927 | 2149353.5547 | 1074676.7773 | 4298707.1093 | At-Risk | Missing
CA1000221 | EASTON AUTHORITY JPA | 1000 | 23 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | Yes | 0 | Yes | 0 | Yes | 0 | 0 | No | 59260.2 | 59260.2 | 29630.1 | 118520.4 | Not At-Risk | Missing
CA1000280 | SIERRA HIGH SCHOOL | 690 | 26 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | No | 1779.9 | No | 90797.7158 | Yes | 0 | 0 | No | 63029.4 | 155607.0158 | 77803.5079 | 311214.0316 | Not At-Risk | Missing
CA1000315 | CLAY JOINT ELEMENTARY SCHOOL | 275 | 5 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | No | 1779.9 | No | 55484.1954 | No | 2031016.4369 | 0 | No | 36645 | 2124925.5323 | 1062462.7662 | 4249851.0646 | Potentially At-Risk | Missing
CA1000316 | KINGS CANYON HIGH SCHOOL | 120 | 1 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | Yes | 0 | No | 42294.8082 | No | 2017621.2682 | 0 | Yes | 0 | 2059916.0764 | 1029958.0382 | 4119832.1529 | HR2W | Missing
CA1000367 | SELMA HIGH SCHOOL | 2225 | 21 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | Yes | 0 | No | 221415.195 | Yes | 0 | 0 | No | 56747.4 | 278162.595 | 139081.2975 | 556325.19 | Not At-Risk | Missing
CA1000476 | FOOTHILL ELEMENTARY SCHOOL | 900 | 12 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | No | 1779.9 | No | 108667.2081 | Yes | 0 | 0 | No | 45439.8 | 155886.9081 | 77943.454 | 311773.8162 | Not At-Risk | Missing
CA1000577 | DUNLAP LEADERSHIP ACADEMY | 78 | 1 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL | Yes | 0 | No | 38720.9098 | No | 2013991.6096 | 0 | Yes | 0 | 2052712.5194 | 1026356.2597 | 4105425.0387 | HR2W | Missing
CA1100104 | WILLOW CREEK CHRISTIAN SCHOOL | 47 | 2 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL | No | 1779.9 | No | 36083.0324 | No | 2011312.5758 | 0 | Yes | 0 | 2049175.5082 | 1024587.7541 | 4098351.0164 | Potentially At-Risk | Missing
CA1100440 | LAKE ELEMENTARY SCHOOL | 205 | 1 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL | Yes | 0 | No | 49527.698 | No | 2024967.0059 | 0 | Yes | 0 | 2074494.7039 | 1037247.3519 | 4148989.4077 | Not At-Risk | Missing
CA1100448 | PLAZA ELEMENTARY SCHOOL | 250 | 4 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL | No | 1779.9 | No | 53356.8749 | No | 2028855.9258 | 0 | Yes | 0 | 2083992.7007 | 1041996.3504 | 4167985.4014 | Not At-Risk | Missing
CA1100527 | CAPAY JOINT UNION ELEM. SCHOOL | 230 | 1 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL | No | 1779.9 | No | 51655.0185 | No | 2027127.517 | 0 | Yes | 0 | 2080562.4354 | 1040281.2177 | 4161124.8709 | Not At-Risk | Missing
CA1100749 | RIVER VALLEY CHRISTIAN SCHOOL | 80 | 2 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL | No | 1779.9 | No | 38891.0954 | No | 2014164.4505 | 0 | Yes | 0 | 2054835.4459 | 1027417.7229 | 4109670.8918 | Not At-Risk | Missing
CA1200546 | CASTERLIN SCHOOL | 130 | 1 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL | No | 1779.9 | No | 43145.7364 | No | 2018485.4726 | 0 | No | 31619.4 | 2095030.5091 | 1047515.2545 | 4190061.0182 | Not At-Risk | Missing
CA1200681 | CUDDEBACK GRAMMAR SCHOOL | 165 | 1 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL | No | 1779.9 | No | 46123.9852 | No | 2021510.1882 | 0 | No | 31619.4 | 2101033.4733 | 1050516.7367 | 4202066.9466 | Not At-Risk | Missing
CA1200684 | MATTOLE ELEMENTARY SCHOOL | 100 | 1 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | No | 31619.4 | 33399.3 | 16699.65 | 66798.6 | Not At-Risk | Missing
CA1200778 | BRIDGEVILLE ELEM. SCHOOL | 50 | 1 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL | No | 1779.9 | No | 36338.3108 | No | 2011571.8372 | 0 | Yes | 0 | 2049690.048 | 1024845.024 | 4099380.096 | At-Risk | Missing
CA1200817 | KNEELAND SCHOOL | 32 | 1 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL | N/A | 0 | No | 34806.6401 | No | 2010016.2692 | 0 | Yes | 0 | 2044822.9092 | 1022411.4546 | 4089645.8185 | Not At-Risk | Missing
CA1300553 | MAGNOLIA UNION SCHOOL | 142 | 1 | LPA43 - IMPERIAL COUNTY | NTNC | NT - SCHOOL | N/A | 0 | No | 44166.8503 | N/A | 0 | 0 | No | 31619.4 | 75786.2503 | 37893.1251 | 151572.5006 | Not At-Risk | Missing
CA1300554 | MEADOWS UNION ELEMENTARY SCHOOL | 550 | 6 | LPA43 - IMPERIAL COUNTY | NTNC | NT - SCHOOL | N/A | 0 | No | 78884.721 | N/A | 0 | 0 | No | 37901.4 | 116786.121 | 58393.0605 | 233572.2419 | Not At-Risk | Missing
CA1300556 | MULBERRY UNION SCHOOL | 85 | 2 | LPA43 - IMPERIAL COUNTY | NTNC | NT - SCHOOL | N/A | 0 | No | 39316.5595 | N/A | 0 | 0 | Yes | 0 | 39316.5595 | 19658.2798 | 78633.1191 | Potentially At-Risk | Missing
CA1300560 | PINE UNION SCHOOL | 217 | 1 | LPA43 - IMPERIAL COUNTY | NTNC | NT - SCHOOL | N/A | 0 | No | 50548.8118 | N/A | 0 | 0 | Yes | 0 | 50548.8118 | 25274.4059 | 101097.6236 | Not At-Risk | Missing
CA1300579 | MCCABE UNION SCHOOL | 1350 | 1 | LPA43 - IMPERIAL COUNTY | NTNC | NT - SCHOOL | N/A | 0 | No | 146958.9772 | Yes | 0 | 0 | Yes | 0 | 146958.9772 | 73479.4886 | 293917.9544 | Not At-Risk | Missing
CA1400019 | ROUND VALLEY SCHOOL | 143 | 2 | DISTRICT 13 - SAN BERNARDINO | NTNC | NT - SCHOOL | Yes | 0 | No | 44251.9431 | No | 2019608.9384 | 0 | No | 32875.8 | 2096736.6815 | 1048368.3408 | 4193473.363 | Not At-Risk | Missing
CA1400522 | PALISADE GLACIER HIGH SCHOOL | 244 | 7 | DISTRICT 13 - SAN BERNARDINO | NTNC | NT - SCHOOL | No | 1779.9 | No | 52846.318 | Yes | 0 | 0 | No | 39157.8 | 93784.018 | 46892.009 | 187568.0359 | Not At-Risk | Missing
CA1502068 | DI GIORGIO SCHOOL WATER SYSTEM | 232 | 1 | DISTRICT 19 - TEHACHAPI | NTNC | NT - SCHOOL | No | 1779.9 | No | 51825.2041 | No | 2027300.3579 | 0 | No | 31619.4 | 2112524.862 | 1056262.431 | 4225049.7239 | HR2W | Missing
CA1502074 | EL TEJON MIDDLE SCHOOL | 550 | 1 | DISTRICT 19 - TEHACHAPI | NTNC | NT - SCHOOL | Yes | 0 | No | 78884.721 | No | 2054782.0588 | 0 | Yes | 0 | 2133666.7798 | 1066833.3899 | 4267333.5596 | Not At-Risk | Missing
CA1502154 | LAKESIDE SCHOOL | 800 | 1 | DISTRICT 12 - VISALIA | NTNC | NT - SCHOOL | No | 1779.9 | No | 100157.926 | No | 2076387.1697 | 0 | No | 31619.4 | 2209944.3957 | 1104972.1979 | 4419888.7915 | HR2W | Missing
CA1502221 | POND SCHOOL WATER SYSTEM | 250 | 2 | DISTRICT 12 - VISALIA | NTNC | NT - SCHOOL | No | 1779.9 | No | 53356.8749 | No | 2028855.9258 | 0 | No | 32875.8 | 2116868.5007 | 1058434.2504 | 4233737.0014 | HR2W | Missing
CA1502229 | RIO BRAVO GREELEY SCHOOL WATER SYSTEM | 887 | 16 | DISTRICT 12 - VISALIA | NTNC | NT - SCHOOL | No | 1779.9 | No | 107561.0014 | No | 2083905.7483 | 0 | No | 50465.4 | 2243712.0497 | 1121856.0248 | 4487424.0994 | HR2W | Missing
CA1502231 | ROSAMOND SCHOOL WATER SYSTEM | 940 | 2 | DISTRICT 19 - TEHACHAPI | NTNC | NT - SCHOOL | Yes | 0 | No | 112070.9209 | Yes | 0 | 0 | Yes | 0 | 112070.9209 | 56035.4604 | 224141.8418 | HR2W | Missing
CA1502260 | SOUTH FORK ELEMENTARY SCHOOL WATER SYS | 154 | 2 | DISTRICT 19 - TEHACHAPI | NTNC | NT - SCHOOL | No | 1779.9 | No | 45187.9641 | No | 2020559.5633 | 0 | Yes | 0 | 2067527.4274 | 1033763.7137 | 4135054.8548 | Not At-Risk | Missing
CA1502607 | PIUTE MOUNTAIN SCHOOL WATER | 50 | 5 | DISTRICT 19 - TEHACHAPI | NTNC | NT - SCHOOL | No | 1779.9 | No | 36338.3108 | No | 2011571.8372 | 0 | No | 36645 | 2086335.048 | 1043167.524 | 4172670.096 | HR2W | Missing
CA1503140 | FRAZIER MOUNTAIN HIGH SCHOOL | 500 | 1 | DISTRICT 19 - TEHACHAPI | NTNC | NT - SCHOOL | Yes | 0 | No | 74630.08 | No | 2050461.0367 | 0 | Yes | 0 | 2125091.1166 | 1062545.5583 | 4250182.2333 | HR2W | Missing
CA1503368 | SOUTH FORK MIDDLE SCHOOL | 204 | 1 | DISTRICT 19 - TEHACHAPI | NTNC | NT - SCHOOL | No | 1779.9 | No | 49442.6051 | No | 2024880.5854 | 0 | Yes | 0 | 2076103.0906 | 1038051.5453 | 4152206.1812 | Not At-Risk | Missing
CA1503683 | PEAK TO PEAK MOUNTAIN CHARTER SCHOOL WS | 100 | 3 | DISTRICT 19 - TEHACHAPI | NTNC | NT - SCHOOL | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 34132.2 | 34132.2 | 17066.1 | 68264.4 | At-Risk | Missing
CA1600009 | HANFORD CHRISTIAN SCHOOL | 175 | 14 | LPA46 - KINGS COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 46974.9134 | No | 2022374.3926 | 0 | No | 47952.6 | 2119081.8059 | 1059540.903 | 4238163.6119 | Not At-Risk | Missing
CA1600011 | PIONEER ELEMENTARY SCHOOL | 750 | 6 | LPA46 - KINGS COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 95903.285 | Yes | 0 | 0 | No | 37901.4 | 135584.585 | 67792.2925 | 271169.1701 | At-Risk | Missing
CA1600013 | LAKESIDE ELEMENTARY SCHOOL | 388 | 5 | LPA46 - KINGS COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 65099.6841 | No | 2040781.947 | 0 | No | 36645 | 2144306.5311 | 1072153.2656 | 4288613.0622 | Not At-Risk | Missing
CA1600015 | KINGS RIVER HARDWICK SCHOOL | 908 | 7 | LPA46 - KINGS COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 109347.9506 | No | 2085720.5776 | 0 | No | 39157.8 | 2236006.2282 | 1118003.1141 | 4472012.4564 | Not At-Risk | Missing
CA1600017 | ISLAND UNION SCHOOL | 416 | 17 | LPA46 - KINGS COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 67482.283 | No | 2043201.7194 | 0 | Yes | 0 | 2110684.0025 | 1055342.0012 | 4221368.005 | Not At-Risk | Missing
CA1800573 | RICHMOND ELEMENTARY SCHOOL | 247 | 1 | DISTRICT 02 - LASSEN | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2028596.6645 | 0 | Yes | 0 | 2030376.5645 | 1015188.2823 | 4060753.129 | At-Risk | Missing
CA1800574 | JOHNSTONVILLE ELEMENTARY SCHOOL | 223 | 1 | DISTRICT 02 - LASSEN | NTNC | NT - SCHOOL | No | 1779.9 | No | 51059.3687 | Yes | 0 | 0 | Yes | 0 | 52839.2687 | 26419.6344 | 105678.5375 | Not At-Risk | Missing
CA1800575 | SHAFFER ELEMENTARY SCHOOL | 320 | 1 | DISTRICT 02 - LASSEN | NTNC | NT - SCHOOL | No | 1779.9 | No | 59313.3723 | No | 2034905.3569 | 0 | No | 31619.4 | 2127618.0292 | 1063809.0146 | 4255236.0583 | Not At-Risk | Missing
CA1800576 | LONG VALLEY CHARTER SCHOOL | 150 | 1 | DISTRICT 02 - LASSEN | NTNC | NT - SCHOOL | No | 1779.9 | No | 44847.5928 | No | 2020213.8815 | 0 | No | 31619.4 | 2098460.7744 | 1049230.3872 | 4196921.5487 | Not At-Risk | Missing
CA1800577 | JANESVILLE ELEMENTARY SCHOOL | 425 | 1 | DISTRICT 02 - LASSEN | NTNC | NT - SCHOOL | No | 1779.9 | No | 68248.1184 | No | 2043979.5034 | 0 | Yes | 0 | 2114007.5219 | 1057003.7609 | 4228015.0437 | Not At-Risk | Missing
CA1900707 | ILEAD AGUA DULCE CHARTER SCHOOL | 450 | 6 | LPA49 - LA COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 92895.5794 | No | 2569951.8582 | 0 | No | 50029.848 | 2715226.7536 | 1357613.3768 | 5430453.5073 | Not At-Risk | Missing
CA1900750 | DEL SUR SCHOOL/WESTSIDE UNION DISTRICT | 825 | 1 | LPA49 - LA COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 135016.5255 | No | 2610655.887 | 0 | Yes | 0 | 2748021.8805 | 1374010.9403 | 5496043.761 | Not At-Risk | Missing
CA1900751 | EASTSIDE UNION SCHOOL DISTRICT | 650 | 18 | LPA49 - LA COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 115360.084 | No | 2591660.6736 | 0 | No | 69931.224 | 2779301.4496 | 1389650.7248 | 5558602.8991 | Not At-Risk | Missing
CA1900886 | HUGHES-ELIZABETH LAKE UNIFIED SCHOOL DIS | 550 | 2 | LPA49 - LA COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 104127.8317 | Yes | 0 | 0 | No | 41737.608 | 148214.9077 | 74107.4538 | 296429.8154 | Not At-Risk | Missing
CA2000150 | LIBERTY HIGH SCHOOL | 1340 | 1 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 146108.049 | Yes | 0 | 0 | Yes | 0 | 147887.949 | 73943.9745 | 295775.898 | At-Risk | Missing
CA2000567 | YOSEMITE HIGH SCHOOL | 862 | 32 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 105433.6809 | Yes | 0 | 0 | No | 70567.8 | 177781.3809 | 88890.6905 | 355562.7618 | HR2W | Missing
CA2000597 | DAIRYLAND SCHOOL | 250 | 8 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 53356.8749 | No | 2028855.9258 | 0 | No | 40414.2 | 2124406.9007 | 1062203.4504 | 4248813.8014 | Not At-Risk | Missing
CA2000598 | ALVIEW SCHOOL | 200 | 1 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 49102.2339 | Yes | 0 | 0 | Yes | 0 | 50882.1339 | 25441.0669 | 101764.2677 | Not At-Risk | Missing
CA2000600 | HOWARD ELEMENTARY SCHOOL | 1081 | 7 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 124069.0086 | No | 2100671.3143 | 0 | Yes | 0 | 2226520.2228 | 1113260.1114 | 4453040.4457 | At-Risk | Missing
CA2000601 | LA VINA SCHOOL | 513 | 7 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 75736.2866 | No | 2051584.5024 | 0 | Yes | 0 | 2129100.6891 | 1064550.3445 | 4258201.3781 | Not At-Risk | Missing
CA2000602 | RIPPERDAN COMMUNITY DAY SCHOOL | 113 | 4 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 41699.1585 | No | 2017016.3251 | 0 | Yes | 0 | 2060495.3836 | 1030247.6918 | 4120990.7672 | HR2W | Missing
CA2000607 | SPRING VALLEY SCHOOL | 150 | 10 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 44847.5928 | No | 2020213.8815 | 0 | Yes | 0 | 2066841.3744 | 1033420.6872 | 4133682.7487 | Not At-Risk | Missing
CA2000611 | COARSEGOLD SCHOOL | 441 | 11 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 69609.6036 | Yes | 0 | 0 | Yes | 0 | 71389.5036 | 35694.7518 | 142779.0071 | HR2W | Missing
CA2000612 | NORTH FORK ELEMENTARY SCHOOL | 500 | 18 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 74630.08 | No | 2050461.0367 | 0 | No | 51721.8 | 2178592.8166 | 1089296.4083 | 4357185.6333 | HR2W | Missing
CA2000616 | WASUMA SCHOOL | 354 | 5 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 62206.5282 | No | 2037843.6519 | 0 | No | 36645 | 2138475.0801 | 1069237.5401 | 4276950.1603 | Not At-Risk | Missing
CA2000760 | DIXIELAND ELEMENTARY SCHOOL | 338 | 4 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 60845.0431 | No | 2036460.9249 | 0 | Yes | 0 | 2099085.8679 | 1049542.934 | 4198171.7358 | Not At-Risk | Missing
CA2000844 | RIVERGOLD ELEMENTARY SCHOOL | 485 | 9 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 73353.6877 | No | 2049164.73 | 0 | No | 41670.6 | 2165968.9177 | 1082984.4588 | 4331937.8354 | Not At-Risk | Missing
CA2000846 | SIERRA VIEW SCHOOL | 250 | 23 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 53356.8749 | No | 2028855.9258 | 0 | No | 59260.2 | 2143252.9007 | 1071626.4504 | 4286505.8014 | Potentially At-Risk | Missing
CA2000947 | MINARETS HIGH SCHOOL | 450 | 17 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 70375.4389 | Yes | 0 | 0 | No | 50465.4 | 122620.7389 | 61310.3695 | 245241.4779 | Not At-Risk | Missing
CA2100538 | TOMALES HIGH SCHOOL | 227 | 2 | DISTRICT 25 - MARIN | NTNC | NT - SCHOOL | No | 2313.87 | No | 66819.662 | Yes | 0 | 0 | No | 42738.54 | 111872.072 | 55936.036 | 223744.144 | Not At-Risk | Missing
CA2100560 | TOMALES ELEM & MIDDLE SCHOOL | 265 | 4 | DISTRICT 25 - MARIN | NTNC | NT - SCHOOL | No | 2313.87 | No | 71023.2473 | No | 0 | 863722.65 | No | 46005.18 | 983064.9473 | 491532.4737 | 1966129.8947 | Not At-Risk | Missing
CA2100582 | NICASIO SCHOOL | 40 | 5 | DISTRICT 25 - MARIN | NTNC | NT - SCHOOL | No | 2313.87 | No | 46133.5974 | No | 2493277.4646 | 0 | No | 47638.5 | 2589363.432 | 1294681.716 | 5178726.864 | HR2W | Missing
CA2210907 | MUSD - SIERRA FOOTHILL CHARTER SCHOOL | 157 | 9 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | N/A | 0 | No | 45443.2426 | N/A | 0 | 0 | No | 41670.6 | 87113.8426 | 43556.9213 | 174227.6852 | At-Risk | Missing
CA2210908 | MUSD -COULTERVILLE - GREELEY HILL SCHOOL | 91 | 6 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | Yes | 0 | No | 39827.1164 | No | 2015115.0753 | 0 | No | 31619.4 | 2086561.5918 | 1043280.7959 | 4173123.1836 | Not At-Risk | Missing
CA2210909 | MUSD - MARIPOSA JUNIOR HIGH SCHOOL | 152 | 20 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | Yes | 0 | No | 45017.7785 | Yes | 0 | 0 | No | 55491 | 100508.7785 | 50254.3892 | 201017.557 | Not At-Risk | Missing
CA2210910 | MUSD - WOODLAND ELEMENTARY SCHOOL | 446 | 24 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | Yes | 0 | No | 70035.0677 | Yes | 0 | 0 | No | 60516.6 | 130551.6677 | 65275.8338 | 261103.3353 | Not At-Risk | Missing
CA2300584 | MENDOCINO SCHOOL DISTRICT- MENDOCINO | 768 | 15 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL | No | 1779.9 | No | 97434.9558 | Yes | 0 | 0 | Yes | 0 | 99214.8558 | 49607.4279 | 198429.7116 | Not At-Risk | Missing
CA2300755 | POTTER VALLEY SCHOOL DISTRICT | 309 | 36 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL | Yes | 0 | No | 58377.3513 | No | 2033954.732 | 0 | No | 74337 | 2166669.0833 | 1083334.5416 | 4333338.1665 | Not At-Risk | Missing
CA2300764 | ANDERSON VALLEY HIGH SCHOOL | 300 | 8 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL | No | 1779.9 | No | 57611.5159 | Yes | 0 | 0 | No | 40414.2 | 99805.6159 | 49902.8079 | 199611.2318 | Not At-Risk | Missing
CA2300770 | ANDERSON VALLEY ELEMENTARY SCHOOL | 350 | 11 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL | No | 1779.9 | No | 61866.1569 | No | 2037497.9702 | 0 | No | 44183.4 | 2145327.4271 | 1072663.7135 | 4290654.8542 | Not At-Risk | Missing
CA2300785 | LEGGETT VALLEY SCHOOL | 100 | 5 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL | No | 1779.9 | No | 40592.9518 | Yes | 0 | 0 | Yes | 0 | 42372.8518 | 21186.4259 | 84745.7037 | Potentially At-Risk | Missing
CA2300826 | MANCHESTER UNION ELEMENTARY SCHOOL | 75 | 1 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL | No | 1779.9 | No | 38465.6313 | No | 2013732.3483 | 0 | Yes | 0 | 2053977.8796 | 1026988.9398 | 4107955.7592 | Not At-Risk | Missing
CA2300829 | ROUND VALLEY HIGH SCHOOL | 162 | 1 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2021250.9268 | 0 | Yes | 0 | 2023030.8268 | 1011515.4134 | 4046061.6536 | Not At-Risk | Missing
CA2300830 | ROUND VALLEY ELEMENTARY SCHOOL | 263 | 1 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2029979.3916 | 0 | Yes | 0 | 2031759.2916 | 1015879.6458 | 4063518.5832 | Not At-Risk | Missing
CA2300846 | MENDOCINO SCHOOL DISTRICT-ALBION SCHOOL | 25 | 2 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL | No | 1779.9 | No | 34210.9903 | No | 2009411.3261 | 0 | Yes | 0 | 2045402.2164 | 1022701.1082 | 4090804.4328 | Not At-Risk | Missing
CA2300847 | WHALE GULCH ELEMENTARY SCHOOL | 50 | 1 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL | N/A | 0 | Yes | 0 | N/A | 0 | 0 | No | 31619.4 | 31619.4 | 15809.7 | 63238.8 | Not At-Risk | Missing
CA2300863 | EEL RIVER CHARTER SCHOOL | 73 | 1 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL | No | 1779.9 | No | 32083.6698 | No | 2013559.5074 | 0 | Yes | 0 | 2047423.0772 | 1023711.5386 | 4094846.1543 | Not At-Risk | Missing
CA2300874 | MONTESSORI DEL MAR LEARNING CENTER | 50 | 3 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL | No | 1779.9 | No | 36338.3108 | No | 2011571.8372 | 0 | Yes | 0 | 2049690.048 | 1024845.024 | 4099380.096 | Not At-Risk | Missing
CA2400062 | SNELLING MERCED FALLS SCHOOL | 85 | 4 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | No | 39316.5595 | No | 2014596.5527 | 0 | No | 35388.6 | 2091081.6122 | 1045540.8061 | 4182163.2244 | Not At-Risk | Missing
CA2400064 | MERQUIN ELEMENTARY SCHOOL | 284 | 2 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | No | 56250.0308 | No | 2031794.2209 | 0 | Yes | 0 | 2089824.1517 | 1044912.0758 | 4179648.3034 | Not At-Risk | Missing
CA2400065 | PLAINSBURG ELEMENTARY SCHOOL | 126 | 5 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | No | 42805.3652 | Yes | 0 | 0 | No | 36645 | 81230.2652 | 40615.1326 | 162460.5303 | HR2W | Missing
CA2400066 | PLANADA ELEMENTARYSCHOOL | 567 | 1 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | No | 80331.2989 | No | 2056251.2064 | 0 | Yes | 0 | 2138362.4053 | 1069181.2027 | 4276724.8106 | Not At-Risk | Missing
CA2400071 | WASHINGTON SCHOOL | 230 | 4 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | No | 51655.0185 | No | 2027127.517 | 0 | No | 35388.6 | 2115951.0354 | 1057975.5177 | 4231902.0709 | At-Risk | Missing
CA2400075 | EL NIDO ELEMENTARY SCHOOL | 219 | 2 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | No | 50718.9974 | No | 2026176.8921 | 0 | No | 32875.8 | 2111551.5895 | 1055775.7948 | 4223103.1791 | At-Risk | Missing
CA2400079 | MCSWAIN ELEMENTARY SCHOOL | 950 | 24 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | No | 112921.8491 | Yes | 0 | 0 | No | 60516.6 | 175218.3491 | 87609.1745 | 350436.6982 | HR2W | Missing
CA2400091 | CHARLESTON SCHOOL | 325 | 1 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | No | 59738.8364 | No | 2035337.4591 | 0 | Yes | 0 | 2096856.1955 | 1048428.0977 | 4193712.391 | Potentially At-Risk | Missing
CA2400097 | CRESSEY SCHOOL | 155 | 7 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | No | 45273.0569 | No | 2020645.9837 | 0 | No | 39157.8 | 2106856.7407 | 1053428.3703 | 4213713.4813 | HR2W | Missing
CA2400099 | GRACE MENNONITE SCHOOL | 100 | 1 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | No | 40592.9518 | No | 2015892.8593 | 0 | No | 31619.4 | 2089885.1112 | 1044942.5556 | 4179770.2223 | HR2W | Missing
CA2400113 | SCHELBY SCHOOL | 290 | 9 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | No | 56760.5877 | Yes | 0 | 0 | No | 41670.6 | 100211.0877 | 50105.5438 | 200422.1754 | HR2W | Missing
CA2400122 | LONGVIEW MENNONITE SCHOOL | 120 | 1 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | No | 42294.8082 | No | 2017621.2682 | 0 | Yes | 0 | 2061695.9764 | 1030847.9882 | 4123391.9529 | At-Risk | Missing
CA2400134 | BUHACH PRESCHOOL (KINDERCARE) | 110 | 3 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | No | 41443.88 | No | 2016757.0638 | 0 | No | 34132.2 | 2094113.0438 | 1047056.5219 | 4188226.0876 | Not At-Risk | Missing
CA2400219 | MERCED NEW LIFE SCHOOL | 36 | 2 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | No | 35147.0113 | No | 2010361.951 | 0 | Yes | 0 | 2047288.8623 | 1023644.4311 | 4094577.7246 | Not At-Risk | Missing
CA2600568 | EDNA BEAMAN ELEMENTARY SCHOOL | 26 | 2 | LPA56 - MONO COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2009497.7465 | 0 | No | 31619.4 | 2042897.0465 | 1021448.5233 | 4085794.0931 | At-Risk | Missing
CA2600570 | COLEVILLE HIGH SCHOOL | 216 | 4 | LPA56 - MONO COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 50463.719 | Yes | 0 | 0 | No | 35388.6 | 87632.219 | 43816.1095 | 175264.438 | Potentially At-Risk | Missing
CA2700552 | ECHO VALLEY SCHOOL WS | 579 | 1 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 105758.1366 | No | 2551037.4321 | 0 | No | 41105.22 | 2700214.6587 | 1350107.3294 | 5400429.3174 | At-Risk | Missing
CA2700577 | ELKHORN SCHOOL WS | 694 | 1 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 118479.5132 | No | 2563360.9873 | 0 | No | 41105.22 | 2725259.5906 | 1362629.7953 | 5450519.1811 | At-Risk | Missing
CA2700705 | PRUNEDALE SCHOOL WS | 655 | 1 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 114165.3072 | No | 2559181.6947 | 0 | No | 41105.22 | 2716766.0919 | 1358383.046 | 5433532.1839 | Not At-Risk | Missing
CA2700727 | SAN ANTONIO SCHOOL DISTRICT WS | 300 | 1 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | Yes | 0 | No | 2521139.4155 | 0 | No | 41105.22 | 2564558.5055 | 1282279.2528 | 5129117.0111 | Not At-Risk | Missing
CA2700964 | BRADLEY UNION SCHOOL WS | 100 | 1 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 52770.8374 | No | 2499707.1456 | 0 | Yes | 0 | 2552477.983 | 1276238.9915 | 5104955.9659 | HR2W | Missing
CA2701221 | WASHINGTON SCHOOL WS | 250 | 2 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 69363.9373 | No | 2515781.348 | 0 | No | 42738.54 | 2630197.6954 | 1315098.8477 | 5260395.3908 | HR2W | Missing
CA2702180 | GRAVES SCHOOL WS | 56 | 2 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 47903.5281 | No | 2494992.0462 | 0 | Yes | 0 | 2545209.4442 | 1272604.7221 | 5090418.8885 | Not At-Risk | Missing
CA2702254 | PACIFIC VALLEY SCHOOL WS | 25 | 5 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 44474.2874 | No | 2491670.0443 | 0 | Yes | 0 | 2538458.2017 | 1269229.1009 | 5076916.4035 | Not At-Risk | Missing
CA2702317 | MISSION SCHOOL WS | 100 | 1 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 52770.8374 | No | 2499707.1456 | 0 | No | 41105.22 | 2595897.073 | 1297948.5365 | 5191794.1459 | HR2W | Missing
CA2702322 | CAPTAIN COOPER SCHOOL WS | 95 | 1 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 52217.734 | No | 2499171.3388 | 0 | Yes | 0 | 2553702.9429 | 1276851.4714 | 5107405.8858 | Not At-Risk | Missing
CA2702490 | CENTRAL BAY HIGH SCHOOL WS | 70 | 1 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 49452.2174 | No | 2496492.3051 | 0 | No | 41105.22 | 2589363.6125 | 1294681.8062 | 5178727.2249 | Not At-Risk | Missing
CA2800847 | NVUSD: CARNEROS SCHOOL | 100 | 1 | LPA58 - NAPA COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 52770.8374 | No | 2499707.1456 | 0 | Yes | 0 | 2554791.853 | 1277395.9265 | 5109583.7059 | Not At-Risk | Missing
CA2800848 | NVUSD: MT. GEORGE SCHOOL | 100 | 1 | LPA58 - NAPA COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 52770.8374 | No | 2499707.1456 | 0 | Yes | 0 | 2554791.853 | 1277395.9265 | 5109583.7059 | Not At-Risk | Missing
CA2800970 | HOWELL MOUNTAIN SCHOOL | 100 | 2 | LPA58 - NAPA COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 52770.8374 | Yes | 0 | 0 | No | 41105.22 | 96189.9274 | 48094.9637 | 192379.8548 | Not At-Risk | Missing
CA2900535 | PLEASANT RIDGE SCHOOL | 120 | 4 | LPA59 - NEVADA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 42294.8082 | No | 2017621.2682 | 0 | Yes | 0 | 2061695.9764 | 1030847.9882 | 4123391.9529 | Not At-Risk | Missing
CA2900536 | CLEAR CREEK SCHOOL | 160 | 8 | LPA59 - NEVADA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 45698.5211 | No | 2021078.0859 | 0 | No | 31619.4 | 2100175.907 | 1050087.9535 | 4200351.814 | Not At-Risk | Missing
CA2900578 | TWIN RIDGES GRIZZLY HILL SCHOOL | 125 | 11 | LPA59 - NEVADA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 42720.2723 | No | 2018053.3704 | 0 | No | 44183.4 | 2106736.9428 | 1053368.4714 | 4213473.8855 | Not At-Risk | Missing
CA2900587 | MOUNTAIN VALLEY CHILD AND FAMILY SERVICE | 50 | 10 | LPA59 - NEVADA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 36338.3108 | No | 2011571.8372 | 0 | No | 42927 | 2092617.048 | 1046308.524 | 4185234.096 | Not At-Risk | Missing
CA2900593 | TWIN RIDGES OAK TREE SCHOOL | 120 | 8 | LPA59 - NEVADA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 42294.8082 | Yes | 0 | 0 | No | 40414.2 | 84488.9082 | 42244.4541 | 168977.8165 | Not At-Risk | Missing
CA2901208 | DONNER TRAIL ELEMENTARY SCHOOL | 60 | 1 | LPA59 - NEVADA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 37189.239 | No | 2012436.0416 | 0 | No | 31619.4 | 2083024.5806 | 1041512.2903 | 4166049.1612 | Potentially At-Risk | Missing
CA3100072 | LIVE OAK WALDORF SCHOOL | 200 | 1 | LPA61 - PLACER COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 49102.2339 | No | 2024534.9037 | 0 | Yes | 0 | 2075417.0375 | 1037708.5188 | 4150834.0751 | Not At-Risk | Missing
CA3100083 | OPHIR ELEMENTARY SCHOOL WATER SYSTEM | 260 | 1 | LPA61 - PLACER COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 54207.8031 | No | 2029720.1303 | 0 | Yes | 0 | 2085707.8334 | 1042853.9167 | 4171415.6667 | Potentially At-Risk | Missing
CA3107342 | LINCOLN HIGH SCHOOL FARM | 50 | 1 | LPA61 - PLACER COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 36338.3108 | No | 2011571.8372 | 0 | Yes | 0 | 2049690.048 | 1024845.024 | 4099380.096 | Not At-Risk | Missing
CA3200079 | PUSD TAYLORSVILLE ELEMENTARY SCHOOL | 94 | 1 | LPA62 - PLUMAS COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2015374.3367 | 0 | Yes | 0 | 2017154.2367 | 1008577.1183 | 4034308.4734 | Not At-Risk | Missing
CA3200215 | SCHRAMEL WATER SYSTEM | 100 | 1 | LPA62 - PLUMAS COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 40592.9518 | No | 2015892.8593 | 0 | Yes | 0 | 2058265.7112 | 1029132.8556 | 4116531.4223 | Not At-Risk | Missing
CA3301308 | COTTONWOOD SCHOOL | 312 | 7 | LPA63 - RIVERSIDE COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 77395.0713 | Yes | 0 | 0 | No | 51688.296 | 129083.3673 | 64541.6836 | 258166.7345 | Not At-Risk | Missing
CA3301309 | HAMILTON SCHOOL | 958 | 20 | LPA63 - RIVERSIDE COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 149955.421 | Yes | 0 | 0 | No | 73248.12 | 223203.541 | 111601.7705 | 446407.082 | Not At-Risk | Missing
CA3400248 | FRANKLIN ELEMENTARY SCHOOL | 650 | 13 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 115360.084 | No | 2591660.6736 | 0 | Yes | 0 | 2709370.2256 | 1354685.1128 | 5418740.4511 | At-Risk | Missing
CA3400250 | PLEASANT GROVE ELEMENTARY SCHOOL | 185 | 10 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 63130.1109 | No | 2541187.6779 | 0 | Yes | 0 | 2606667.2567 | 1303333.6284 | 5213334.5134 | Not At-Risk | Missing
CA3400251 | SIERRA ENTERPRISE ELEMENTARY SCHOOL | 430 | 13 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 90649.1289 | No | 2567780.9767 | 0 | Yes | 0 | 2660779.5736 | 1330389.7868 | 5321559.1473 | Not At-Risk | Missing
CA3400253 | COSUMNES RIVER ELEMENTARY SCHOOL | 560 | 8 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 105251.0569 | Yes | 0 | 0 | Yes | 0 | 107600.5249 | 53800.2625 | 215201.0498 | Not At-Risk | Missing
CA3400254 | DILLARD ELEMENTARY SCHOOL | 350 | 4 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | Yes | 0 | No | 2559097.4505 | 0 | Yes | 0 | 2561446.9185 | 1280723.4593 | 5122893.8371 | Not At-Risk | Missing
CA3400259 | GRANT HIGH SCHOOL [SWS] | 1400 | 12 | LPA64 - SACRAMENTO COUNTY | NTNC | SCHOOL | Yes | 0 | No | 199601.9761 | No | 2673068.7312 | 0 | Yes | 0 | 2872670.7073 | 1436335.3537 | 5745341.4146 | Not At-Risk | Missing
CA3400267 | BATES ELEMENTARY SCHOOL | 375 | 10 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 84471.3902 | Yes | 0 | 0 | No | 56663.64 | 143484.4982 | 71742.2491 | 286968.9964 | Not At-Risk | Missing
CA3400268 | WALNUT GROVE ELEMENTARY SCHOOL | 200 | 2 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 64814.9487 | No | 2542815.839 | 0 | No | 43396.056 | 2653376.3117 | 1326688.1559 | 5306752.6234 | Not At-Risk | Missing
CA3400271 | ARCOHE ELEM SCHOOL - MAIN CAMPUS | 465 | 2 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 94580.4172 | Yes | 0 | 0 | Yes | 0 | 96929.8852 | 48464.9426 | 193859.7705 | Not At-Risk | Missing
CA3400273 | WILTON BIBLE CHURCH | 125 | 5 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 56390.7595 | No | 2534675.0332 | 0 | No | 48371.4 | 2641786.6607 | 1320893.3304 | 5283573.3215 | Not At-Risk | Missing
CA3400391 | BRADSHAW CHRISTIAN SCHOOL | 935 | 8 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 147372.003 | No | 2622595.7355 | 0 | Yes | 0 | 2772317.2065 | 1386158.6032 | 5544634.4129 | Not At-Risk | Missing
CA3500507 | BITTERWATER-TULLY SCHOOL WS | 45 | 2 | DISTRICT 05 - MONTEREY | NTNC | NT - SCHOOL | Yes | 0 | No | 46686.7007 | N/A | 0 | 0 | No | 42738.54 | 89425.2407 | 44712.6204 | 178850.4815 | At-Risk | Missing
CA3500521 | SOUTHSIDE ELEMENTARY SCHOOL | 300 | 2 | DISTRICT 05 - MONTEREY | NTNC | NT - SCHOOL | No | 2313.87 | No | 74894.9707 | No | 2521139.4155 | 0 | No | 42738.54 | 2641086.7962 | 1320543.3981 | 5282173.5924 | Not At-Risk | Missing
CA3500571 | SAN BENITO HIGH SCHOOL | 3310 | 61 | DISTRICT 05 - MONTEREY | NTNC | NT - SCHOOL | No | 2313.87 | No | 407863.1765 | Yes | 0 | 0 | No | 139104.42 | 549281.4665 | 274640.7333 | 1098562.9331 | Not At-Risk | Missing
CA3500801 | WILLOW GROVE UNION ELEMENTARY SCHOOL | 25 | 4 | DISTRICT 05 - MONTEREY | NTNC | NT - SCHOOL | No | 2313.87 | No | 44474.2874 | No | 2491670.0443 | 0 | No | 46005.18 | 2584463.3817 | 1292231.6909 | 5168926.7635 | At-Risk | Missing
CA3500905 | ANZAR HIGH SCHOOL | 328 | 9 | DISTRICT 05 - MONTEREY | NTNC | NT - SCHOOL | No | 2313.87 | No | 77992.3493 | Yes | 0 | 0 | No | 54171.78 | 134477.9993 | 67238.9997 | 268955.9986 | Not At-Risk | Missing
CA3600432 | LUCERNE VALLEY ELEMENTARY SCHOOL | 441 | 15 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - SCHOOL | Yes | 0 | Yes | 0 | No | 2536249.1658 | 0 | No | 63971.7 | 2600220.8658 | 1300110.4329 | 5200441.7317 | Not At-Risk | Missing
CA3600790 | NEWBERRY ELEMENTARY SCHOOL | 255 | 2 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 69917.0407 | No | 2516317.1548 | 0 | Yes | 0 | 2588548.0655 | 1294274.0327 | 5177096.1309 | At-Risk | Missing
CA3601057 | MOUNTAIN VIEW CONTINUATION SCHOOL | 30 | 4 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - SCHOOL | Yes | 0 | Yes | 0 | No | 2492205.8511 | 0 | No | 46005.18 | 2538211.0311 | 1269105.5155 | 5076422.0622 | Not At-Risk | Missing
CA3601095 | LUCERNE VALLEY HIGH SCHOOL | 329 | 11 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - SCHOOL | Yes | 0 | Yes | 0 | No | 2524247.0947 | 0 | No | 57438.42 | 2581685.5147 | 1290842.7573 | 5163371.0293 | Not At-Risk | Missing
CA3601179 | EL MIRAGE SCHOOL | 50 | 9 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 47239.8041 | Yes | 0 | 0 | No | 54171.78 | 103725.4541 | 51862.727 | 207450.9081 | Not At-Risk | Missing
CA3700018 | CAMPO ELEMENTARY SCHOOL | 300 | 3 | LPA67 - SAN DIEGO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 76047.201 | Yes | 0 | 0 | Yes | 0 | 78396.669 | 39198.3345 | 156793.338 | HR2W | Missing
CA3700117 | MOUNTAIN EMPIRE HIGH SCHOOL | 1000 | 12 | LPA67 - SAN DIEGO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 154672.9669 | Yes | 0 | 0 | No | 59980.536 | 217002.9709 | 108501.4855 | 434005.9419 | Not At-Risk | Missing
CA3700118 | CAMP LOCKETT MIDDLE SCHOOL | 150 | 4 | LPA67 - SAN DIEGO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 59198.8226 | No | 2537388.6352 | 0 | No | 46712.952 | 2645649.8777 | 1322824.9389 | 5291299.7555 | At-Risk | Missing
CA3700963 | POTRERO ELEMENTARY SCHOOL | 300 | 19 | LPA67 - SAN DIEGO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 76047.201 | No | 2553670.2467 | 0 | No | 71589.672 | 2703656.5877 | 1351828.2938 | 5407313.1754 | Not At-Risk | Missing
CA3701005 | SPENCER VALLEY SCHOOL DISTRICT | 40 | 4 | LPA67 - SAN DIEGO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 46843.345 | No | 2525448.7867 | 0 | No | 46712.952 | 2621354.5518 | 1310677.2759 | 5242709.1035 | Not At-Risk | Missing
CA3701010 | WARNER UNIFIED SCHOOL DISTRICT | 250 | 15 | LPA67 - SAN DIEGO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 70431.0748 | Yes | 0 | 0 | No | 64955.88 | 137736.4228 | 68868.2114 | 275472.8457 | HR2W | Missing
CA3702364 | CLOVER FLAT ELEMENTARY SCHOOL | 160 | 5 | LPA67 - SAN DIEGO COUNTY | NTNC | NT - SCHOOL | No | 2349.468 | No | 60322.0478 | No | 2538474.0759 | 0 | No | 48371.4 | 2649516.9917 | 1324758.4959 | 5299033.9834 | Not At-Risk | Missing
CA3900748 | ESCALON USD- COLLEGEVILLE SCH | 100 | 1 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 40592.9518 | Yes | 0 | 0 | No | 31619.4 | 72212.3518 | 36106.1759 | 144424.7037 | Not At-Risk | Missing
CA3900756 | LINDEN USD-GLENWOOD SCHOOL | 100 | 1 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2015892.8593 | 0 | Yes | 0 | 2017672.7593 | 1008836.3797 | 4035345.5187 | Not At-Risk | Missing
CA3900757 | LINDEN USD-WATERLOO ELEMENTARY | 225 | 1 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 51229.5544 | No | 2026695.4148 | 0 | Yes | 0 | 2079704.8691 | 1039852.4346 | 4159409.7383 | Not At-Risk | Missing
CA3900846 | OAK VIEW UNION ELEMENTARY SCH | 350 | 1 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 61866.1569 | No | 2037497.9702 | 0 | Yes | 0 | 2099364.1271 | 1049682.0635 | 4198728.2542 | Not At-Risk | Missing
CA3900848 | LODI USD-TURNER ACADEMY AT TOKAY COLONY | 166 | 2 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 46209.078 | No | 2021596.6086 | 0 | No | 32875.8 | 2100681.4866 | 1050340.7433 | 4201362.9731 | Not At-Risk | Missing
CA3900849 | LODI USD-LIVE OAK SCHOOL | 100 | 1 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 40592.9518 | No | 2015892.8593 | 0 | No | 31619.4 | 2088105.2112 | 1044052.6056 | 4176210.4223 | Not At-Risk | Missing
CA3900850 | LODI USD-HOUSTON SCHOOL | 405 | 4 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 66546.262 | No | 2042251.0946 | 0 | No | 35388.6 | 2144185.9566 | 1072092.9783 | 4288371.9132 | Not At-Risk | Missing
CA3900978 | SJ COUNTY-REDWOOD SCHOOL | 83 | 1 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2014423.7118 | 0 | Yes | 0 | 2016203.6118 | 1008101.8059 | 4032407.2236 | HR2W | Missing
CA3900993 | NEW JERUSALEM SCHOOL | 210 | 1 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2025399.1081 | 0 | Yes | 0 | 2027179.0081 | 1013589.5041 | 4054358.0162 | Potentially At-Risk | Missing
CA3901014 | BANTA ELEMENTARY SCHOOL | 200 | 1 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 49102.2339 | No | 2024534.9037 | 0 | Yes | 0 | 2073637.1375 | 1036818.5688 | 4147274.2751 | Not At-Risk | Missing
CA3901085 | LODI USD-DAVIS SCHOOL | 630 | 1 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 85692.1466 | No | 2061695.6943 | 0 | No | 31619.4 | 2179007.2409 | 1089503.6205 | 4358014.4818 | Not At-Risk | Missing
CA3901090 | NORTH VALLEY SCHOOL PWS | 35 | 1 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 35061.9185 | No | 2010275.5305 | 0 | No | 31619.4 | 2076956.849 | 1038478.4245 | 4153913.6981 | Potentially At-Risk | Missing
CA3901107 | JEFFERSON ESD-JEFFERSON SCHOOL | 60 | 1 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 37189.239 | No | 2012436.0416 | 0 | No | 31619.4 | 2081244.6806 | 1040622.3403 | 4162489.3612 | Not At-Risk | Missing
CA3901163 | MUSD-NEW HAVEN SCHOOL | 300 | 3 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 57611.5159 | No | 2033176.948 | 0 | No | 34132.2 | 2124920.6639 | 1062460.332 | 4249841.3278 | Not At-Risk | Missing
CA3901167 | EUSD-VAN ALLEN SCHOOL | 200 | 1 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 49102.2339 | No | 2024534.9037 | 0 | No | 31619.4 | 2105256.5375 | 1052628.2688 | 4210513.0751 | Potentially At-Risk | Missing
CA3901169 | MUSD-NILE GARDEN SCHOOL | 804 | 3 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 100498.2973 | No | 2076732.8515 | 0 | No | 34132.2 | 2211363.3488 | 1105681.6744 | 4422726.6976 | HR2W | Missing
CA3901209 | ST MARYS HIGH SCHOOL | 950 | 11 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 112921.8491 | No | 2089350.2362 | 0 | No | 44183.4 | 2246455.4853 | 1123227.7426 | 4492910.9706 | Not At-Risk | Missing
CA3901325 | RIPON CHRISTIAN SCHOOLS | 900 | 1 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 108667.2081 | No | 2085029.214 | 0 | Yes | 0 | 2195476.3221 | 1097738.1611 | 4390952.6442 | At-Risk | Missing
CA3901331 | RIPON USD-COLONY OAK SCHOOL | 100 | 1 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 40592.9518 | No | 2015892.8593 | 0 | No | 31619.4 | 2088105.2112 | 1044052.6056 | 4176210.4223 | Not At-Risk | Missing
CA3902136 | LINDEN USD-CHARTVILLE SCHOOL | 40 | 1 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2010707.6327 | 0 | Yes | 0 | 2012487.5327 | 1006243.7664 | 4024975.0655 | Potentially At-Risk | Missing
CA4000675 | BRANCH ELEMENTARY SCHOOL | 500 | 1 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | Yes | 0 | No | 2542571.6855 | 0 | Yes | 0 | 2544885.5555 | 1272442.7777 | 5089771.111 | Not At-Risk | Missing
CA4000693 | CRESTON ELEMENTARY SCHOOL | 100 | 1 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 2313.87 | 1156.935 | 4627.74 | Not At-Risk | Missing
CA4000732 | CARRISA PLAINS ELEMENTARY | 65 | 1 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 48899.1141 | No | 2495956.4983 | 0 | Yes | 0 | 2547169.4824 | 1273584.7412 | 5094338.9648 | HR2W | Missing
CA4000767 | SANTA LUCIA SCHOOL | 52 | 1 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 47461.0454 | No | 2494563.4008 | 0 | Yes | 0 | 2544338.3162 | 1272169.1581 | 5088676.6324 | Not At-Risk | Missing
CA4000774 | PLEASANT VALLEY ELEMENTARY | 100 | 1 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 52770.8374 | Yes | 0 | 0 | Yes | 0 | 55084.7074 | 27542.3537 | 110169.4148 | Potentially At-Risk | Missing
CA4100513 | PESCADERO HIGH SCHOOL | 192 | 1 | DISTRICT 17 - SANTA CLARA | NTNC | NT - SCHOOL | No | 2349.468 | No | 63916.3685 | No | 2541947.4864 | 0 | Yes | 0 | 2608213.3229 | 1304106.6615 | 5216426.6458 | HR2W | Missing
CA4200747 | VISTA DE LAS CRUCES | 50 | 2 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 47239.8041 | Yes | 0 | 0 | Yes | 41105.22 | 90658.8941 | 45329.447 | 181317.7881 | Not At-Risk | Missing
CA4200833 | BONITA SCHOOL | 589 | 1 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 106864.3433 | No | 2552109.0456 | 0 | Yes | 0 | 2661287.2589 | 1330643.6294 | 5322574.5177 | At-Risk | Missing
CA4200879 | CUYAMA ELEMENTARY SCHOOL | 250 | 1 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 69363.9373 | No | 2515781.348 | 0 | Yes | 41105.22 | 2628564.3754 | 1314282.1877 | 5257128.7508 | Not At-Risk | Missing
CA4300593 | MORGAN HILL USD-MACHADO SCHOOL | 60 | 1 | DISTRICT 17 - SANTA CLARA | NTNC | NT - SCHOOL | No | 2349.468 | No | 49089.7955 | No | 0 | 836900.604 | Yes | 41737.608 | 930077.4755 | 465038.7378 | 1860154.951 | Not At-Risk | Missing
CA4300605 | GILROY USD-RUCKER SCHOOL | 688 | 1 | DISTRICT 17 - SANTA CLARA | NTNC | NT - SCHOOL | No | 2349.468 | No | 119628.3398 | No | 2595785.3485 | 0 | Yes | 0 | 2717763.1564 | 1358881.5782 | 5435526.3127 | Not At-Risk | Missing
CA4300610 | ANCHORPOINT CHRISTIAN SCHOOL | 167 | 1 | DISTRICT 17 - SANTA CLARA | NTNC | NT - SCHOOL | No | 2349.468 | No | 61108.3054 | No | 2539233.8845 | 0 | Yes | 41737.608 | 2644429.2659 | 1322214.633 | 5288858.5318 | At-Risk | Missing
CA4300721 | LOMA PRIETA JUSD-LOMA PRIETA SCHOOL | 560 | 8 | DISTRICT 17 - SANTA CLARA | NTNC | NT - SCHOOL | No | 2349.468 | No | 105251.0569 | Yes | 0 | 0 | Yes | 53346.744 | 160947.2689 | 80473.6345 | 321894.5378 | Not At-Risk | Missing
CA4300779 | LAKESIDE SD-LAKESIDE SCHOOL | 127 | 4 | DISTRICT 17 - SANTA CLARA | NTNC | NT - SCHOOL | No | 2349.468 | No | 56615.4045 | No | 2534892.1214 | 0 | Yes | 46712.952 | 2640569.9459 | 1320284.973 | 5281139.8919 | Not At-Risk | Missing
CA4400750 | APTOS HIGH SCHOOL | 1925 | 6 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | Yes | 0 | Yes | 0 | 0 | Yes | 49271.82 | 51585.69 | 25792.845 | 103171.38 | Not At-Risk | Missing
CA4400751 | BONNY DOON SCHOOL | 160 | 10 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 59408.0774 | No | 2506136.8266 | 0 | Yes | 55805.1 | 2623663.8739 | 1311831.937 | 5247327.7479 | Not At-Risk | Missing
CA4400754 | MONTE VISTA CHRISTIAN SCHOOL | 1083 | 43 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 164934.6192 | Yes | 0 | 0 | Yes | 109704.66 | 276953.1492 | 138476.5746 | 553906.2984 | Not At-Risk | Missing
CA4400756 | MOUNTAIN ELEMENTARY SCHOOL | 250 | 1 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 69363.9373 | No | 2515781.348 | 0 | Yes | 0 | 2587459.1554 | 1293729.5777 | 5174918.3108 | Potentially At-Risk | Missing
CA4400757 | ALIANZA CHARTER SCHOOL/WCSA | 967 | 3 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | Yes | 0 | No | 2592616.0358 | 0 | Yes | 44371.86 | 2639301.7658 | 1319650.8829 | 5278603.5316 | Not At-Risk | Missing
CA4400758 | RENAISSANCE HIGH SCHOOL | 250 | 2 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 69363.9373 | No | 2515781.348 | 0 | Yes | 41105.22 | 2628564.3754 | 1314282.1877 | 5257128.7508 | Potentially At-Risk | Missing
CA4400875 | SANTA CRUZ WALDORF SCHOOL | 190 | 2 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - SCHOOL | No | 2313.87 | No | 62726.6974 | Yes | 0 | 0 | Yes | 41105.22 | 106145.7874 | 53072.8937 | 212291.5747 | Not At-Risk | Missing
CA4500041 | ANDERSON UNION HIGH SCHOOL | 700 | 2 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 91648.644 | Yes | 0 | 0 | Yes | 0 | 93428.544 | 46714.272 | 186857.088 | Not At-Risk | Missing
CA4500160 | PACHECO ELEMENTARY SCHOOL | 400 | 2 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2041818.9923 | 0 | Yes | 31619.4 | 2075218.2923 | 1037609.1462 | 4150436.5847 | Not At-Risk | Missing
CA4500161 | PRAIRIE ELEMENTARY SCHOOL | 375 | 1 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 63993.4774 | No | 2039658.4813 | 0 | Yes | 0 | 2105431.8587 | 1052715.9293 | 4210863.7174 | Not At-Risk | Missing
CA4500162 | INDIAN SPRINGS SCHOOL | 25 | 1 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 34210.9903 | No | 2009411.3261 | 0 | Yes | 31619.4 | 2075241.7164 | 1037620.8582 | 4150483.4328 | Not At-Risk | Missing
CA4500163 | JUNCTION SCHOOL DISTRICT | 700 | 2 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 91648.644 | Yes | 0 | 0 | Yes | 0 | 93428.544 | 46714.272 | 186857.088 | Not At-Risk | Missing
CA4500170 | MONTGOMERY CREEK SCHOOL | 95 | 1 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL | Yes | 0 | Yes | 0 | No | 2015460.7571 | 0 | Yes | 0 | 2015460.7571 | 1007730.3786 | 4030921.5142 | Not At-Risk | Missing
CA4500180 | MILLVILLE ELEMENTARY SCHOOL | 110 | 2 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 41443.88 | No | 2016757.0638 | 0 | Yes | 31619.4 | 2091600.2438 | 1045800.1219 | 4183200.4876 | Not At-Risk | Missing
CA4500181 | WHITMORE UNION ELEM SCHOOL | 35 | 2 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 35061.9185 | Yes | 0 | 0 | Yes | 32875.8 | 69717.6185 | 34858.8093 | 139435.237 | Not At-Risk | Missing
CA4500183 | BLACK BUTTE ELEMENTARY SCHOOL | 250 | 1 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 53356.8749 | No | 2028855.9258 | 0 | Yes | 0 | 2083992.7007 | 1041996.3504 | 4167985.4014 | Not At-Risk | Missing
CA4500190 | OAK RUN ELEMENTARY SCHOOL | 125 | 1 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 42720.2723 | No | 2018053.3704 | 0 | Yes | 0 | 2062553.5428 | 1031276.7714 | 4125107.0855 | Not At-Risk | Missing
CA4500193 | VERDE VALE ELEMENTARY SCHOOL | 290 | 1 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2032312.7436 | 0 | Yes | 0 | 2034092.6436 | 1017046.3218 | 4068185.2871 | Not At-Risk | Missing
CA4500214 | WEST VALLEY HIGH SCHOOL | 850 | 1 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 104412.5671 | No | 2080708.1919 | 0 | Yes | 0 | 2186900.6589 | 1093450.3295 | 4373801.3178 | Not At-Risk | Missing
CA4500322 | BLACK BUTTE JUNIOR HIGH SCHOOL | 100 | 1 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 40592.9518 | No | 2015892.8593 | 0 | Yes | 0 | 2058265.7112 | 1029132.8556 | 4116531.4223 | Not At-Risk | Missing
CA4700559 | BUTTEVILLE UNION SCHOOL | 165 | 2 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL | No | 1779.9 | No | 46123.9852 | No | 2021510.1882 | 0 | Yes | 31619.4 | 2101033.4733 | 1050516.7367 | 4202066.9466 | Not At-Risk | Missing
CA4700569 | WILLOW CREEK SCHOOL | 100 | 1 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL | Yes | 0 | No | 40592.9518 | No | 2015892.8593 | 0 | Yes | 0 | 2056485.8112 | 1028242.9056 | 4112971.6223 | Potentially At-Risk | Missing
CA4700577 | BIG SPRINGS UNION ELEM. SCHOOL | 95 | 2 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL | Yes | 0 | No | 40167.4877 | No | 2015460.7571 | 0 | Yes | 32875.8 | 2088504.0448 | 1044252.0224 | 4177008.0897 | Not At-Risk | Missing
CA4700582 | GAZELLE SCHOOL | 60 | 1 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL | No | 1779.9 | No | 37189.239 | No | 2012436.0416 | 0 | Yes | 31619.4 | 2083024.5806 | 1041512.2903 | 4166049.1612 | At-Risk | Missing
CA4700585 | JUNCTION ELEMENTARY SCHOOL | 40 | 1 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL | No | 1779.9 | No | 35487.3826 | No | 2010707.6327 | 0 | Yes | 31619.4 | 2079594.3153 | 1039797.1577 | 4159188.6307 | HR2W | Missing
CA4700591 | DELPHIC ELEMENTARY SCHOOL | 50 | 1 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL | No | 1779.9 | No | 36338.3108 | No | 2011571.8372 | 0 | Yes | 31619.4 | 2081309.448 | 1040654.724 | 4162618.896 | At-Risk | Missing
CA4900679 | FORT ROSS SCHOOL DISTRICT | 100 | 2 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 52770.8374 | No | 2499707.1456 | 0 | Yes | 0 | 2554791.853 | 1277395.9265 | 5109583.7059 | Not At-Risk | Missing
CA4900680 | HORICON SCHOOL | 100 | 4 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | Yes | 0 | Yes | 0 | N/A | 0 | 0 | Yes | 46005.18 | 46005.18 | 23002.59 | 92010.36 | Not At-Risk | Missing
CA4900693 | BELLEVUE UNION SCH DIST-BELLEVUE SCHOOL | 591 | 2 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 107085.5846 | No | 2552323.3683 | 0 | Yes | 42738.54 | 2704461.3629 | 1352230.6814 | 5408922.7258 | Not At-Risk | Missing
CA4900694 | WRIGHT ELEMENTARY SCHOOL | 500 | 11 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 97019.1039 | No | 2542571.6855 | 0 | Yes | 57438.42 | 2699343.0794 | 1349671.5397 | 5398686.1589 | Not At-Risk | Missing
CA4900695 | NORTHWEST PREP | 325 | 1 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 77660.4873 | No | 2523818.4493 | 0 | Yes | 41105.22 | 2644898.0266 | 1322449.0133 | 5289796.0532 | Not At-Risk | Missing
CA4900699 | OLIVET ELEMENTARY SCHOOL | 400 | 6 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 85957.0373 | No | 2531855.5505 | 0 | Yes | 49271.82 | 2669398.2778 | 1334699.1389 | 5338796.5556 | Not At-Risk | Missing
CA4900703 | OAK GROVE SCHOOL | 500 | 7 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 97019.1039 | Yes | 0 | 0 | Yes | 50905.14 | 150238.1139 | 75119.057 | 300476.2279 | Not At-Risk | Missing
CA4900704 | ALEXANDER VALLEY UNION SCHOOL DISTRICT | 200 | 5 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 63832.904 | No | 2510423.2806 | 0 | Yes | 47638.5 | 2624208.5546 | 1312104.2773 | 5248417.1091 | Not At-Risk | Missing
CA4900705 | GEYSERVILLE NEWTECH ACADEMY | 200 | 1 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 63832.904 | No | 2510423.2806 | 0 | Yes | 0 | 2576570.0546 | 1288285.0273 | 5153140.1091 | Not At-Risk | Missing
CA4900707 | TWIN HILLS SCHOOL DIST-TWIN HILLS SCHOOL | 400 | 2 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | Yes | 0 | No | 2531855.5505 | 0 | Yes | 42738.54 | 2576907.9605 | 1288453.9803 | 5153815.921 | Not At-Risk | Missing
CA4900708 | GRAVENSTEIN SCHOOL DISTRICT-GRAVENSTEIN | 398 | 7 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 85735.796 | No | 2531641.2278 | 0 | Yes | 50905.14 | 2670596.0338 | 1335298.0169 | 5341192.0676 | Not At-Risk | Missing
CA4900710 | TWIN HILLS SCHOOL DIST-APPLE BLOSSOM SCH | 400 | 1 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | Yes | 0 | No | 85957.0373 | No | 2531855.5505 | 0 | Yes | 0 | 2617812.5878 | 1308906.2939 | 5235625.1756 | Not At-Risk | Missing
CA4900711 | GRAVENSTEIN SCHOOL DISTRICT-HILLCREST | 289 | 1 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 73678.1433 | No | 2519960.6407 | 0 | Yes | 41105.22 | 2637057.874 | 1318528.937 | 5274115.748 | Not At-Risk | Missing
CA4900714 | LIBERTY SCHOOL | 225 | 3 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 66598.4207 | No | 2513102.3143 | 0 | Yes | 44371.86 | 2626386.465 | 1313193.2325 | 5252772.93 | At-Risk | Missing
CA4900716 | CINNABAR ELEMENTARY SCHOOL | 228 | 2 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | Yes | 0 | No | 66930.2827 | No | 2513423.7983 | 0 | Yes | 41105.22 | 2621459.301 | 1310729.6505 | 5242918.6021 | At-Risk | Missing
CA4900719 | WEST SIDE UNION SCHOOL DISTRICT | 200 | 5 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 63832.904 | No | 2510423.2806 | 0 | Yes | 47638.5 | 2624208.5546 | 1312104.2773 | 5248417.1091 | Not At-Risk | Missing
CA4900739 | DUNHAM SCHOOL | 200 | 2 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 63832.904 | No | 2510423.2806 | 0 | Yes | 42738.54 | 2619308.5946 | 1309654.2973 | 5238617.1891 | Not At-Risk | Missing
CA4900907 | SUMMERFIELD WALDORF SCHOOL | 299 | 13 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 74784.35 | No | 2521032.2542 | 0 | Yes | 60705.06 | 2658835.5342 | 1329417.7671 | 5317671.0684 | Not At-Risk | Missing
CA4900945 | PRESENTATION SCHOOL | 200 | 4 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 63832.904 | No | 2510423.2806 | 0 | Yes | 46005.18 | 2622575.2346 | 1311287.6173 | 5245150.4691 | Not At-Risk | Missing
CA4901156 | WILLOWSIDE SCHOOL | 460 | 5 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 92594.2773 | No | 2538285.2315 | 0 | Yes | 47638.5 | 2680831.8788 | 1340415.9394 | 5361663.7576 | Not At-Risk | Missing
CA4901168 | SALMON CREEK MIDDLE SCHOOL | 300 | 14 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 74894.9707 | No | 2521139.4155 | 0 | Yes | 62338.38 | 2660686.6362 | 1330343.3181 | 5321373.2724 | Potentially At-Risk | Missing
CA4901190 | LIETO WATER SYSTEM (REACH CHARTR SCHOOL) | 134 | 2 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 56531.94 | No | 2503350.6315 | 0 | Yes | 0 | 2562196.4415 | 1281098.2208 | 5124392.883 | Not At-Risk | Missing
CA4901215 | PLUMFIELD ACADEMY (OCCIDENTAL RD.) | 30 | 1 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | No | 2313.87 | No | 45027.3907 | No | 2492205.8511 | 0 | Yes | 41105.22 | 2580652.3318 | 1290326.1659 | 5161304.6637 | Not At-Risk | Missing
CA4901436 | SEBASTOPOL CHARTER SCHOOL | 360 | 1 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL | Yes | 0 | No | 81532.2106 | No | 2527569.0965 | 0 | Yes | 41105.22 | 2650206.5272 | 1325103.2636 | 5300413.0543 | At-Risk | Missing
CA5000101 | CHATOM SCHOOL (EH) | 500 | 1 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 74630.08 | No | 2050461.0367 | 0 | Yes | 0 | 2126871.0166 | 1063435.5083 | 4253742.0333 | Not At-Risk | Missing
CA5000109 | CERES UNIFIED/WESTPORT SCHOOL | 450 | 1 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2046140.0145 | 0 | Yes | 31619.4 | 2079539.3145 | 1039769.6573 | 4159078.629 | At-Risk | Missing
CA5000132 | VALLEY HOME SCHOOL TEXAS | 80 | 1 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 38891.0954 | No | 2014164.4505 | 0 | Yes | 31619.4 | 2084674.9459 | 1042337.4729 | 4169349.8918 | Not At-Risk | Missing
CA5000133 | HART- RANSOM UNION SCHOOL & DISTRICT | 650 | 4 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 87394.003 | No | 2063424.1032 | 0 | Yes | 35388.6 | 2187986.6062 | 1093993.3031 | 4375973.2124 | Not At-Risk | Missing
CA5000155 | ROBERTS FERRY SCHOOL CAFETERIA | 100 | 2 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 40592.9518 | No | 2015892.8593 | 0 | Yes | 0 | 2058265.7112 | 1029132.8556 | 4116531.4223 | Not At-Risk | Missing
CA5000249 | STANISLAUS UNION SCHOOL DIST | 390 | 1 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 65269.8697 | No | 2040954.7879 | 0 | Yes | 31619.4 | 2137844.0576 | 1068922.0288 | 4275688.1153 | HR2W | Missing
CA5000255 | MOUNTAIN VIEW ELEMENTARY SCHOOL | 364 | 1 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 63057.4564 | Yes | 0 | 0 | Yes | 0 | 64837.3564 | 32418.6782 | 129674.7128 | HR2W | Missing
CA5000273 | GRATTON SCHOOL | 110 | 2 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 41443.88 | No | 2016757.0638 | 0 | Yes | 32875.8 | 2091076.7438 | 1045538.3719 | 4182153.4876 | HR2W | Missing
CA5000274 | PARADISE SCHOOL | 152 | 4 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2020386.7224 | 0 | Yes | 35388.6 | 2057555.2224 | 1028777.6112 | 4115110.4448 | At-Risk | Missing
CA5000277 | VALLEY HOME SCHOOL PIONEER | 26 | 1 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 34296.0831 | No | 2009497.7465 | 0 | Yes | 31619.4 | 2075413.2297 | 1037706.6148 | 4150826.4593 | Not At-Risk | Missing
CA5000295 | SHILOH SCHOOL DISTRICT | 105 | 7 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 41018.4159 | No | 2016324.9616 | 0 | Yes | 0 | 2059123.2775 | 1029561.6387 | 4118246.555 | HR2W | Missing
CA5000335 | BRETHREN HERITAGE SCHOOL, INC | 25 | 2 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL | Yes | 0 | Yes | 0 | No | 2009411.3261 | 0 | Yes | 0 | 2009411.3261 | 1004705.663 | 4018822.6522 | Not At-Risk | Missing
CA5000404 | WOOD COLONY CHRISTIAN SCHOOL | 90 | 2 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL | Yes | 0 | Yes | 0 | No | 2015028.6549 | 0 | Yes | 32875.8 | 2047904.4549 | 1023952.2275 | 4095808.9098 | Not At-Risk | Missing
CA5000568 | GREGORI HIGH SCHOOL | 2000 | 9 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL | Yes | 0 | No | 202269.3104 | No | 2180091.7017 | 0 | Yes | 41670.6 | 2424031.6121 | 1212015.8061 | 4848063.2243 | Not At-Risk | Missing
CA5000584 | MESA ELEMENTARY SCHOOL | 860 | 5 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 105263.4953 | No | 2081572.3963 | 0 | Yes | 0 | 2188615.7916 | 1094307.8958 | 4377231.5831 | Not At-Risk | Missing
CA5100136 | EAST NICOLAUS JOINT UNION HIGH SCHOOL | 338 | 1 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL | No | 1779.9 | No | 60845.0431 | No | 2036460.9249 | 0 | Yes | 0 | 2099085.8679 | 1049542.934 | 4198171.7358 | Not At-Risk | Missing
CA5100138 | BROWNS ELEMENTARY SCHOOL | 160 | 1 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL | No | 1779.9 | No | 45698.5211 | No | 2021078.0859 | 0 | Yes | 31619.4 | 2100175.907 | 1050087.9535 | 4200351.814 | HR2W | Missing
CA5100140 | MARCUM ILLINOIS ELEMENTARY SCHOOL | 185 | 7 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL | No | 1779.9 | No | 47825.8416 | No | 2023238.597 | 0 | Yes | 0 | 2072844.3386 | 1036422.1693 | 4145688.6772 | Not At-Risk | Missing
CA5100141 | MERIDIAN ELEMENTARY SCHOOL | 100 | 1 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL | Yes | 0 | No | 40592.9518 | No | 2015892.8593 | 0 | Yes | 0 | 2056485.8112 | 1028242.9056 | 4112971.6223 | HR2W | Missing
CA5100142 | NUESTRO SCHOOL | 120 | 1 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2017621.2682 | 0 | Yes | 31619.4 | 2051020.5682 | 1025510.2841 | 4102041.1364 | At-Risk | Missing
CA5100143 | PLEASANT GROVE ELEM. SCHOOL | 185 | 1 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL | No | 1779.9 | No | 47825.8416 | No | 2023238.597 | 0 | Yes | 31619.4 | 2104463.7386 | 1052231.8693 | 4208927.4772 | Not At-Risk | Missing
CA5100145 | WINSHIP ELEMENTARY SCHOOL | 38 | 2 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL | No | 1779.9 | No | 35317.197 | Yes | 0 | 0 | Yes | 32875.8 | 69972.897 | 34986.4485 | 139945.7939 | HR2W | Missing
CA5100149 | BARRY ELEMENTARY SCHOOL | 650 | 1 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL | No | 1779.9 | No | 87394.003 | No | 2063424.1032 | 0 | Yes | 0 | 2152598.0062 | 1076299.0031 | 4305196.0124 | HR2W | Missing
CA5100172 | ENCINAL ELEMENTARY SCHOOL | 128 | 1 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL | No | 1779.9 | No | 42975.5508 | No | 2018312.6317 | 0 | Yes | 0 | 2063068.0825 | 1031534.0413 | 4126136.1651 | Potentially At-Risk | Missing
CA5200506 | PLUM VALLEY ELEM SCHOOL (NEW SCHOOL) | 70 | 1 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 38040.1672 | No | 2013300.246 | 0 | Yes | 31619.4 | 2084739.7133 | 1042369.8566 | 4169479.4265 | Not At-Risk | Missing
CA5200507 | BERRENDOS SCHOOL | 325 | 4 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 59738.8364 | No | 2035337.4591 | 0 | Yes | 0 | 2096856.1955 | 1048428.0977 | 4193712.391 | Not At-Risk | Missing
CA5200511 | BEND ELEMENTARY SCHOOL | 100 | 5 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2015892.8593 | 0 | Yes | 0 | 2017672.7593 | 1008836.3797 | 4035345.5187 | Not At-Risk | Missing
CA5200513 | EVERGREEN UNION SCHOOL DISTRICT | 1100 | 8 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 125685.7721 | Yes | 0 | 0 | Yes | 37901.4 | 165367.0721 | 82683.5361 | 330734.1443 | Not At-Risk | Missing
CA5200518 | FLOURNOY SCHOOL | 32 | 2 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 34806.6401 | No | 2010016.2692 | 0 | Yes | 32875.8 | 2079478.6092 | 1039739.3046 | 4158957.2185 | Not At-Risk | Missing
CA5200519 | GERBER UNION ELEMENTARY SCHOOL DISTRICT | 625 | 1 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 85266.6825 | No | 2061263.5921 | 0 | Yes | 0 | 2148310.1746 | 1074155.0873 | 4296620.3492 | Not At-Risk | Missing
CA5200520 | KIRKWOOD ELEMENTARY SCHOOL | 111 | 4 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 41528.9729 | No | 2016843.4842 | 0 | Yes | 35388.6 | 2095540.9571 | 1047770.4785 | 4191081.9141 | Not At-Risk | Missing
CA5200538 | LASSEN VIEW UNION ELEMENTARY SCHOOL DIST | 350 | 4 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 61866.1569 | No | 2037497.9702 | 0 | Yes | 0 | 2101144.0271 | 1050572.0135 | 4202288.0542 | Not At-Risk | Missing
CA5200540 | REEDS CREEK SCHOOL | 196 | 7 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 48761.8626 | No | 2024189.2219 | 0 | Yes | 0 | 2074730.9845 | 1037365.4922 | 4149461.969 | Potentially At-Risk | Missing
CA5200544 | VINA ELEMENTARY SCHOOL | 90 | 2 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 39742.0236 | No | 2015028.6549 | 0 | Yes | 32875.8 | 2089426.3785 | 1044713.1893 | 4178852.7571 | Not At-Risk | Missing
CA5200565 | RICHFIELD ELEMENTARY SCHOOL | 280 | 9 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 55909.6595 | No | 2031448.5391 | 0 | Yes | 41670.6 | 2130808.6986 | 1065404.3493 | 4261617.3973 | Not At-Risk | Missing
CA5205007 | RANCHO TEHAMA ELEM SCHOOL | 90 | 5 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2015028.6549 | 0 | Yes | 34132.2 | 2050940.7549 | 1025470.3775 | 4101881.5098 | Not At-Risk | Missing
CA5304105 | BURNT RANCH SCHOOL | 125 | 2 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL | No | 1779.9 | No | 42720.2723 | No | 2018053.3704 | 0 | Yes | 31619.4 | 2094172.9428 | 1047086.4714 | 4188345.8855 | At-Risk | Missing
CA5304209 | JUNCTION CITY SCHOOL | 80 | 2 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL | Yes | 0 | No | 38891.0954 | N/A | 0 | 0 | Yes | 0 | 38891.0954 | 19445.5477 | 77782.1908 | Not At-Risk | Missing
CA5305107 | SO TRINITY UNIFIED SCHOOL DIST. | 100 | 6 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL | No | 1779.9 | No | 40592.9518 | No | 2015892.8593 | 0 | Yes | 34132.2 | 2092397.9112 | 1046198.9556 | 4184795.8223 | Potentially At-Risk | Missing
CA5400519 | PALO VERDE SCHOOL | 500 | 26 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | No | 1779.9 | No | 74630.08 | No | 2050461.0367 | 0 | Yes | 63029.4 | 2189900.4166 | 1094950.2083 | 4379800.8333 | At-Risk | Missing
CA5400538 | ACCELERATED CHARTER HIGH SCHOOL | 172 | 10 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2022115.1313 | 0 | Yes | 41670.6 | 2065565.6313 | 1032782.8156 | 4131131.2625 | At-Risk | Missing
CA5400558 | SAUCELITO ELEMENTARY SCHOOL | 91 | 11 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | Yes | 0 | No | 39827.1164 | No | 2015115.0753 | 0 | Yes | 44183.4 | 2099125.5918 | 1049562.7959 | 4198251.1836 | HR2W | Missing
CA5400620 | GRAND VIEW SCHOOL | 400 | 9 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2041818.9923 | 0 | Yes | 0 | 2043598.8923 | 1021799.4462 | 4087197.7847 | Not At-Risk | Missing
CA5400624 | KINGS RIVER ELEMENTARY SCHOOL | 550 | 9 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | No | 1779.9 | No | 78884.721 | No | 2054782.0588 | 0 | Yes | 41670.6 | 2177117.2798 | 1088558.6399 | 4354234.5596 | Not At-Risk | Missing
CA5400636 | OROSI HIGH SCHOOL | 1200 | 8 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | No | 1779.9 | No | 134195.0542 | No | 2110955.347 | 0 | Yes | 31619.4 | 2278549.7012 | 1139274.8506 | 4557099.4024 | HR2W | Missing
CA5400704 | THREE RIVERS ELEMENTARY SCHOOL | 180 | 6 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | Yes | 0 | No | 47400.3775 | No | 2022806.4948 | 0 | Yes | 0 | 2070206.8723 | 1035103.4361 | 4140413.7445 | At-Risk | Missing
CA5400709 | SEQUOIA UNION ELEMENTARY SCHOOL | 400 | 26 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | No | 1779.9 | No | 66120.7979 | No | 2041818.9923 | 0 | Yes | 63029.4 | 2172749.0903 | 1086374.5451 | 4345498.1805 | Not At-Risk | Missing
CA5400711 | SIERRA VIEW JR ACADEMY | 104 | 5 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | Yes | 0 | No | 40933.3231 | No | 2016238.5411 | 0 | Yes | 36645 | 2093816.8642 | 1046908.4321 | 4187633.7284 | HR2W | Missing
CA5400713 | OAK VALLEY SCHOOL | 652 | 10 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | Yes | 0 | No | 87564.1886 | No | 2063596.9441 | 0 | Yes | 42927 | 2194088.1327 | 1097044.0664 | 4388176.2654 | At-Risk | Missing
CA5400714 | SUNDALE UNION SCHOOL | 827 | 11 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | No | 1779.9 | No | 102455.4322 | No | 2078720.5217 | 0 | Yes | 44183.4 | 2227139.2539 | 1113569.6269 | 4454278.5077 | Not At-Risk | Missing
CA5400795 | WAUKENA ELEMENTARY SCHOOL | 255 | 7 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | Yes | 0 | No | 53782.339 | No | 2029288.0281 | 0 | Yes | 39157.8 | 2122228.167 | 1061114.0835 | 4244456.3341 | HR2W | Missing
CA5400844 | ELBOW CREEK SCHOOL | 530 | 11 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | No | 1779.9 | No | 77182.8646 | No | 2053053.65 | 0 | Yes | 44183.4 | 2176199.8145 | 1088099.9073 | 4352399.6291 | HR2W | Missing
CA5400846 | ELBOW SCHOOL | 95 | 3 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | No | 1779.9 | No | 40167.4877 | No | 2015460.7571 | 0 | Yes | 34132.2 | 2091540.3448 | 1045770.1724 | 4183080.6897 | Not At-Risk | Missing
CA5400850 | PACKWOOD SCHOOL | 105 | 2 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | No | 1779.9 | No | 41018.4159 | No | 2016324.9616 | 0 | Yes | 0 | 2059123.2775 | 1029561.6387 | 4118246.555 | HR2W | Missing
CA5400873 | UNION SCHOOL | 330 | 1 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2035769.5613 | 0 | Yes | 31619.4 | 2069168.8613 | 1034584.4307 | 4138337.7226 | Not At-Risk | Missing
CA5400882 | PLEASANT VIEW WEST SCHOOL | 220 | 9 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | Yes | 0 | No | 50804.0903 | No | 2026263.3125 | 0 | Yes | 0 | 2077067.4028 | 1038533.7014 | 4154134.8056 | Potentially At-Risk | Missing
CA5400884 | ROCKFORD SCHOOL | 285 | 4 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | Yes | 0 | No | 56335.1236 | No | 2031880.6414 | 0 | Yes | 0 | 2088215.7649 | 1044107.8825 | 4176431.5299 | Not At-Risk | Missing
CA5400886 | COLUMBINE SCHOOL | 250 | 8 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | No | 1779.9 | No | 53356.8749 | No | 2028855.9258 | 0 | Yes | 40414.2 | 2124406.9007 | 1062203.4504 | 4248813.8014 | Not At-Risk | Missing
CA5400919 | BUENA VISTA SCHOOL | 250 | 9 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | Yes | 0 | No | 53356.8749 | Yes | 0 | 0 | Yes | 41670.6 | 95027.4749 | 47513.7374 | 190054.9498 | At-Risk | Missing
CA5400972 | OUTSIDE CREEK SCHOOL | 125 | 2 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | No | 1779.9 | No | 42720.2723 | No | 2018053.3704 | 0 | Yes | 0 | 2062553.5428 | 1031276.7714 | 4125107.0855 | Potentially At-Risk | Missing
CA5400994 | HOPE ELEMENTARY SCHOOL | 275 | 7 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | Yes | 0 | No | 55484.1954 | No | 2031016.4369 | 0 | Yes | 39157.8 | 2125658.4323 | 1062829.2162 | 4251316.8646 | HR2W | Missing
CA5402008 | HOT SPRINGS SCHOOL | 42 | 1 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | No | 1779.9 | No | 35657.5683 | No | 2010880.4736 | 0 | Yes | 0 | 2048317.9419 | 1024158.9709 | 4096635.8837 | Not At-Risk | Missing
CA5403130 | ELEANOR ROOSEVELT COMM LEARNING CTR | 295 | 5 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | No | 1779.9 | No | 57186.0518 | No | 2032744.8458 | 0 | Yes | 36645 | 2128355.7976 | 1064177.8988 | 4256711.5952 | Not At-Risk | Missing
CA5403146 | LIBERTY ELEMENTARY SCHOOL | 500 | 5 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL | Yes | 0 | No | 74630.08 | No | 2050461.0367 | 0 | Yes | 36645 | 2161736.1166 | 1080868.0583 | 4323472.2333 | Not At-Risk | Missing
CA5500148 | CHINESE CAMP SCHOOL | 35 | 1 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | Yes | 0 | No | 35061.9185 | No | 2010275.5305 | 0 | Yes | 0 | 2045337.449 | 1022668.7245 | 4090674.8981 | Not At-Risk | Missing
CA5500152 | CURTIS CREEK ELEMENTARY SCHOOL | 546 | 1 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | No | 78544.3497 | No | 2054436.3771 | 0 | Yes | 0 | 2134760.6268 | 1067380.3134 | 4269521.2535 | Not At-Risk | Missing
CA5500171 | SIERRA OUTDOOR SCHOOL | 283 | 19 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 54234.6 | 56014.5 | 28007.25 | 112029 | Not At-Risk | Missing
CA5500221 | PINECREST ELEMENTARY SCHOOL | 25 | 10 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2009411.3261 | 0 | Yes | 0 | 2011191.2261 | 1005595.613 | 4022382.4522 | Not At-Risk | Missing
CA5500242 | SIERRA WALDORF SCHOOL | 132 | 17 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL | No | 1779.9 | No | 43315.9221 | No | 2018658.3135 | 0 | Yes | 51721.8 | 2115475.9356 | 1057737.9678 | 4230951.8712 | Not At-Risk | Missing
CA5601405 | SANTA CLARA SCHOOL | 39 | 1 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - SCHOOL | No | 2349.468 | No | 46731.0225 | No | 2525340.2426 | 0 | Yes | 0 | 2574420.7332 | 1287210.3666 | 5148841.4663 | Not At-Risk | Missing
CA5602403 | LAGUNA VISTA SCHOOL/OCEANVIEW SCHOOL DIS | 600 | 1 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - SCHOOL | No | 2349.468 | No | 109743.9578 | No | 2586233.4698 | 0 | Yes | 0 | 2698326.8956 | 1349163.4478 | 5396653.7912 | Not At-Risk | Missing
CA5602406 | RIO SCHOOL DIST/RIO DEL VALLE SCHOOL | 820 | 1 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - SCHOOL | N/A | 0 | No | 134454.9128 | N/A | 0 | 0 | Yes | 0 | 134454.9128 | 67227.4564 | 268909.8257 | Not At-Risk | Missing
CA5602407 | RIO MESA HIGH SCHOOL/OXNARD UHS | 2600 | 13 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - SCHOOL | N/A | 0 | No | 334389.0034 | Yes | 0 | 0 | Yes | 0 | 334389.0034 | 167194.5017 | 668778.0069 | At-Risk | Missing
CA5700509 | CLARKSBURG MIDDLE SCHOOL | 460 | 3 | LPA87 - YOLO COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 71226.3671 | No | 2047004.2189 | 0 | Yes | 34132.2 | 2154142.6861 | 1077071.343 | 4308285.3722 | Not At-Risk | Missing
CA5700510 | DELTA HIGH SCHOOL | 250 | 7 | LPA87 - YOLO COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 53356.8749 | No | 2028855.9258 | 0 | Yes | 39157.8 | 2123150.5007 | 1061575.2504 | 4246301.0014 | Not At-Risk | Missing
CA5700623 | DAVIS JUSD - FAIRFIELD SCHOOL | 65 | 1 | LPA87 - YOLO COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 37614.7031 | No | 2012868.1438 | 0 | Yes | 0 | 2052262.7469 | 1026131.3735 | 4104525.4939 | HR2W | Missing
CA5700643 | PLAINFIELD ELEM SCHOOL - WATER | 400 | 17 | LPA87 - YOLO COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | Yes | 0 | No | 2041818.9923 | 0 | Yes | 50465.4 | 2094064.2923 | 1047032.1462 | 4188128.5847 | Not At-Risk | Missing
CA5800006 | YES CHARTER ACADEMY | 125 | 1 | LPA88 - YUBA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 42720.2723 | No | 2018053.3704 | 0 | Yes | 31619.4 | 2094172.9428 | 1047086.4714 | 4188345.8855 | HR2W | Missing
CA5800840 | MJUSD CORDUA SCHOOL | 110 | 3 | LPA88 - YUBA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 41443.88 | No | 2016757.0638 | 0 | Yes | 0 | 2059980.8438 | 1029990.4219 | 4119961.6876 | Not At-Risk | Missing
CA5800843 | MJUSD FOOTHILL INTERMEDIATE SCHOOL | 325 | 2 | LPA88 - YUBA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 59738.8364 | No | 2035337.4591 | 0 | Yes | 0 | 2096856.1955 | 1048428.0977 | 4193712.391 | Not At-Risk | Missing
CA5800844 | MJUSD BROWNS VALLEY SCHOOL | 155 | 5 | LPA88 - YUBA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 45273.0569 | No | 2020645.9837 | 0 | Yes | 36645 | 2104343.9407 | 1052171.9703 | 4208687.8813 | Not At-Risk | Missing
CA5800845 | MJUSD DOBBINS SCHOOL | 85 | 3 | LPA88 - YUBA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 39316.5595 | No | 2014596.5527 | 0 | Yes | 0 | 2055693.0122 | 1027846.5061 | 4111386.0244 | Not At-Risk | Missing
CA5800847 | MJUSD LOMA RICA SCHOOL | 150 | 6 | LPA88 - YUBA COUNTY | NTNC | NT - SCHOOL | No | 1779.9 | No | 44847.5928 | No | 2020213.8815 | 0 | Yes | 0 | 2066841.3744 | 1033420.6872 | 4133682.7487 | Not At-Risk | Missing
CA5200514 | GOLDEN ACRES TRAILER PARK | 18 | 16 | LPA82 - TEHAMA COUNTY | C | MOBILE HOME PARK | No | 1779.9 | Yes | 0 | Yes | 0 | 0 | Yes | 0 | 1779.9 | 889.95 | 3559.8 | Not At-Risk | Missing

## Meters Cost
PWSID | WATER SYSTEM NAME | Total Service Connection | UNMETERED SERVICE CONNECTIONS | Equioment Cost | Cost equipment&Softeware | County | County Multiplier | Cost with Multiplier | Cost before inflation ($) | Final Cost with inflation ($)
CA0400051 | DINGERVILLE USA PARK | 80 | 80 | 96000 | 125000 | BUTTE | 0 | 0 | 125000 | 130875
CA1910012 | BELLFLOWER HOME GARDEN WATER COMPANY | 342 | 335 | 402000 | 431000 | LOS ANGELES | 0.32 | 137920 | 568920 | 595659.24
CA1502315 | CAMP OWEN WATER SYSTEM | 23 | 23 | 27600 | 56600 | KERN | 0 | 0 | 56600 | 59260.2
CA1500447 | SIERRA BREEZE MUTUAL WATER COMPANY | 60 | 60 | 72000 | 101000 | KERN | 0 | 0 | 101000 | 105747
CA3200114 | EVERGREEN MOTEL & MHP | 40 | 40 | 48000 | 77000 | PLUMAS | 0 | 0 | 77000 | 80619
CA2810012 | PACIFIC UNION COLLEGE | 313 | 198 | 237600 | 266600 | NAPA | 0.3 | 79980 | 346580 | 362869.26
CA1009051 | CANTUA CREEK VINEYARDS, IV, LLC. | 16 | 16 | 19200 | 48200 | FRESNO | 0 | 0 | 48200 | 50465.4
CA1910022 | CALIF STATE POLYTECHNICAL UNIV - POMONA | 148 | 91 | 109200 | 138200 | LOS ANGELES | 0.32 | 44224 | 182424 | 190997.928
CA2400053 | EL NIDO MOBILE HOME PARK | 50 | 50 | 60000 | 89000 | MERCED | 0 | 0 | 89000 | 93183
CA3600383 | MWD OF SO CAL GENE PLANT | 61 | 61 | 73200 | 102200 | SAN BERNARDINO | 0.3 | 30660 | 132860 | 139104.42
CA5000048 | LAZY B MOBILEHOME PARK | 49 | 49 | 58800 | 87800 | STANISLAUS | 0 | 0 | 87800 | 91926.6
CA4910701 | U.S. COAST GUARD TRAINING CENTER | 217 | 27 | 32400 | 61400 | SONOMA | 0.3 | 18420 | 79820 | 83571.54
CA2700678 | PARADISE RD WS #05 | 15 | 15 | 18000 | 47000 | MONTEREY | 0.3 | 14100 | 61100 | 63971.7
CA2701647 | GREEN ACRES WA | 20 | 20 | 24000 | 53000 | MONTEREY | 0.3 | 15900 | 68900 | 72138.3
CA0400021 | ROBINSON'S CORNER MHP | 22 | 22 | 26400 | 55400 | BUTTE | 0 | 0 | 55400 | 58003.8
CA5500071 | RAWHIDE INVESTMENT COMPANY | 100 | 100 | 120000 | 149000 | TUOLUMNE | 0 | 0 | 149000 | 156003
CA3900568 | CARIBOU MOBILE PARK PWS | 72 | 72 | 86400 | 115400 | SAN JOAQUIN | 0 | 0 | 115400 | 120823.8
CA3400331 | WESTERNER MOBILE HOME PARK | 49 | 49 | 58800 | 87800 | SACRAMENTO | 0.32 | 28096 | 115896 | 121343.112
CA3400130 | THE COURTLAND GROUP | 34 | 34 | 40800 | 69800 | SACRAMENTO | 0.32 | 22336 | 92136 | 96466.392
CA4500210 | LASSEN PINES MUTUAL WATER CO INC | 198 | 198 | 237600 | 266600 | SHASTA | 0 | 0 | 266600 | 279130.2
CA2710702 | FORT HUNTER LIGGETT | 160 | 160 | 192000 | 221000 | MONTEREY | 0.3 | 66300 | 287300 | 300803.1
CA3600184 | NORTH SHORE MWC | 32 | 32 | 38400 | 67400 | SAN BERNARDINO | 0.3 | 20220 | 87620 | 91738.14
CA3500511 | CASA DE FRUTA ORCHARDS | 20 | 20 | 24000 | 53000 | SAN BENITO | 0.3 | 15900 | 68900 | 72138.3
CA1400020 | ABERDEEN WATER SYSTEM | 75 | 75 | 90000 | 119000 | INYO | 0 | 0 | 119000 | 124593
CA3410022 | OLYMPIA MOBILODGE | 200 | 200 | 240000 | 269000 | SACRAMENTO | 0.32 | 86080 | 355080 | 371768.76
CA1000023 | FCSA #14/BELMONT MANOR | 41 | 41 | 49200 | 78200 | FRESNO | 0 | 0 | 78200 | 81875.4
CA5010029 | CITY OF MODESTO - DEL RIO | 401 | 1 | 1200 | 30200 | STANISLAUS | 0 | 0 | 30200 | 31619.4
CA4900796 | SANTA ROSA MOBILE ESTATES | 141 | 141 | 169200 | 198200 | SONOMA | 0.3 | 59460 | 257660 | 269770.02
CA1000299 | THREE PALMS MOBILEHOME PARK | 105 | 105 | 126000 | 155000 | FRESNO | 0 | 0 | 155000 | 162285
CA1800534 | SPAULDING EAGLE LAKE MWC | 82 | 82 | 98400 | 127400 | LASSEN | 0 | 0 | 127400 | 133387.8
CA1900636 | EL RANCHO MOBILE HOME PARK | 76 | 76 | 91200 | 120200 | LOS ANGELES | 0.32 | 38464 | 158664 | 166121.208
CA5200010 | WOODSON BRIDGE RV PARK | 46 | 46 | 55200 | 84200 | TEHAMA | 0 | 0 | 84200 | 88157.4
CA3810702 | TREASURE ISLAND | 172 | 62 | 74400 | 103400 | SAN FRANCISCO | 0.32 | 33088 | 136488 | 142902.936
CA2000832 | SKP PARK OF THE SIERRAS INC | 261 | 261 | 313200 | 342200 | MADERA | 0 | 0 | 342200 | 358283.4
CA4300792 | ABORN HEIGHTS WATER MUTUAL ASSOCIATION | 19 | 2 | 2400 | 31400 | SANTA CLARA | 0.32 | 10048 | 41448 | 43396.056
CA1500475 | KRISTA MUTUAL WATER COMPANY | 179 | 179 | 214800 | 243800 | KERN | 0 | 0 | 243800 | 255258.6
CA5800863 | FELLOWSHIP OF FRIENDS | 30 | 30 | 36000 | 65000 | YUBA | 0 | 0 | 65000 | 68055
CA3100023 | AUBURN MOBILE HOME VILLAGE | 23 | 23 | 27600 | 56600 | PLACER | 0 | 0 | 56600 | 59260.2
CA1210010 | SCOTIA CSD | 304 | 152 | 182400 | 211400 | HUMBOLDT | 0 | 0 | 211400 | 221335.8
CA1500575 | SAN JOAQUIN ESTATES MUTUAL WATER COMPANY | 61 | 61 | 73200 | 102200 | KERN | 0 | 0 | 102200 | 107003.4
CA5410014 | TIPTON COMMUNITY SERVICES DIST | 608 | 598 | 717600 | 746600 | TULARE | 0 | 0 | 746600 | 781690.2
CA3900719 | MOKELUMNE MOBILE SENIOR PARK | 25 | 25 | 30000 | 59000 | SAN JOAQUIN | 0 | 0 | 59000 | 61773
CA1500507 | ST. CLAIR RANCHOS MUTUAL WATER CO. | 32 | 32 | 38400 | 67400 | KERN | 0 | 0 | 67400 | 70567.8
CA4000648 | KEN MAR GARDENS | 45 | 45 | 54000 | 83000 | SAN LUIS OBISPO | 0.3 | 24900 | 107900 | 112971.3
CA5700554 | CAMPERS INN - RV & GOLF COURSE | 68 | 68 | 81600 | 110600 | YOLO | 0 | 0 | 110600 | 115798.2
CA0300019 | FIDDLETOWN COMMUNITY SERVICE | 66 | 1 | 1200 | 30200 | AMADOR | 0 | 0 | 30200 | 31619.4
CA5500125 | MOTHER LODE MOBILE ESTATES | 75 | 75 | 90000 | 119000 | TUOLUMNE | 0 | 0 | 119000 | 124593
CA3103310 | EMIGRANT GAP MUTUAL WATER CO. | 43 | 43 | 51600 | 80600 | PLACER | 0 | 0 | 80600 | 84388.2
CA3301803 | CASTRO TRAILER PARK | 44 | 44 | 52800 | 81800 | RIVERSIDE | 0.32 | 26176 | 107976 | 113050.872
CA2710005 | CASTROVILLE COMMUNITY SERVICES DISTRICT | 1884 | 225 | 270000 | 299000 | MONTEREY | 0.3 | 89700 | 388700 | 406968.9
CA1400111 | MEADOWCREEK MUTUAL WATER COMPANY | 284 | 273 | 327600 | 356600 | INYO | 0 | 0 | 356600 | 373360.2
CA4500219 | CREEKSIDE MOBILEHOME PARK | 41 | 41 | 49200 | 78200 | SHASTA | 0 | 0 | 78200 | 81875.4
CA4900548 | HOLLAND HEIGHTS MUTUAL WATER COMPANY | 117 | 117 | 140400 | 169400 | SONOMA | 0.3 | 50820 | 220220 | 230570.34
CA2710300 | CSP-PFEIFFER BIG SUR | 129 | 129 | 154800 | 183800 | MONTEREY | 0.3 | 55140 | 238940 | 250170.18
CA4900728 | EVERGREEN MOBILE ESTATES | 23 | 23 | 27600 | 56600 | SONOMA | 0.3 | 16980 | 73580 | 77038.26
CA5710004 | KNIGHTS LANDING SVC. DIST. | 287 | 287 | 344400 | 373400 | YOLO | 0 | 0 | 373400 | 390949.8
CA2701897 | BERRY DR WS #02 | 19 | 19 | 22800 | 51800 | MONTEREY | 0.3 | 15540 | 67340 | 70504.98
CA1500211 | STOCKDALE ANNEX MUTUAL WATER | 143 | 143 | 171600 | 200600 | KERN | 0 | 0 | 200600 | 210028.2
CA1900817 | CLEAR SKIES MOBILE HOME PARK | 47 | 47 | 56400 | 85400 | LOS ANGELES | 0.32 | 27328 | 112728 | 118026.216
CA3310800 | CALIFORNIA REHABILITATION CENTER - NORCO | 1357 | 1355 | 1626000 | 1655000 | RIVERSIDE | 0.32 | 529600 | 2184600 | 2287276.2
CA2702608 | THIMIO MWC | 21 | 21 | 25200 | 54200 | MONTEREY | 0.3 | 16260 | 70460 | 73771.62
CA3610031 | MUSCOY MWC NO. 1 | 1407 | 6 | 7200 | 36200 | SAN BERNARDINO | 0.3 | 10860 | 47060 | 49271.82
CA2600501 | BIRCHIM COMMUNITY SERVICE DISTRICT | 76 | 76 | 91200 | 120200 | MONO | 0 | 0 | 120200 | 125849.4
CA0800548 | KLAMATH C.S.D. | 59 | 16 | 19200 | 48200 | DEL NORTE | 0 | 0 | 48200 | 50465.4
CA1502564 | SIERRA MEADOWS | 51 | 50 | 60000 | 89000 | KERN | 0 | 0 | 89000 | 93183
CA0400027 | FOOTHILL SOLAR COMPANY | 127 | 127 | 152400 | 181400 | BUTTE | 0 | 0 | 181400 | 189925.8
CA3900813 | HAVEN ACRES RIVER CLUB INC | 51 | 51 | 61200 | 90200 | SAN JOAQUIN | 0 | 0 | 90200 | 94439.4
CA2900529 | GOLD COUNTRY HOME PARK - WATER SYSTEM | 27 | 27 | 32400 | 61400 | NEVADA | 0 | 0 | 61400 | 64285.8
CA4300997 | NASA AMES RESEARCH CENTER | 300 | 235 | 282000 | 311000 | SANTA CLARA | 0.32 | 99520 | 410520 | 429814.44
CA5500120 | 49ER TRAILER RANCH | 80 | 48 | 57600 | 86600 | TUOLUMNE | 0 | 0 | 86600 | 90670.2
CA4900587 | BRAND WATER COMPANY | 34 | 34 | 40800 | 69800 | SONOMA | 0.3 | 20940 | 90740 | 95004.78
CA2700541 | DEL MONTE FARMS RD WS #03 | 16 | 16 | 19200 | 48200 | MONTEREY | 0.3 | 14460 | 62660 | 65605.02
CA2700638 | MAHER RD WS #05 | 17 | 17 | 20400 | 49400 | MONTEREY | 0.3 | 14820 | 64220 | 67238.34
CA2700665 | OAK HEIGHTS W & R CO INC | 35 | 35 | 42000 | 71000 | MONTEREY | 0.3 | 21300 | 92300 | 96638.1
CA4710010 | TULELAKE, CITY OF | 471 | 16 | 19200 | 48200 | SISKIYOU | 0 | 0 | 48200 | 50465.4
CA1009232 | SUMNER PECK RANCH | 19 | 19 | 22800 | 51800 | FRESNO | 0 | 0 | 51800 | 54234.6
CA0400014 | LAKE MADRONE WATER DISTRICT | 123 | 1 | 1200 | 30200 | BUTTE | 0 | 0 | 30200 | 31619.4
CA2400201 | VOLTA COMMUNITY SD | 44 | 44 | 52800 | 81800 | MERCED | 0 | 0 | 81800 | 85644.6
CA2700522 | CABANA HOLIDAY WS | 146 | 146 | 175200 | 204200 | MONTEREY | 0.3 | 61260 | 265460 | 277936.62
CA3900733 | COUNTRY CLUB VISTA MUTUAL WATER CO | 31 | 31 | 37200 | 66200 | SAN JOAQUIN | 0 | 0 | 66200 | 69311.4
CA5301103 | COVINGTON MILL - A | 42 | 42 | 50400 | 79400 | TRINITY | 0 | 0 | 79400 | 83131.8
CA2000501 | BASS LAKE ANNEX 3 | 28 | 28 | 33600 | 62600 | MADERA | 0 | 0 | 62600 | 65542.2
CA4900660 | YULUPA MUTUAL WATER COMPANY | 59 | 59 | 70800 | 99800 | SONOMA | 0.3 | 29940 | 129740 | 135837.78
CA1410007 | HIGHLAND MOBILE HOME PARK | 500 | 500 | 600000 | 629000 | INYO | 0 | 0 | 629000 | 658563
CA0510012 | CAMANCHE SOUTH SHORE-EBMUD | 448 | 448 | 537600 | 566600 | CALAVERAS | 0 | 0 | 566600 | 593230.2
CA5500077 | SLIDE INN SNOWBOWL WATER CO | 153 | 124 | 148800 | 177800 | TUOLUMNE | 0 | 0 | 177800 | 186156.6
CA1500561 | ROUND MOUNTAIN WATER COMPANY | 18 | 18 | 21600 | 50600 | KERN | 0 | 0 | 50600 | 52978.2
CA4900599 | RANDAL'S RANCHETTE MUTUAL WATER COMPANY | 29 | 29 | 34800 | 63800 | SONOMA | 0.3 | 19140 | 82940 | 86838.18
CA5301104 | COVINGTON MILL MWC-DIVISION B | 99 | 99 | 118800 | 147800 | TRINITY | 0 | 0 | 147800 | 154746.6
CA5301010 | BUD FINE MWC | 40 | 40 | 48000 | 77000 | TRINITY | 0 | 0 | 77000 | 80619
CA3600166 | MILL CREEK MSC | 72 | 72 | 86400 | 115400 | SAN BERNARDINO | 0.3 | 34620 | 150020 | 157070.94
CA2300731 | CITY OF 10,000 BUDDHAS | 50 | 50 | 60000 | 89000 | MENDOCINO | 0 | 0 | 89000 | 93183
CA3200509 | CLIO PUBLIC UTILITY DISTRICT | 53 | 53 | 63600 | 92600 | PLUMAS | 0 | 0 | 92600 | 96952.2
CA1200588 | SEAWOOD ESTATES MUTUAL WATER COMPANY | 23 | 4 | 4800 | 33800 | HUMBOLDT | 0 | 0 | 33800 | 35388.6
CA5200570 | SURREY VILLAGE WATER CO. INC. | 75 | 75 | 90000 | 119000 | TEHAMA | 0 | 0 | 119000 | 124593
CA5200584 | LITTLE AVENUE WATER SYSTEM | 16 | 16 | 19200 | 48200 | TEHAMA | 0 | 0 | 48200 | 50465.4
CA1500349 | STOCKDALE MUTUAL WATER CO. | 81 | 81 | 97200 | 126200 | KERN | 0 | 0 | 126200 | 132131.4
CA0400019 | OROVILLE MOBILE HOME PARK | 35 | 35 | 42000 | 71000 | BUTTE | 0 | 0 | 71000 | 74337
CA1200643 | BEACH CREEK MOBILE HOME PARK | 24 | 24 | 28800 | 57800 | HUMBOLDT | 0 | 0 | 57800 | 60516.6
CA1410001 | BISHOP, CITY OF | 1158 | 1158 | 1389600 | 1418600 | INYO | 0 | 0 | 1418600 | 1485274.2
CA4500018 | SALT CREEK SUMMER HOMES | 47 | 47 | 56400 | 85400 | SHASTA | 0 | 0 | 85400 | 89413.8
CA3010097 | MIDWAY CITY MUTUAL WC | 198 | 198 | 237600 | 266600 | ORANGE | 0.3 | 79980 | 346580 | 362869.26
CA3910003 | ESCALON, CITY OF | 2510 | 3 | 3600 | 32600 | SAN JOAQUIN | 0 | 0 | 32600 | 34132.2
CA2610003 | BRIDGEPORT PUD | 258 | 258 | 309600 | 338600 | MONO | 0 | 0 | 338600 | 354514.2
CA2701731 | BRANDON CREEK MWS | 26 | 7 | 8400 | 37400 | MONTEREY | 0.3 | 11220 | 48620 | 50905.14
CA5810700 | BEALE AIR FORCE BASE | 841 | 826 | 991200 | 1020200 | YUBA | 0 | 0 | 1020200 | 1068149.4
CA1700579 | VILLA BLUE ESTATES WATER DISTRICT | 21 | 21 | 25200 | 54200 | LAKE | 0 | 0 | 54200 | 56747.4
CA1009179 | BRITZ/FIVE POINT SYSTEM | 23 | 23 | 27600 | 56600 | FRESNO | 0 | 0 | 56600 | 59260.2
CA3301355 | ANZA RV RESORT | 101 | 101 | 121200 | 150200 | RIVERSIDE | 0.32 | 48064 | 198264 | 207582.408
CA3500505 | THOUSAND TRAILS SAN BENITO PRESERVE | 365 | 365 | 438000 | 467000 | SAN BENITO | 0.3 | 140100 | 607100 | 635633.7
CA1800523 | PINEVIEW MOBILE HOME PARK | 52 | 52 | 62400 | 91400 | LASSEN | 0 | 0 | 91400 | 95695.8
CA1500209 | ALTA SIERRA MUTUAL WATER CO. | 225 | 223 | 267600 | 296600 | KERN | 0 | 0 | 296600 | 310540.2
CA4500063 | CEDAR CREEK MOBILEHOME PARK | 20 | 20 | 24000 | 53000 | SHASTA | 0 | 0 | 53000 | 55491
CA2701367 | TIERRA MEADOWS HOA WS | 21 | 21 | 25200 | 54200 | MONTEREY | 0.3 | 16260 | 70460 | 73771.62
CA4710006 | MCCLOUD C.S.D. | 730 | 730 | 876000 | 905000 | SISKIYOU | 0 | 0 | 905000 | 947535
CA2000524 | SKY ACRES MUTUAL WATER CORP | 64 | 64 | 76800 | 105800 | MADERA | 0 | 0 | 105800 | 110772.6
CA3301682 | TRAILS END MUTUAL WATER COMPANY | 34 | 34 | 40800 | 69800 | RIVERSIDE | 0.32 | 22336 | 92136 | 96466.392
CA5402036 | R-RANCH IN THE SEQUOIAS | 115 | 115 | 138000 | 167000 | TULARE | 0 | 0 | 167000 | 174849
CA4900558 | BELMONT TERRACE MUTUAL WATER COMPANY | 87 | 87 | 104400 | 133400 | SONOMA | 0.3 | 40020 | 173420 | 181570.74
CA3900637 | BIG WHEEL MOBILE HOME PARK | 63 | 63 | 75600 | 104600 | SAN JOAQUIN | 0 | 0 | 104600 | 109516.2
CA4300992 | GOLDEN HEIGHTS MUTUAL WATER COMPANY | 21 | 18 | 21600 | 50600 | SANTA CLARA | 0.32 | 16192 | 66792 | 69931.224
CA2701570 | LOS CARNEROS MWA | 24 | 24 | 28800 | 57800 | MONTEREY | 0.3 | 17340 | 75140 | 78671.58
CA5810006 | NORTH YUBA WATER DISTRICT | 785 | 1 | 1200 | 30200 | YUBA | 0 | 0 | 30200 | 31619.4
CA4000653 | RANCHO COLINA MOBILE HOME PARK | 127 | 59 | 70800 | 99800 | SAN LUIS OBISPO | 0.3 | 29940 | 129740 | 135837.78
CA3810003 | HHW&P MOCCASIN COMPOUND-SFPUC | 81 | 33 | 39600 | 68600 | SAN FRANCISCO | 0.32 | 21952 | 90552 | 94807.944
CA4800561 | SNUG HARBOR RESORT | 110 | 108 | 129600 | 158600 | SOLANO | 0.3 | 47580 | 206180 | 215870.46
CA1900794 | ANTELOPE PARK MUTUAL WATER COMPANY | 145 | 145 | 174000 | 203000 | LOS ANGELES | 0.32 | 64960 | 267960 | 280554.12
CA0400041 | FOREST RANCH MOBILE PARK | 16 | 16 | 19200 | 48200 | BUTTE | 0 | 0 | 48200 | 50465.4
CA1810002 | WESTWOOD C.S.D. | 949 | 1 | 1200 | 30200 | LASSEN | 0 | 0 | 30200 | 31619.4
CA2700702 | PRUNEDALE MWC | 84 | 69 | 82800 | 111800 | MONTEREY | 0.3 | 33540 | 145340 | 152170.98
CA2700772 | STRUVE RD WS #02 | 105 | 105 | 126000 | 155000 | MONTEREY | 0.3 | 46500 | 201500 | 210970.5
CA4900673 | ATHENA TERRACE MUTUAL WATER COMPANY | 23 | 21 | 25200 | 54200 | SONOMA | 0.3 | 16260 | 70460 | 73771.62
CA0400026 | MEADOWBROOK OAKS | 26 | 26 | 31200 | 60200 | BUTTE | 0 | 0 | 60200 | 63029.4
CA0310008 | CAMANCHE NORTH SHORE INC. | 211 | 211 | 253200 | 282200 | AMADOR | 0 | 0 | 282200 | 295463.4
CA1900529 | CAMP WILLIAMS-RESORT WATER | 69 | 12 | 14400 | 43400 | LOS ANGELES | 0.32 | 13888 | 57288 | 59980.536
CA4500247 | WEST COTTONWOOD APARTMENTS | 17 | 17 | 20400 | 49400 | SHASTA | 0 | 0 | 49400 | 51721.8
CA5000090 | RIVERVIEW MOBILE HOME ESTATES | 175 | 175 | 210000 | 239000 | STANISLAUS | 0 | 0 | 239000 | 250233
CA5010023 | CITY OF MODESTO - SOUTH TURLOCK | 332 | 2 | 2400 | 31400 | STANISLAUS | 0 | 0 | 31400 | 32875.8
CA4200924 | EL RANCHO TAJIGUAS | 20 | 20 | 24000 | 53000 | SANTA BARBARA | 0.3 | 15900 | 68900 | 72138.3
CA0300011 | SUTTER PINES MHP | 19 | 19 | 22800 | 51800 | AMADOR | 0 | 0 | 51800 | 54234.6
CA3310080 | LAKE HEMET MWD-CAMP GROUND | 287 | 287 | 344400 | 373400 | RIVERSIDE | 0.32 | 119488 | 492888 | 516053.736
CA5700571 | MADISON SERVICE DIST | 149 | 149 | 178800 | 207800 | YOLO | 0 | 0 | 207800 | 217566.6
CA1400078 | SCE BISHOP CREEK PLANT 4 | 15 | 15 | 18000 | 47000 | INYO | 0 | 0 | 47000 | 49209
CA2700594 | HIDDEN VALLEY WA | 32 | 32 | 38400 | 67400 | MONTEREY | 0.3 | 20220 | 87620 | 91738.14
CA4900561 | WILLOWSIDE MUTUAL WATER COMPANY | 160 | 122 | 146400 | 175400 | SONOMA | 0.3 | 52620 | 228020 | 238736.94
CA1510800 | CCI - TEHACHAPI | 1806 | 1806 | 2167200 | 2196200 | KERN | 0 | 0 | 2196200 | 2299421.4
CA1100445 | ORLAND MOBILE H.P. | 54 | 16 | 19200 | 48200 | GLENN | 0 | 0 | 48200 | 50465.4
CA1500458 | R.S. MUTUAL WATER COMPANY | 24 | 24 | 28800 | 57800 | KERN | 0 | 0 | 57800 | 60516.6
CA4300517 | CHEMEKETA PARK MUTUAL WATER COMPANY | 153 | 153 | 183600 | 212600 | SANTA CLARA | 0.32 | 68032 | 280632 | 293821.704
CA4900721 | COLONIAL PARK | 194 | 194 | 232800 | 261800 | SONOMA | 0.3 | 78540 | 340340 | 356335.98
CA1510802 | KERN VALLEY STATE PRISON | 2249 | 2249 | 2698800 | 2727800 | KERN | 0 | 0 | 2727800 | 2856006.6
CA2000527 | YOSEMITE FORKS EST MUTUAL | 99 | 99 | 118800 | 147800 | MADERA | 0 | 0 | 147800 | 154746.6
CA3010008 | EASTSIDE WATER ASSOCIATION | 333 | 333 | 399600 | 428600 | ORANGE | 0.3 | 128580 | 557180 | 583367.46
CA1810004 | LEAVITT LAKE CSD | 259 | 1 | 1200 | 30200 | LASSEN | 0 | 0 | 30200 | 31619.4
CA3710750 | NAS NORTH ISLAND & NAB CORONADO | 1663 | 798 | 957600 | 986600 | SAN DIEGO | 0.32 | 315712 | 1302312 | 1363520.664
CA4500246 | EL RIO ESTATES | 155 | 155 | 186000 | 215000 | SHASTA | 0 | 0 | 215000 | 225105
CA2700536 | CORRAL DE TIERRA ESTATES WC | 16 | 16 | 19200 | 48200 | MONTEREY | 0.3 | 14460 | 62660 | 65605.02
CA5210001 | CITY OF CORNING | 2378 | 10 | 12000 | 41000 | TEHAMA | 0 | 0 | 41000 | 42927
CA4000650 | MESA DUNES MOBILE HOME ESTATES | 313 | 5 | 6000 | 35000 | SAN LUIS OBISPO | 0.3 | 10500 | 45500 | 47638.5
CA5200545 | MODERN VILLAGE MWC | 19 | 19 | 22800 | 51800 | TEHAMA | 0 | 0 | 51800 | 54234.6
CA3610063 | GOLDEN STATE WATER CO - MORONGO DEL SUR | 818 | 3 | 3600 | 32600 | SAN BERNARDINO | 0.3 | 9780 | 42380 | 44371.86
CA5400505 | HARTLAND CHRISTIAN CAMP | 54 | 54 | 64800 | 93800 | TULARE | 0 | 0 | 93800 | 98208.6
CA4500203 | RAPID RIVER MOBILEHOME PARK | 44 | 44 | 52800 | 81800 | SHASTA | 0 | 0 | 81800 | 85644.6
CA3110033 | CASTLE CITY MHP | 201 | 201 | 241200 | 270200 | PLACER | 0 | 0 | 270200 | 282899.4
CA4900723 | SHAMROCK MOBILE HOME PARK | 127 | 127 | 152400 | 181400 | SONOMA | 0.3 | 54420 | 235820 | 246903.54
CA4000802 | SANTA YSABEL RANCH MWC | 151 | 44 | 52800 | 81800 | SAN LUIS OBISPO | 0.3 | 24540 | 106340 | 111337.98
CA2800530 | MEYERS WATER CO. | 92 | 92 | 110400 | 139400 | NAPA | 0.3 | 41820 | 181220 | 189737.34
CA3301380 | SAINT ANTHONY TRAILER PARK | 68 | 68 | 81600 | 110600 | RIVERSIDE | 0.32 | 35392 | 145992 | 152853.624
CA1100452 | SHADY OAKS TRAILER PARK | 43 | 43 | 51600 | 80600 | GLENN | 0 | 0 | 80600 | 84388.2
CA0707623 | WILCOX STATION RANCH | 15 | 15 | 18000 | 47000 | CONTRA COSTA | 0.3 | 14100 | 61100 | 63971.7
CA5000313 | BUEHNER WATER SYSTEM | 50 | 50 | 60000 | 89000 | STANISLAUS | 0 | 0 | 89000 | 93183
CA1000213 | HARRIS FARMS/HORSE BARN | 20 | 20 | 24000 | 53000 | FRESNO | 0 | 0 | 53000 | 55491
CA5400537 | LINDYS LANDING | 177 | 177 | 212400 | 241400 | TULARE | 0 | 0 | 241400 | 252745.8
CA3301280 | GOLDEN ERA PRODUCTIONS | 30 | 30 | 36000 | 65000 | RIVERSIDE | 0.32 | 20800 | 85800 | 89832.6
CA1500459 | LAKE OF THE WOODS MOBILE VILLAGE | 86 | 86 | 103200 | 132200 | KERN | 0 | 0 | 132200 | 138413.4
CA3301226 | MWD - EAGLE MOUNTAIN | 25 | 25 | 30000 | 59000 | RIVERSIDE | 0.32 | 18880 | 77880 | 81540.36
CA2701046 | CAMPHORA APARTMENTS | 42 | 42 | 50400 | 79400 | MONTEREY | 0.3 | 23820 | 103220 | 108071.34
CA1510801 | WASCO ST. PRISON RECEPTION CTR | 1768 | 1765 | 2118000 | 2147000 | KERN | 0 | 0 | 2147000 | 2247909
CA0210002 | KIRKWOOD MEADOWS PUBLIC UTILITY DISTRICT | 863 | 3 | 3600 | 32600 | ALPINE | 0 | 0 | 32600 | 34132.2
CA4200702 | VIEJA MUTUAL WATER COMPANY | 26 | 25 | 30000 | 59000 | SANTA BARBARA | 0.3 | 17700 | 76700 | 80304.9
CA1500380 | DE RANCHO Y MOBILE VILLA WATER | 90 | 90 | 108000 | 137000 | KERN | 0 | 0 | 137000 | 143439
CA3700968 | SAN PASQUAL ACADEMY | 64 | 60 | 72000 | 101000 | SAN DIEGO | 0.32 | 32320 | 133320 | 139586.04
CA3500509 | TRES PINOS CWD | 121 | 108 | 129600 | 158600 | SAN BENITO | 0.3 | 47580 | 206180 | 215870.46
CA3702354 | WARNER SPRINGS ESTATES | 307 | 302 | 362400 | 391400 | SAN DIEGO | 0.32 | 125248 | 516648 | 540930.456
CA1000445 | LINDA VISTA FARMS | 17 | 17 | 20400 | 49400 | FRESNO | 0 | 0 | 49400 | 51721.8
CA5200508 | RIO VISTA MOBILE HOME PARK | 195 | 1 | 1200 | 30200 | TEHAMA | 0 | 0 | 30200 | 31619.4
CA4900644 | BRIDGEHAVEN PARK | 31 | 20 | 24000 | 53000 | SONOMA | 0.3 | 15900 | 68900 | 72138.3
CA1010035 | DEL REY COMMUNITY SERV DIST | 312 | 312 | 374400 | 403400 | FRESNO | 0 | 0 | 403400 | 422359.8
CA0600008 | COLUSA CO. WWD #1 - GRIMES | 123 | 123 | 147600 | 176600 | COLUSA | 0 | 0 | 176600 | 184900.2
CA4900641 | SUNRISE MOUNTAIN MUTUAL WATER COMPANY | 51 | 51 | 61200 | 90200 | SONOMA | 0.3 | 27060 | 117260 | 122771.22
CA5601201 | LIMONEIRA RANCH #1 | 232 | 232 | 278400 | 307400 | VENTURA | 0.32 | 98368 | 405768 | 424839.096
CA0707573 | DELTA MUTUAL WATER COMPANY | 119 | 119 | 142800 | 171800 | CONTRA COSTA | 0.3 | 51540 | 223340 | 233836.98
CA5304502 | SALYER HEIGHTS W.S., INC | 42 | 1 | 1200 | 30200 | TRINITY | 0 | 0 | 30200 | 31619.4
CA3205001 | WALKER RANCH CSD | 1107 | 936 | 1123200 | 1152200 | PLUMAS | 0 | 0 | 1152200 | 1206353.4
CA2300644 | WOODSIDE RV PARK | 58 | 58 | 69600 | 98600 | MENDOCINO | 0 | 0 | 98600 | 103234.2
CA1410800 | CDF - OWENS VALLEY CONSERVATION CAMP | 37 | 37 | 44400 | 73400 | INYO | 0 | 0 | 73400 | 76849.8
CA4901445 | JAMES COURT WATER SYSTEM | 40 | 40 | 48000 | 77000 | SONOMA | 0.3 | 23100 | 100100 | 104804.7
CA2000688 | ECCO | 15 | 15 | 18000 | 47000 | MADERA | 0 | 0 | 47000 | 49209
CA2701403 | PINE ST WS #01 | 17 | 17 | 20400 | 49400 | MONTEREY | 0.3 | 14820 | 64220 | 67238.34
CA4700551 | COPCO LAKE MWC | 61 | 61 | 73200 | 102200 | SISKIYOU | 0 | 0 | 102200 | 107003.4
CA2900530 | ROUGH & READY MOBILEHOME VILLAGE | 56 | 56 | 67200 | 96200 | NEVADA | 0 | 0 | 96200 | 100721.4
CA5510851 | CDCR - SIERRA CONSERVATION CENTER | 578 | 578 | 693600 | 722600 | TUOLUMNE | 0 | 0 | 722600 | 756562.2
CA2410006 | DELHI CWD | 2303 | 1 | 1200 | 30200 | MERCED | 0 | 0 | 30200 | 31619.4
CA3303003 | GALINDO HOUSING FACILITY | 38 | 38 | 45600 | 74600 | RIVERSIDE | 0.32 | 23872 | 98472 | 103100.184
CA1502449 | CYPRESS CANYON WATER SYSTEM | 16 | 16 | 19200 | 48200 | KERN | 0 | 0 | 48200 | 50465.4
CA3700919 | LAKE WOHLFORD RESORT | 137 | 10 | 12000 | 41000 | SAN DIEGO | 0.32 | 13120 | 54120 | 56663.64
CA0900404 | OAKLANE MOBILE VILLAGE, LLC. | 35 | 2 | 2400 | 31400 | EL DORADO | 0.3 | 9420 | 40820 | 42738.54
CA2300638 | WILDWOOD CAMPGROUND | 50 | 50 | 60000 | 89000 | MENDOCINO | 0 | 0 | 89000 | 93183
CA1500543 | AGAPE MUTUAL WATER SYSTEM | 16 | 16 | 19200 | 48200 | KERN | 0 | 0 | 48200 | 50465.4
CA4800531 | VACA VILLA APARTMENTS | 40 | 39 | 46800 | 75800 | SOLANO | 0.3 | 22740 | 98540 | 103171.38
CA1200591 | BIG LAGOON PARK WATER CO. | 76 | 76 | 91200 | 120200 | HUMBOLDT | 0 | 0 | 120200 | 125849.4
CA1800503 | SUSAN RIVER PARK WATER CO. | 50 | 50 | 60000 | 89000 | LASSEN | 0 | 0 | 89000 | 93183
CA4110019 | O'CONNOR TRACT CO-OPERATIVE WATER CO. | 359 | 322 | 386400 | 415400 | SAN MATEO | 0.32 | 132928 | 548328 | 574099.416
CA4210700 | AMERICAN WATER O&M, LLC - VAFB | 1161 | 1118 | 1341600 | 1370600 | SANTA BARBARA | 0.3 | 411180 | 1781780 | 1865523.66
CA3901217 | HAYNES BOARD & CARE HOME | 15 | 15 | 18000 | 47000 | SAN JOAQUIN | 0 | 0 | 47000 | 49209
CA2700674 | PARADISE LAKE MUTUAL WATER CO. | 76 | 76 | 91200 | 120200 | MONTEREY | 0.3 | 36060 | 156260 | 163604.22
CA4100529 | CAMP LOMA MAR | 21 | 5 | 6000 | 35000 | SAN MATEO | 0.32 | 11200 | 46200 | 48371.4
CA4000716 | AVILA VALLEY MUTUAL WATER CO | 29 | 1 | 1200 | 30200 | SAN LUIS OBISPO | 0.3 | 9060 | 39260 | 41105.22
CA1100413 | COUNTRY LEISURE MOBILE ESTATES | 33 | 33 | 39600 | 68600 | GLENN | 0 | 0 | 68600 | 71824.2
CA4700541 | CHATEAU SHASTA MOBILE HOME & RV PARK | 63 | 63 | 75600 | 104600 | SISKIYOU | 0 | 0 | 104600 | 109516.2
CA2300634 | OCEAN'S EDGE ESTATES | 71 | 71 | 85200 | 114200 | MENDOCINO | 0 | 0 | 114200 | 119567.4
CA3601010 | CRYSTAL LAKE PROPERTY OWNERS | 59 | 59 | 70800 | 99800 | SAN BERNARDINO | 0.3 | 29940 | 129740 | 135837.78
CA1500485 | ANTELOPE VALLEY MOBILE ESTATES | 28 | 28 | 33600 | 62600 | KERN | 0 | 0 | 62600 | 65542.2
CA0400040 | ALMOND GROVE MOBILE PARK | 175 | 175 | 210000 | 239000 | BUTTE | 0 | 0 | 239000 | 250233
CA0400023 | GOLDEN OAKS MOBILE ESTATES | 52 | 52 | 62400 | 91400 | BUTTE | 0 | 0 | 91400 | 95695.8
CA5601401 | KROTONA INSTITUTE | 31 | 31 | 37200 | 66200 | VENTURA | 0.32 | 21184 | 87384 | 91491.048
CA3310046 | FARM MUTUAL W.C. (THE) | 1265 | 7 | 8400 | 37400 | RIVERSIDE | 0.32 | 11968 | 49368 | 51688.296
CA5200539 | FRIENDLY ACRES MHP | 51 | 51 | 61200 | 90200 | TEHAMA | 0 | 0 | 90200 | 94439.4
CA2010006 | MADERA CO SA3-PARKSDALE | 542 | 542 | 650400 | 679400 | MADERA | 0 | 0 | 679400 | 711331.8
CA5305103 | MAD RIVER COMPOUND - USFS | 16 | 16 | 19200 | 48200 | TRINITY | 0 | 0 | 48200 | 50465.4
CA1800512 | CLEAR CREEK CSD-WESTWOOD | 166 | 166 | 199200 | 228200 | LASSEN | 0 | 0 | 228200 | 238925.4
CA3600152 | LOMA LINDA UNIVERSITY | 95 | 10 | 12000 | 41000 | SAN BERNARDINO | 0.3 | 12300 | 53300 | 55805.1
CA1100436 | ORLAND OAKS MHP | 83 | 83 | 99600 | 128600 | GLENN | 0 | 0 | 128600 | 134644.2
CA4300912 | MECCHI WATER COMPANY | 27 | 26 | 31200 | 60200 | SANTA CLARA | 0.32 | 19264 | 79464 | 83198.808
CA1500584 | GOOSELAKE WATER COMPANY | 32 | 32 | 38400 | 67400 | KERN | 0 | 0 | 67400 | 70567.8
CA3400169 | SPINDRIFT MARINA | 50 | 50 | 60000 | 89000 | SACRAMENTO | 0.32 | 28480 | 117480 | 123001.56
CA3100029 | TAHOE CITY PUD - TIMBERLAND | 137 | 107 | 128400 | 157400 | PLACER | 0 | 0 | 157400 | 164797.8
CA0707507 | WILLOW PARK MARINA | 125 | 125 | 150000 | 179000 | CONTRA COSTA | 0.3 | 53700 | 232700 | 243636.9
CA1400099 | MOUNTAIN VIEW TRAILER COURT | 24 | 21 | 25200 | 54200 | INYO | 0 | 0 | 54200 | 56747.4
CA1610700 | LEMOORE NAVAL AIR STATION | 1396 | 1247 | 1496400 | 1525400 | KINGS | 0 | 0 | 1525400 | 1597093.8
CA2700792 | SUMMERHILL MHP WS | 34 | 34 | 40800 | 69800 | MONTEREY | 0.3 | 20940 | 90740 | 95004.78
CA2700740 | SAN MIGUEL WS #03 | 16 | 16 | 19200 | 48200 | MONTEREY | 0.3 | 14460 | 62660 | 65605.02
CA0400155 | BIGGERS GLEN MUTUAL WATER CO | 29 | 29 | 34800 | 63800 | BUTTE | 0 | 0 | 63800 | 66798.6
CA4900905 | MARK WEST MEADOWS MUTUAL WATER | 15 | 15 | 18000 | 47000 | SONOMA | 0.3 | 14100 | 61100 | 63971.7
CA2900502 | FLORISTON WATER SYSTEM | 46 | 46 | 55200 | 84200 | NEVADA | 0 | 0 | 84200 | 88157.4
CA1500426 | ROSE VILLA APARTMENTS | 32 | 32 | 38400 | 67400 | KERN | 0 | 0 | 67400 | 70567.8
CA1500571 | KERN MOBILE ESTATES LLC | 60 | 60 | 72000 | 101000 | KERN | 0 | 0 | 101000 | 105747
CA1502232 | ROSAMOND MOBILEHOME PARK | 79 | 79 | 94800 | 123800 | KERN | 0 | 0 | 123800 | 129618.6
CA1910066 | LEISURE LAKE MOBILE ESTATES | 211 | 211 | 253200 | 282200 | LOS ANGELES | 0.32 | 90304 | 372504 | 390011.688
CA2701740 | BLUFFS WS | 44 | 44 | 52800 | 81800 | MONTEREY | 0.3 | 24540 | 106340 | 111337.98
CA3500527 | VALENZUELA WATER SYSTEM | 17 | 17 | 20400 | 49400 | SAN BENITO | 0.3 | 14820 | 64220 | 67238.34
CA3210011 | PLUMAS EUREKA CSD | 554 | 552 | 662400 | 691400 | PLUMAS | 0 | 0 | 691400 | 723895.8
CA3200134 | BLAIRSDEN WATER USERS ASSN | 50 | 50 | 60000 | 89000 | PLUMAS | 0 | 0 | 89000 | 93183
CA4900791 | WESTERN MOBILE HOME PARK | 73 | 73 | 87600 | 116600 | SONOMA | 0.3 | 34980 | 151580 | 158704.26
CA5000058 | FISHERMAN'S BEND MHP | 66 | 66 | 79200 | 108200 | STANISLAUS | 0 | 0 | 108200 | 113285.4
CA1910099 | PARADISE RANCH MHP | 95 | 1 | 1200 | 30200 | LOS ANGELES | 0.32 | 9664 | 39864 | 41737.608
CA1502247 | DESERT BREEZE MOBILE HOME ESTATES | 63 | 63 | 75600 | 104600 | KERN | 0 | 0 | 104600 | 109516.2
CA4500008 | LAKESHORE VILLA MUTUAL WATER CO | 40 | 40 | 48000 | 77000 | SHASTA | 0 | 0 | 77000 | 80619
CA4010832 | ATASCADERO STATE HOSPITAL | 875 | 875 | 1050000 | 1079000 | SAN LUIS OBISPO | 0.3 | 323700 | 1402700 | 1468626.9
CA4110020 | PALO ALTO PARK MUTUAL WATER COMPANY | 692 | 656 | 787200 | 816200 | SAN MATEO | 0.32 | 261184 | 1077384 | 1128021.048
CA0409183 | SIERRA MOON WATER COMPANY | 86 | 86 | 103200 | 132200 | BUTTE | 0 | 0 | 132200 | 138413.4
CA1900046 | PETER PITCHESS HONOR RANCHO DETN. CTR | 1952 | 1952 | 2342400 | 2371400 | LOS ANGELES | 0.32 | 758848 | 3130248 | 3277369.656
CA5602140 | SATICOY COUNTRY CLUB-CITY OF VENTURA | 82 | 8 | 9600 | 38600 | VENTURA | 0.32 | 12352 | 50952 | 53346.744
CA2702439 | WOODLAND HEIGHTS MWC | 37 | 37 | 44400 | 73400 | MONTEREY | 0.3 | 22020 | 95420 | 99904.74
CA5200559 | ABBEY OF NEW CLAIRVAUX | 22 | 22 | 26400 | 55400 | TEHAMA | 0 | 0 | 55400 | 58003.8
CA3910018 | SAN JOAQUIN RIVER CLUB INC | 385 | 385 | 462000 | 491000 | SAN JOAQUIN | 0 | 0 | 491000 | 514077
CA2700992 | MILLER'S LODGE WS | 51 | 51 | 61200 | 90200 | MONTEREY | 0.3 | 27060 | 117260 | 122771.22
CA5200007 | HOWELL'S LAKESIDE WATER CO. | 55 | 55 | 66000 | 95000 | TEHAMA | 0 | 0 | 95000 | 99465
CA1502465 | PANAMA ROAD PROPERTY OWNERS ASSOC | 16 | 16 | 19200 | 48200 | KERN | 0 | 0 | 48200 | 50465.4
CA2000512 | EAST ACRES MUTUAL WATER COMPANY | 85 | 85 | 102000 | 131000 | MADERA | 0 | 0 | 131000 | 137157
CA2000724 | SA 14 CHUK CHANSE SUBDIVISION | 31 | 31 | 37200 | 66200 | MADERA | 0 | 0 | 66200 | 69311.4
CA4500101 | LAKE SHASTA PINES RV PARK & CAMPGROUND | 50 | 50 | 60000 | 89000 | SHASTA | 0 | 0 | 89000 | 93183
CA5000005 | CROWS LANDING COMM SVC DISTRICT | 138 | 138 | 165600 | 194600 | STANISLAUS | 0 | 0 | 194600 | 203746.2
CA4100512 | LOMA MAR MUTUAL | 34 | 34 | 40800 | 69800 | SAN MATEO | 0.32 | 22336 | 92136 | 96466.392
CA5500193 | TAMARRON MOBILE HOME PARK | 100 | 100 | 120000 | 149000 | TUOLUMNE | 0 | 0 | 149000 | 156003
CA2700682 | PARADISE RD WS #09 | 17 | 17 | 20400 | 49400 | MONTEREY | 0.3 | 14820 | 64220 | 67238.34
CA2300743 | DOLPHIN ISLE MARINA | 86 | 86 | 103200 | 132200 | MENDOCINO | 0 | 0 | 132200 | 138413.4
CA3107339 | FOLSOM LAKE MUTUAL WATER CO | 101 | 101 | 121200 | 150200 | PLACER | 0 | 0 | 150200 | 157259.4
CA2300705 | LITTLE LAKE MOBILE HOME PARK | 19 | 1 | 1200 | 30200 | MENDOCINO | 0 | 0 | 30200 | 31619.4
CA4710009 | WEED, CITY OF | 1110 | 19 | 22800 | 51800 | SISKIYOU | 0 | 0 | 51800 | 54234.6
CA0202522 | SIERRA PINES MOBILE HOME PARK | 32 | 32 | 38400 | 67400 | ALPINE | 0 | 0 | 67400 | 70567.8
CA3400135 | KORTHS PIRATES LAIR | 64 | 64 | 76800 | 105800 | SACRAMENTO | 0.32 | 33856 | 139656 | 146219.832
CA0800557 | HUNTER VALLEY CSD | 62 | 62 | 74400 | 103400 | DEL NORTE | 0 | 0 | 103400 | 108259.8
CA2010004 | MADERA CO CMD19-PARKWOOD | 496 | 496 | 595200 | 624200 | MADERA | 0 | 0 | 624200 | 653537.4
CA3701934 | PINE VALLEY BIBLE CONFERENCE CENTER | 57 | 57 | 68400 | 97400 | SAN DIEGO | 0.32 | 31168 | 128568 | 134610.696
CA4900789 | BLUE SPRUCE MOBILE HOME PARK | 56 | 56 | 67200 | 96200 | SONOMA | 0.3 | 28860 | 125060 | 130937.82
CA5410012 | STRATHMORE PUBLIC UTIL DIST | 551 | 550 | 660000 | 689000 | TULARE | 0 | 0 | 689000 | 721383
CA1900541 | WESTERN SKIES MOBILE HOME PARK | 61 | 61 | 73200 | 102200 | LOS ANGELES | 0.32 | 32704 | 134904 | 141244.488
CA2610700 | USMC/MTN WARFARE TRNG CTR - BRIDGEPORT | 30 | 30 | 36000 | 65000 | MONO | 0 | 0 | 65000 | 68055
CA5500096 | SIERRA TWAIN HARTE MHP | 46 | 46 | 55200 | 84200 | TUOLUMNE | 0 | 0 | 84200 | 88157.4
CA5610702 | U.S.N., SAN NICOLAS ISLAND | 106 | 101 | 121200 | 150200 | VENTURA | 0.32 | 48064 | 198264 | 207582.408
CA3600504 | KNOLL ENTERPRISES | 25 | 25 | 30000 | 59000 | SAN BERNARDINO | 0.3 | 17700 | 76700 | 80304.9
CA3500836 | BETABEL RV RESORT | 176 | 176 | 211200 | 240200 | SAN BENITO | 0.3 | 72060 | 312260 | 326936.22
CA1010053 | SHAVER LAKE HEIGHTS MWC | 220 | 220 | 264000 | 293000 | FRESNO | 0 | 0 | 293000 | 306771
CA1700527 | MOUNTAIN OF ATTENTION WATER | 26 | 26 | 31200 | 60200 | LAKE | 0 | 0 | 60200 | 63029.4
CA3900559 | WINE COUNTRY APARTMENTS | 16 | 16 | 19200 | 48200 | SAN JOAQUIN | 0 | 0 | 48200 | 50465.4
CA5000263 | OASIS INVESTMENTS | 31 | 31 | 37200 | 66200 | STANISLAUS | 0 | 0 | 66200 | 69311.4
CA3900983 | CHERRY LANE TRAILER PARK | 43 | 43 | 51600 | 80600 | SAN JOAQUIN | 0 | 0 | 80600 | 84388.2
CA3901114 | KING ISLAND TRAILER PARK WATER SYSTEM | 76 | 76 | 91200 | 120200 | SAN JOAQUIN | 0 | 0 | 120200 | 125849.4
CA5200008 | BREESE SUBDIVISION 2 | 30 | 30 | 36000 | 65000 | TEHAMA | 0 | 0 | 65000 | 68055
CA3400164 | VIEIRA'S RESORT, INC | 107 | 107 | 128400 | 157400 | SACRAMENTO | 0.32 | 50368 | 207768 | 217533.096
CA3900701 | CURRIER ESTATES WATER CORP | 37 | 37 | 44400 | 73400 | SAN JOAQUIN | 0 | 0 | 73400 | 76849.8
CA0910019 | LAKESIDE PARK ASSOCIATION | 139 | 138 | 165600 | 194600 | EL DORADO | 0.3 | 58380 | 252980 | 264870.06
CA5000072 | MULBERRY MHP | 53 | 53 | 63600 | 92600 | STANISLAUS | 0 | 0 | 92600 | 96952.2
CA3301529 | RAMONA WATER COMPANY | 95 | 95 | 114000 | 143000 | RIVERSIDE | 0.32 | 45760 | 188760 | 197631.72
CA1500449 | FOURTH STREET WATER SYSTEM | 28 | 28 | 33600 | 62600 | KERN | 0 | 0 | 62600 | 65542.2
CA3310802 | CHUCKAWALLA VALLEY STATE PRISON | 1864 | 1862 | 2234400 | 2263400 | RIVERSIDE | 0.32 | 724288 | 2987688 | 3128109.336
CA2700709 | RANCHO BORROMEO MWS | 36 | 36 | 43200 | 72200 | MONTEREY | 0.3 | 21660 | 93860 | 98271.42
CA2210002 | PONDEROSA BASIN MUTUAL WTR CO | 314 | 314 | 376800 | 405800 | MARIPOSA | 0 | 0 | 405800 | 424872.6
CA5500080 | TWAIN HARTE VALLEY MWC | 106 | 106 | 127200 | 156200 | TUOLUMNE | 0 | 0 | 156200 | 163541.4
CA2700669 | ORCHARD LN WS #02 | 16 | 16 | 19200 | 48200 | MONTEREY | 0.3 | 14460 | 62660 | 65605.02
CA1100444 | ORLAND ESTATES MOBILE H.P. | 74 | 74 | 88800 | 117800 | GLENN | 0 | 0 | 117800 | 123336.6
CA3110042 | TAHOE SWISS VILLAGE UTILITY | 395 | 384 | 460800 | 489800 | PLACER | 0 | 0 | 489800 | 512820.6
CA1300550 | COUNTRY LIFE MH & RV PARK | 306 | 152 | 182400 | 211400 | IMPERIAL | 0 | 0 | 211400 | 221335.8
CA5500128 | GOLD RUSH MOBILE HOME PARK | 53 | 6 | 7200 | 36200 | TUOLUMNE | 0 | 0 | 36200 | 37901.4
CA4900513 | MADRONE MUTUAL WATER COMPANY | 23 | 18 | 21600 | 50600 | SONOMA | 0.3 | 15180 | 65780 | 68871.66
CA4900792 | WAYSIDE GARDENS MOBILE HOME PARK | 50 | 50 | 60000 | 89000 | SONOMA | 0.3 | 26700 | 115700 | 121137.9
CA3600391 | HILLCREST MOBILE ESTATES | 180 | 180 | 216000 | 245000 | SAN BERNARDINO | 0.3 | 73500 | 318500 | 333469.5
CA5500048 | DON PEDRO REC AG:FLEM.MEADOWS | 18 | 18 | 21600 | 50600 | TUOLUMNE | 0 | 0 | 50600 | 52978.2
CA4300611 | CASA DE FRUTA WATER SYSTEM | 37 | 30 | 36000 | 65000 | SANTA CLARA | 0.32 | 20800 | 85800 | 89832.6
CA1410005 | INDIAN CREEK CSD | 297 | 289 | 346800 | 375800 | INYO | 0 | 0 | 375800 | 393462.6
CA3301294 | GLEN IVY HOT SPRINGS | 49 | 41 | 49200 | 78200 | RIVERSIDE | 0.32 | 25024 | 103224 | 108075.528
CA0410007 | PARADISE IRRIGATION DISTRICT | 2369 | 2369 | 2842800 | 2871800 | BUTTE | 0 | 0 | 2871800 | 3006774.6
CA0707572 | BETHEL ISLAND MUTUAL WATER CO | 45 | 45 | 54000 | 83000 | CONTRA COSTA | 0.3 | 24900 | 107900 | 112971.3
CA1400030 | GLENWOOD MOBILE ESTATES | 170 | 170 | 204000 | 233000 | INYO | 0 | 0 | 233000 | 243951
CA3301990 | AMEZCUA - GARCIA WATER | 113 | 113 | 135600 | 164600 | RIVERSIDE | 0.32 | 52672 | 217272 | 227483.784
CA5601141 | SOUTH MOUNTAIN MUTUAL WATER CO | 27 | 27 | 32400 | 61400 | VENTURA | 0.32 | 19648 | 81048 | 84857.256
CA2702466 | SAN VICENTE MWC | 21 | 21 | 25200 | 54200 | MONTEREY | 0.3 | 16260 | 70460 | 73771.62
CA3110031 | WARD WELL WATER COMPANY | 226 | 226 | 271200 | 300200 | PLACER | 0 | 0 | 300200 | 314309.4
CA1500557 | STOCKDALE RANCHOS MUTUAL WATER CO | 95 | 95 | 114000 | 143000 | KERN | 0 | 0 | 143000 | 149721
CA1500481 | RIVERNOOK CAMPGROUND | 290 | 290 | 348000 | 377000 | KERN | 0 | 0 | 377000 | 394719
CA1500489 | BRITE LAKE MUTUAL WATER COMPANY | 27 | 27 | 32400 | 61400 | KERN | 0 | 0 | 61400 | 64285.8
CA3700074 | CUYAMACA WATER DISTRICT | 159 | 159 | 190800 | 219800 | SAN DIEGO | 0.32 | 70336 | 290136 | 303772.392
CA1100254 | VOYLES TRAILER PARK | 15 | 15 | 18000 | 47000 | GLENN | 0 | 0 | 47000 | 49209
CA2700548 | DOLAN RD MWC | 40 | 26 | 31200 | 60200 | MONTEREY | 0.3 | 18060 | 78260 | 81938.22
CA2700775 | TIERRA VERDE MWC | 16 | 16 | 19200 | 48200 | MONTEREY | 0.3 | 14460 | 62660 | 65605.02
CA2300892 | COVELO MOBILE HOME PARK | 30 | 30 | 36000 | 65000 | MENDOCINO | 0 | 0 | 65000 | 68055
CA5200255 | CORNING RV PARK | 40 | 40 | 48000 | 77000 | TEHAMA | 0 | 0 | 77000 | 80619
CA3600025 | BAR-LEN MWC | 42 | 42 | 50400 | 79400 | SAN BERNARDINO | 0.3 | 23820 | 103220 | 108071.34
CA5200500 | REEDS CREEK ESTATES | 25 | 25 | 30000 | 59000 | TEHAMA | 0 | 0 | 59000 | 61773
CA4100538 | CAMP JONES GULCH | 65 | 65 | 78000 | 107000 | SAN MATEO | 0.32 | 34240 | 141240 | 147878.28
CA3600382 | MWD OF SO CAL IRON MOUNTAIN | 38 | 38 | 45600 | 74600 | SAN BERNARDINO | 0.3 | 22380 | 96980 | 101538.06
CA3500910 | DUNNEVILLE ESTATES CSA #50 | 30 | 30 | 36000 | 65000 | SAN BENITO | 0.3 | 19500 | 84500 | 88471.5
CA1009214 | WESTSIDE HARVESTING | 24 | 24 | 28800 | 57800 | FRESNO | 0 | 0 | 57800 | 60516.6
CA1805004 | CDCR-HIGH DESERT STATE PRISON | 2724 | 2724 | 3268800 | 3297800 | LASSEN | 0 | 0 | 3297800 | 3452796.6
CA5200571 | MOUNTAIN VALLEY APTS & RVP | 47 | 47 | 56400 | 85400 | TEHAMA | 0 | 0 | 85400 | 89413.8
CA2702026 | APRICOT LN WS | 16 | 16 | 19200 | 48200 | MONTEREY | 0.3 | 14460 | 62660 | 65605.02
CA3900602 | TAHAMA VILLAGE MOBILE HOME PARK | 68 | 68 | 81600 | 110600 | SAN JOAQUIN | 0 | 0 | 110600 | 115798.2
CA1900785 | MITCHELL'S AVENUE E MOBILE HOME PARK | 24 | 24 | 28800 | 57800 | LOS ANGELES | 0.32 | 18496 | 76296 | 79881.912
CA4910027 | SONOMA STATE UNIVERSITY | 93 | 65 | 78000 | 107000 | SONOMA | 0.3 | 32100 | 139100 | 145637.7
CA4400598 | PURESOURCE WATER, INC | 77 | 65 | 78000 | 107000 | SANTA CRUZ | 0.3 | 32100 | 139100 | 145637.7
CA3400190 | IMPERIAL MANOR MOBILEHOME COMMUNITY | 186 | 186 | 223200 | 252200 | SACRAMENTO | 0.32 | 80704 | 332904 | 348550.488
CA1300628 | IMPERIAL LAKES INC. | 15 | 15 | 18000 | 47000 | IMPERIAL | 0 | 0 | 47000 | 49209
CA2600621 | WHITE MOUNTAIN MUTUAL WATER COMPANY | 43 | 43 | 51600 | 80600 | MONO | 0 | 0 | 80600 | 84388.2
CA1500289 | ATHAL MUTUAL WATER SYSTEM | 55 | 55 | 66000 | 95000 | KERN | 0 | 0 | 95000 | 99465
CA1500546 | HARVEST MOON MUTUAL WATER CO | 49 | 49 | 58800 | 87800 | KERN | 0 | 0 | 87800 | 91926.6
CA3910020 | STOCKTON VERDE MOBILE HOME PARK | 293 | 10 | 12000 | 41000 | SAN JOAQUIN | 0 | 0 | 41000 | 42927
CA3500524 | RIVER OAKS R.V.P. | 15 | 14 | 16800 | 45800 | SAN BENITO | 0.3 | 13740 | 59540 | 62338.38
CA2610701 | USMC - HOUSING COLEVILLE | 116 | 115 | 138000 | 167000 | MONO | 0 | 0 | 167000 | 174849
CA3200138 | MEADOW EDGE MHP | 31 | 31 | 37200 | 66200 | PLUMAS | 0 | 0 | 66200 | 69311.4
CA4300571 | SULLIVAN MUTUAL WATER | 16 | 16 | 19200 | 48200 | SANTA CLARA | 0.32 | 15424 | 63624 | 66614.328
CA0900102 | GOLD BEACH PARK | 40 | 40 | 48000 | 77000 | EL DORADO | 0.3 | 23100 | 100100 | 104804.7
CA1300546 | GOLD ROCK RANCH | 76 | 76 | 91200 | 120200 | IMPERIAL | 0 | 0 | 120200 | 125849.4
CA3901075 | FAIRWAY ESTATES PWS CSA-18 | 47 | 47 | 56400 | 85400 | SAN JOAQUIN | 0 | 0 | 85400 | 89413.8
CA1400056 | BROOKSIDE ESTATES MUTUAL WATER COMPANY | 21 | 21 | 25200 | 54200 | INYO | 0 | 0 | 54200 | 56747.4
CA3400128 | HAPPY HARBOR (SWS) | 45 | 45 | 54000 | 83000 | SACRAMENTO | 0.32 | 26560 | 109560 | 114709.32
CA1500465 | OAK KNOLLS MUTUAL WATER COMPANY | 47 | 47 | 56400 | 85400 | KERN | 0 | 0 | 85400 | 89413.8
CA4700627 | JUNIPER CREEK ESTATES | 51 | 51 | 61200 | 90200 | SISKIYOU | 0 | 0 | 90200 | 94439.4
CA4300603 | OAK DELL PARK | 53 | 53 | 63600 | 92600 | SANTA CLARA | 0.32 | 29632 | 122232 | 127976.904
CA1010800 | CAL FIRE - MIRAMONTE CONSERVATION CAMP | 19 | 18 | 21600 | 50600 | FRESNO | 0 | 0 | 50600 | 52978.2
CA1300622 | SPORTSMANS PARADISE | 30 | 30 | 36000 | 65000 | IMPERIAL | 0 | 0 | 65000 | 68055
CA3100040 | SHADY GLEN COMM WATER SYSTEM | 121 | 121 | 145200 | 174200 | PLACER | 0 | 0 | 174200 | 182387.4
CA1400070 | SIERRA GRANDE ESTATES MUTUAL WATER CO. | 49 | 49 | 58800 | 87800 | INYO | 0 | 0 | 87800 | 91926.6
CA5400670 | TRIPLE R MUTUAL WATER CO | 154 | 6 | 7200 | 36200 | TULARE | 0 | 0 | 36200 | 37901.4
CA4900640 | SONOMA COUNTY MUTUAL WATER COMPANY | 18 | 18 | 21600 | 50600 | SONOMA | 0.3 | 15180 | 65780 | 68871.66
CA1500378 | MAHER MUTUAL WATER COMPANY | 50 | 50 | 60000 | 89000 | KERN | 0 | 0 | 89000 | 93183
CA3910019 | LINDEN COUNTY WATER DISTRICT | 617 | 4 | 4800 | 33800 | SAN JOAQUIN | 0 | 0 | 33800 | 35388.6
CA5400556 | RIVER RETREAT MUTUAL | 25 | 25 | 30000 | 59000 | TULARE | 0 | 0 | 59000 | 61773
CA3702236 | PALOMAR OBSERVATORY | 27 | 27 | 32400 | 61400 | SAN DIEGO | 0.32 | 19648 | 81048 | 84857.256
CA3301717 | VALLEY VIEW TRAILER PARK | 37 | 37 | 44400 | 73400 | RIVERSIDE | 0.32 | 23488 | 96888 | 101441.736
CA3900649 | GLENWOOD MOBILE HOME PARK | 50 | 50 | 60000 | 89000 | SAN JOAQUIN | 0 | 0 | 89000 | 93183
CA3400217 | HOMETOWN COLONIAL ESTATES LLC | 146 | 146 | 175200 | 204200 | SACRAMENTO | 0.32 | 65344 | 269544 | 282212.568
CA1510004 | CASA LOMA WATER CO, INC. | 248 | 248 | 297600 | 326600 | KERN | 0 | 0 | 326600 | 341950.2
CA4900788 | EL CRYSTAL MOBILE HOME PARK | 57 | 57 | 68400 | 97400 | SONOMA | 0.3 | 29220 | 126620 | 132571.14
CA2300667 | WOODS, THE (MENDOCINO) | 115 | 115 | 138000 | 167000 | MENDOCINO | 0 | 0 | 167000 | 174849
CA2010801 | VALLEY STATE PRISON | 74 | 71 | 85200 | 114200 | MADERA | 0 | 0 | 114200 | 119567.4
CA1010025 | CITY OF PARLIER | 2663 | 15 | 18000 | 47000 | FRESNO | 0 | 0 | 47000 | 49209
CA3700859 | RANCHO DEL CAMPO WATER SYSTEM | 110 | 58 | 69600 | 98600 | SAN DIEGO | 0.32 | 31552 | 130152 | 136269.144
CA4900892 | SUMMIT VIEW RANCH MUTUAL WATER CO. | 24 | 3 | 3600 | 32600 | SONOMA | 0.3 | 9780 | 42380 | 44371.86
CA2701498 | HARBOR VIEW WA | 29 | 29 | 34800 | 63800 | MONTEREY | 0.3 | 19140 | 82940 | 86838.18
CA3200078 | FRCCSD OLD MILL RANCH | 23 | 23 | 27600 | 56600 | PLUMAS | 0 | 0 | 56600 | 59260.2
CA1500461 | FOUNTAIN TRAILER PARK WATER | 33 | 33 | 39600 | 68600 | KERN | 0 | 0 | 68600 | 71824.2
CA5010007 | HILLSVIEW HOMES | 230 | 230 | 276000 | 305000 | STANISLAUS | 0 | 0 | 305000 | 319335
CA1700610 | BELLA LAGO MOBILE HOME PARK | 46 | 46 | 55200 | 84200 | LAKE | 0 | 0 | 84200 | 88157.4
CA5200864 | R-WILD HORSE RANCH | 17 | 17 | 20400 | 49400 | TEHAMA | 0 | 0 | 49400 | 51721.8
CA3200195 | GREENHAVEN HOA | 18 | 18 | 21600 | 50600 | PLUMAS | 0 | 0 | 50600 | 52978.2
CA1000259 | NEW HORIZONS MOBILE/RV PARK | 77 | 77 | 92400 | 121400 | FRESNO | 0 | 0 | 121400 | 127105.8
CA2210903 | FISHCAMP MUTUAL WATER COMPANY | 75 | 75 | 90000 | 119000 | MARIPOSA | 0 | 0 | 119000 | 124593
CA5200512 | BEND MOBILEHOME & RV PARK | 42 | 42 | 50400 | 79400 | TEHAMA | 0 | 0 | 79400 | 83131.8
CA3600155 | RIVER RANCH MHP | 138 | 138 | 165600 | 194600 | SAN BERNARDINO | 0.3 | 58380 | 252980 | 264870.06
CA5610701 | NAVAL BASE VENTURA COUNTY, PORT HUENEME | 609 | 540 | 648000 | 677000 | VENTURA | 0.32 | 216640 | 893640 | 935641.08
CA1900649 | GOLDEN SANDS MOBILE HOME PARK | 152 | 152 | 182400 | 211400 | LOS ANGELES | 0.32 | 67648 | 279048 | 292163.256
CA1600023 | AZCAL MANAGEMENT CO | 21 | 21 | 25200 | 54200 | KINGS | 0 | 0 | 54200 | 56747.4
CA3900805 | MOREHEAD PARK | 113 | 113 | 135600 | 164600 | SAN JOAQUIN | 0 | 0 | 164600 | 172336.2
CA5800832 | CASTLEWOOD MOBILE HOME PARK | 88 | 88 | 105600 | 134600 | YUBA | 0 | 0 | 134600 | 140926.2
CA0800605 | WEST PARK PROPERTIES | 42 | 42 | 50400 | 79400 | DEL NORTE | 0 | 0 | 79400 | 83131.8
CA2400167 | BALLICO CSD | 73 | 73 | 87600 | 116600 | MERCED | 0 | 0 | 116600 | 122080.2
CA4800564 | HIDDEN ACRES TRAILER VILLA | 54 | 54 | 64800 | 93800 | SOLANO | 0.3 | 28140 | 121940 | 127671.18
CA3010093 | EAST ORANGE COUNTY WD - WZ | 16 | 1 | 1200 | 30200 | ORANGE | 0.3 | 9060 | 39260 | 41105.22
CA2300735 | HOLLY RANCH VILLAGE | 19 | 19 | 22800 | 51800 | MENDOCINO | 0 | 0 | 51800 | 54234.6
CA1310008 | WESTMORLAND, CITY OF | 501 | 2 | 2400 | 31400 | IMPERIAL | 0 | 0 | 31400 | 32875.8
CA1502620 | POND MUTUAL WATER COMPANY | 18 | 18 | 21600 | 50600 | KERN | 0 | 0 | 50600 | 52978.2
CA4000568 | SAN SIMEON CSD | 206 | 1 | 1200 | 30200 | SAN LUIS OBISPO | 0.3 | 9060 | 39260 | 41105.22
CA5000237 | NORTH OAKS MUTUAL WATER CO | 78 | 78 | 93600 | 122600 | STANISLAUS | 0 | 0 | 122600 | 128362.2
CA3600262 | SNOWCREST HEIGHTS IMP ASSOC | 125 | 125 | 150000 | 179000 | SAN BERNARDINO | 0.3 | 53700 | 232700 | 243636.9
CA5000016 | OID #41 - MOUNTAIN VIEW | 42 | 42 | 50400 | 79400 | STANISLAUS | 0 | 0 | 79400 | 83131.8
CA5200014 | WILSON ACRES MUTUAL WATER | 28 | 28 | 33600 | 62600 | TEHAMA | 0 | 0 | 62600 | 65542.2
CA5000017 | PARK HEIGHTS MUTUAL WATER CO | 95 | 95 | 114000 | 143000 | STANISLAUS | 0 | 0 | 143000 | 149721
CA3900705 | FINNLEES TRAILER PARK | 26 | 26 | 31200 | 60200 | SAN JOAQUIN | 0 | 0 | 60200 | 63029.4
CA1900038 | LANCASTER PARK MOBILE HOME PARK | 21 | 21 | 25200 | 54200 | LOS ANGELES | 0.32 | 17344 | 71544 | 74906.568
CA1500593 | UPLANDS OF THE KERN MUTUAL WATER COMPANY | 20 | 20 | 24000 | 53000 | KERN | 0 | 0 | 53000 | 55491
CA1700596 | BLUE LAKES VILLAGE | 44 | 44 | 52800 | 81800 | LAKE | 0 | 0 | 81800 | 85644.6
CA1510701 | EDWARDS AFB - MAIN BASE | 1058 | 1058 | 1269600 | 1298600 | KERN | 0 | 0 | 1298600 | 1359634.2
CA3610016 | GLEN MARTIN MWC | 338 | 338 | 405600 | 434600 | SAN BERNARDINO | 0.3 | 130380 | 564980 | 591534.06
CA1000345 | PANOCHE WATER DISTRICT | 46 | 46 | 55200 | 84200 | FRESNO | 0 | 0 | 84200 | 88157.4
CA5500057 | LONG BARN PROPERTY OWNERS | 162 | 162 | 194400 | 223400 | TUOLUMNE | 0 | 0 | 223400 | 233899.8
CA5800850 | REBEL RIDGE VILLAGE | 41 | 16 | 19200 | 48200 | YUBA | 0 | 0 | 48200 | 50465.4
CA3510002 | SAN JUAN BAUTISTA, CITY OF | 834 | 3 | 3600 | 32600 | SAN BENITO | 0.3 | 9780 | 42380 | 44371.86
CA2701822 | ROBLEY PROPERTY MWS | 33 | 33 | 39600 | 68600 | MONTEREY | 0.3 | 20580 | 89180 | 93371.46
CA3400335 | HOLIDAY MOBILE VILLAGE | 115 | 115 | 138000 | 167000 | SACRAMENTO | 0.32 | 53440 | 220440 | 230800.68
CA3110017 | SIERRA LAKES COUNTY WATER DIST | 1223 | 822 | 986400 | 1015400 | PLACER | 0 | 0 | 1015400 | 1063123.8
CA5403084 | FAIRWAY MUTUAL WATER CO | 45 | 45 | 54000 | 83000 | TULARE | 0 | 0 | 83000 | 86901
CA1200501 | ALDERPOINT COUNTY WATER | 79 | 79 | 94800 | 123800 | HUMBOLDT | 0 | 0 | 123800 | 129618.6
CA4300999 | UVAS PINES RV PARK | 43 | 43 | 51600 | 80600 | SANTA CLARA | 0.32 | 25792 | 106392 | 111392.424
CA2700547 | DESMOND RD WS #03 | 19 | 19 | 22800 | 51800 | MONTEREY | 0.3 | 15540 | 67340 | 70504.98
CA0409181 | BLUE OAK TERRACE MUTUAL | 23 | 23 | 27600 | 56600 | BUTTE | 0 | 0 | 56600 | 59260.2
CA1400110 | PARK WEST MUTUAL WATER COMPANY | 67 | 67 | 80400 | 109400 | INYO | 0 | 0 | 109400 | 114541.8
CA4000775 | MUSTANG SPRINGS MUTUAL WATER | 16 | 16 | 19200 | 48200 | SAN LUIS OBISPO | 0.3 | 14460 | 62660 | 65605.02
CA4210005 | SAN VICENTE WATER COMPANY | 278 | 278 | 333600 | 362600 | SANTA BARBARA | 0.3 | 108780 | 471380 | 493534.86
CA4500081 | LAZY LANDING MOBILE HOME PARK | 110 | 110 | 132000 | 161000 | SHASTA | 0 | 0 | 161000 | 168567
CA1400034 | KEOUGH'S HOT SPRINGS | 36 | 36 | 43200 | 72200 | INYO | 0 | 0 | 72200 | 75593.4
CA3900517 | ALMOND PARK WATER SYSTEM | 20 | 20 | 24000 | 53000 | SAN JOAQUIN | 0 | 0 | 53000 | 55491
CA5400940 | SIERRA KING HOMEOWNERS ASSN | 49 | 49 | 58800 | 87800 | TULARE | 0 | 0 | 87800 | 91926.6
CA1400026 | RAWSON CREEK MUTUAL WATER COMPANY | 40 | 40 | 48000 | 77000 | INYO | 0 | 0 | 77000 | 80619
CA1500452 | RIVERDALE VILLAGE | 290 | 290 | 348000 | 377000 | KERN | 0 | 0 | 377000 | 394719
CA4700638 | OAK VALLEY ACRES P.O.A. | 27 | 27 | 32400 | 61400 | SISKIYOU | 0 | 0 | 61400 | 64285.8
CA5800827 | WHISPERING PINES MOBILE HOME PARK | 19 | 19 | 22800 | 51800 | YUBA | 0 | 0 | 51800 | 54234.6
CA1500588 | SON SHINE PROPERTIES | 106 | 106 | 127200 | 156200 | KERN | 0 | 0 | 156200 | 163541.4
CA3301209 | DESERT VIEW TRAILER PARK | 22 | 22 | 26400 | 55400 | RIVERSIDE | 0.32 | 17728 | 73128 | 76565.016
CA3301028 | BALDY MOUNTAIN RANCH | 80 | 50 | 60000 | 89000 | RIVERSIDE | 0.32 | 28480 | 117480 | 123001.56
CA1400135 | WILSON CIRCLE MUTUAL WATER COMPANY | 48 | 48 | 57600 | 86600 | INYO | 0 | 0 | 86600 | 90670.2
CA3900842 | DOUBLE L MOBILE ESTATES | 150 | 150 | 180000 | 209000 | SAN JOAQUIN | 0 | 0 | 209000 | 218823
CA3910701 | DEFENSE DISTRIB. DEPOT, SHARPE SITE | 70 | 70 | 84000 | 113000 | SAN JOAQUIN | 0 | 0 | 113000 | 118311
CA4500194 | VILLAGE GREEN | 32 | 32 | 38400 | 67400 | SHASTA | 0 | 0 | 67400 | 70567.8
CA5403023 | DELFT COLONY WATER | 99 | 99 | 118800 | 147800 | TULARE | 0 | 0 | 147800 | 154746.6
CA2701355 | PRINCES CAMP RESORT WS | 55 | 55 | 66000 | 95000 | MONTEREY | 0.3 | 28500 | 123500 | 129304.5
CA1503475 | WESTERN ACRES MUTUAL WATER COMPANY | 90 | 90 | 108000 | 137000 | KERN | 0 | 0 | 137000 | 143439
CA1300555 | MITCHELLS CAMP FAMILY ASSOC. | 70 | 70 | 84000 | 113000 | IMPERIAL | 0 | 0 | 113000 | 118311
CA0800800 | PINE GROVE TRAILER PARK | 51 | 51 | 61200 | 90200 | DEL NORTE | 0 | 0 | 90200 | 94439.4
CA4500094 | RIVERLAND MOBILEHOME PARK | 93 | 93 | 111600 | 140600 | SHASTA | 0 | 0 | 140600 | 147208.2
CA5000019 | RIVERDALE PARK TRACT CSD | 182 | 180 | 216000 | 245000 | STANISLAUS | 0 | 0 | 245000 | 256515
CA3100069 | AUBURN RIDGE WOODS | 54 | 54 | 64800 | 93800 | PLACER | 0 | 0 | 93800 | 98208.6
CA1009028 | HARRIS FARMS SOUTH #101-144 | 40 | 40 | 48000 | 77000 | FRESNO | 0 | 0 | 77000 | 80619
CA1400066 | ASPENDELL MUTUAL WATER COMPANY | 94 | 94 | 112800 | 141800 | INYO | 0 | 0 | 141800 | 148464.6
CA2701452 | MONTEREY DUNES MWA | 124 | 2 | 2400 | 31400 | MONTEREY | 0.3 | 9420 | 40820 | 42738.54
CA3600064 | CAMP WATERMAN MWC | 30 | 30 | 36000 | 65000 | SAN BERNARDINO | 0.3 | 19500 | 84500 | 88471.5
CA1510703 | CHINA LAKE NAVAL AIR WEAPONS STATION | 1380 | 25 | 30000 | 59000 | KERN | 0 | 0 | 59000 | 61773
CA1000550 | FCSA #44D/MONTE VERDI | 124 | 1 | 1200 | 30200 | FRESNO | 0 | 0 | 30200 | 31619.4
CA3610854 | SEARLES VALLEY MINERALS OPERATIONS INC | 779 | 3 | 3600 | 32600 | SAN BERNARDINO | 0.3 | 9780 | 42380 | 44371.86
CA1009147 | FARMING D | 29 | 29 | 34800 | 63800 | FRESNO | 0 | 0 | 63800 | 66798.6
CA4500062 | LONE TREE MOBILE HOME PARK | 26 | 26 | 31200 | 60200 | SHASTA | 0 | 0 | 60200 | 63029.4
CA3901474 | HESKETT, JOE WATER SYSTEM | 15 | 15 | 18000 | 47000 | SAN JOAQUIN | 0 | 0 | 47000 | 49209
CA3900624 | IL VINETO | 83 | 83 | 99600 | 128600 | SAN JOAQUIN | 0 | 0 | 128600 | 134644.2
CA1700549 | CORINTHIAN BAY MUTUAL WATER COMPANY | 74 | 74 | 88800 | 117800 | LAKE | 0 | 0 | 117800 | 123336.6
CA1900555 | LOS ANGELES, CITY OF - POWER PLANT #1 | 19 | 19 | 22800 | 51800 | LOS ANGELES | 0.32 | 16576 | 68376 | 71589.672
CA1700519 | CRESCENT BAY IMPROVEMENT COMPANY | 24 | 24 | 28800 | 57800 | LAKE | 0 | 0 | 57800 | 60516.6
CA5410801 | PORTERVILLE DEVELOPMENTAL CENTER | 99 | 99 | 118800 | 147800 | TULARE | 0 | 0 | 147800 | 154746.6
CA3410003 | GOLDEN STATE WATER CO - ARDEN WATER SERV | 1716 | 533 | 639600 | 668600 | SACRAMENTO | 0.32 | 213952 | 882552 | 924031.944
CA3110043 | TAHOE CITY PUD - MADDEN CREEK | 183 | 155 | 186000 | 215000 | PLACER | 0 | 0 | 215000 | 225105
CA0707547 | KNIGHTSEN COMMUNITY WATER SYSTEM | 18 | 18 | 21600 | 50600 | CONTRA COSTA | 0.3 | 15180 | 65780 | 68871.66
CA0707501 | ANGLER S RANCH #3 | 32 | 32 | 38400 | 67400 | CONTRA COSTA | 0.3 | 20220 | 87620 | 91738.14
CA5410017 | LONDON COMMUNITY SERV DIST | 320 | 320 | 384000 | 413000 | TULARE | 0 | 0 | 413000 | 432411
CA0400151 | KEEFER CREEK ESTATES | 55 | 55 | 66000 | 95000 | BUTTE | 0 | 0 | 95000 | 99465
CA1500404 | PINEBROOK COMMUNITY WATER WELL | 42 | 42 | 50400 | 79400 | KERN | 0 | 0 | 79400 | 83131.8
CA0707569 | ANGLERS SUBDIVISION 4 | 89 | 89 | 106800 | 135800 | CONTRA COSTA | 0.3 | 40740 | 176540 | 184837.38
CA2910001 | CITY OF GRASS VALLEY | 2486 | 2 | 2400 | 31400 | NEVADA | 0 | 0 | 31400 | 32875.8
CA5700788 | NORTH DAVIS MEADOWS | 96 | 96 | 115200 | 144200 | YOLO | 0 | 0 | 144200 | 150977.4
CA1900976 | THE OAKS | 26 | 26 | 31200 | 60200 | LOS ANGELES | 0.32 | 19264 | 79464 | 83198.808
CA1900158 | LITTLE BALDY WATER | 36 | 36 | 43200 | 72200 | LOS ANGELES | 0.32 | 23104 | 95304 | 99783.288
CA4300615 | THOUSAND TRAILS - MORGAN HILL | 320 | 320 | 384000 | 413000 | SANTA CLARA | 0.32 | 132160 | 545160 | 570782.52
CA2900511 | SHADY LAKE WATER ASSOCIATION | 28 | 28 | 33600 | 62600 | NEVADA | 0 | 0 | 62600 | 65542.2
CA0910007 | LUKINS BROTHERS WATER COMPANY | 982 | 830 | 996000 | 1025000 | EL DORADO | 0.3 | 307500 | 1332500 | 1395127.5
CA3900596 | VILLA CEREZOS | 82 | 82 | 98400 | 127400 | SAN JOAQUIN | 0 | 0 | 127400 | 133387.8
CA1410503 | NPS - DEATH VALLEY, COW CREEK/NEVARES | 61 | 61 | 73200 | 102200 | INYO | 0 | 0 | 102200 | 107003.4
CA3103835 | LAKEVIEW HILLS COMMUNITY ASSOC | 152 | 152 | 182400 | 211400 | PLACER | 0 | 0 | 211400 | 221335.8
CA1010501 | NPS-GRANT GROVE | 100 | 100 | 120000 | 149000 | FRESNO | 0 | 0 | 149000 | 156003
CA2600622 | SIERRA EAST HOA | 30 | 30 | 36000 | 65000 | MONO | 0 | 0 | 65000 | 68055
CA4900665 | RUSSIAN RIVER MUTUAL WATER CO. | 30 | 30 | 36000 | 65000 | SONOMA | 0.3 | 19500 | 84500 | 88471.5
CA1200541 | PHILLIPSVILLE C.S.D. | 66 | 65 | 78000 | 107000 | HUMBOLDT | 0 | 0 | 107000 | 112029
CA4500195 | STARLITE PINES MUTUAL WATER CO INC | 165 | 165 | 198000 | 227000 | SHASTA | 0 | 0 | 227000 | 237669
CA2300668 | POINT CABRILLO HIGHLANDS | 21 | 21 | 25200 | 54200 | MENDOCINO | 0 | 0 | 54200 | 56747.4
CA3400125 | FREEPORT MARINA | 27 | 27 | 32400 | 61400 | SACRAMENTO | 0.32 | 19648 | 81048 | 84857.256
CA4400571 | DAVENPORT COUNTY SANITATION | 108 | 18 | 21600 | 50600 | SANTA CRUZ | 0.3 | 15180 | 65780 | 68871.66
CA1900961 | WINTERHAVEN MOBILE ESTATES | 20 | 20 | 24000 | 53000 | LOS ANGELES | 0.32 | 16960 | 69960 | 73248.12
CA4200616 | SKYLINE PARK | 95 | 95 | 114000 | 143000 | SANTA BARBARA | 0.3 | 42900 | 185900 | 194637.3
CA3600031 | BIG PINE TRACT | 136 | 136 | 163200 | 192200 | SAN BERNARDINO | 0.3 | 57660 | 249860 | 261603.42
CA2700771 | SPRINGFIELD WATER COMPANY | 34 | 34 | 40800 | 69800 | MONTEREY | 0.3 | 20940 | 90740 | 95004.78
CA4910026 | ODD FELLOWS RECREATION CLUB | 268 | 268 | 321600 | 350600 | SONOMA | 0.3 | 105180 | 455780 | 477201.66
CA1210007 | DEL ORO WATER CO-FERNDALE | 785 | 9 | 10800 | 39800 | HUMBOLDT | 0 | 0 | 39800 | 41670.6
CA1400031 | RANCH ROAD ESTATES MUTUAL WATER COMPANY | 27 | 27 | 32400 | 61400 | INYO | 0 | 0 | 61400 | 64285.8
CA4900799 | EL PORTAL MOBILE ESTATES | 122 | 122 | 146400 | 175400 | SONOMA | 0.3 | 52620 | 228020 | 238736.94
CA1500555 | MUSTANG MUTUAL WATER SYSTEM | 51 | 51 | 61200 | 90200 | KERN | 0 | 0 | 90200 | 94439.4
CA3400150 | DELTA CROSSING MHP | 22 | 22 | 26400 | 55400 | SACRAMENTO | 0.32 | 17728 | 73128 | 76565.016
CA4000749 | TERRA DE ORO WATER COMPANY | 17 | 17 | 20400 | 49400 | SAN LUIS OBISPO | 0.3 | 14820 | 64220 | 67238.34
CA5000408 | WESTLEY CSD | 35 | 35 | 42000 | 71000 | STANISLAUS | 0 | 0 | 71000 | 74337
CA3301267 | FISHERMAN'S RETREAT | 172 | 172 | 206400 | 235400 | RIVERSIDE | 0.32 | 75328 | 310728 | 325332.216
CA0800556 | HRC C.S.D. | 54 | 54 | 64800 | 93800 | DEL NORTE | 0 | 0 | 93800 | 98208.6
CA5410022 | CAMP NELSON WATER COMPANY | 301 | 300 | 360000 | 389000 | TULARE | 0 | 0 | 389000 | 407283
CA1200715 | GREEN DIAMOND RESOURCE COMPANY - KORBEL | 18 | 17 | 20400 | 49400 | HUMBOLDT | 0 | 0 | 49400 | 51721.8
CA2701364 | PEDRAZZI MWC | 96 | 96 | 115200 | 144200 | MONTEREY | 0.3 | 43260 | 187460 | 196270.62
CA5000061 | MARTIN'S MOBILE HOME COURT | 20 | 20 | 24000 | 53000 | STANISLAUS | 0 | 0 | 53000 | 55491
CA4500003 | MEL MAR MUTUAL WATER CO | 91 | 91 | 109200 | 138200 | SHASTA | 0 | 0 | 138200 | 144695.4
CA0707598 | CAMINO MOBILEHOME | 75 | 75 | 90000 | 119000 | CONTRA COSTA | 0.3 | 35700 | 154700 | 161970.9
CA1200547 | MILL CREEK M.W.C. | 36 | 36 | 43200 | 72200 | HUMBOLDT | 0 | 0 | 72200 | 75593.4
CA5000060 | CASA DE AMIGOS MOBILE HOME PARK | 73 | 73 | 87600 | 116600 | STANISLAUS | 0 | 0 | 116600 | 122080.2
CA3110013 | TAHOE CITY PUD - TAHOE CEDARS | 1181 | 1135 | 1362000 | 1391000 | PLACER | 0 | 0 | 1391000 | 1456377
CA3301045 | BLYTHE MOBILE HOME ESTATES | 25 | 25 | 30000 | 59000 | RIVERSIDE | 0.32 | 18880 | 77880 | 81540.36
CA4900603 | RIEBLI MUTUAL WATER COMPANY | 47 | 47 | 56400 | 85400 | SONOMA | 0.3 | 25620 | 111020 | 116237.94
CA3301330 | INDIAN OAKS TRAILER PARK | 63 | 63 | 75600 | 104600 | RIVERSIDE | 0.32 | 33472 | 138072 | 144561.384
CA2010009 | BAKMAN WATER-ROLLING HILLS | 339 | 339 | 406800 | 435800 | MADERA | 0 | 0 | 435800 | 456282.6
CA3701961 | PINE VALLEY TRAILER PARK | 92 | 92 | 110400 | 139400 | SAN DIEGO | 0.32 | 44608 | 184008 | 192656.376
CA3610033 | MT BALDY HOMEOWNERS ASSN. | 112 | 110 | 132000 | 161000 | SAN BERNARDINO | 0.3 | 48300 | 209300 | 219137.1
CA3900569 | EL RIO MOBILE HOME PARK | 28 | 28 | 33600 | 62600 | SAN JOAQUIN | 0 | 0 | 62600 | 65542.2
CA1010026 | PINEDALE COUNTY WATER DISTRICT | 2120 | 1990 | 2388000 | 2417000 | FRESNO | 0 | 0 | 2417000 | 2530599
CA4500104 | SUNRISE MOBILEHOME PARK | 16 | 16 | 19200 | 48200 | SHASTA | 0 | 0 | 48200 | 50465.4
CA1000005 | BIG CREEK COMMUNITY SERV DIST | 67 | 13 | 15600 | 44600 | FRESNO | 0 | 0 | 44600 | 46696.2
CA0900422 | CRYSTAL CAVES MHP | 40 | 40 | 48000 | 77000 | EL DORADO | 0.3 | 23100 | 100100 | 104804.7
CA2700612 | LAGUNA SECA WC | 58 | 58 | 69600 | 98600 | MONTEREY | 0.3 | 29580 | 128180 | 134204.46
CA2600699 | CHALFANT VALLEY WEST M.W.C. | 15 | 15 | 18000 | 47000 | MONO | 0 | 0 | 47000 | 49209
CA0400008 | GRAN MUTUAL WATER CO | 105 | 54 | 64800 | 93800 | BUTTE | 0 | 0 | 93800 | 98208.6
CA2600546 | CROWLEY LAKE MUTUAL WATER COMPANY | 57 | 57 | 68400 | 97400 | MONO | 0 | 0 | 97400 | 101977.8
CA3100538 | ROSECREST MUTUAL | 15 | 15 | 18000 | 47000 | PLACER | 0 | 0 | 47000 | 49209
CA1000054 | LAS DELTAS MUTUAL WATER SYSTEM | 107 | 106 | 127200 | 156200 | FRESNO | 0 | 0 | 156200 | 163541.4
CA1200566 | ORLEANS MUTUAL WATER CO. | 38 | 38 | 45600 | 74600 | HUMBOLDT | 0 | 0 | 74600 | 78106.2
CA3900664 | NEW HOPE LANDING GENERAL STORE | 44 | 44 | 52800 | 81800 | SAN JOAQUIN | 0 | 0 | 81800 | 85644.6
CA5710009 | UC - DAVIS | 686 | 401 | 481200 | 510200 | YOLO | 0 | 0 | 510200 | 534179.4
CA1810003 | LASSEN COUNTY WATER DISTRICT #1 | 147 | 147 | 176400 | 205400 | LASSEN | 0 | 0 | 205400 | 215053.8
CA4901309 | HILTON MUTUAL WATER COMPANY | 16 | 15 | 18000 | 47000 | SONOMA | 0.3 | 14100 | 61100 | 63971.7
CA3610703 | USMC - 29 PALMS | 2480 | 2302 | 2762400 | 2791400 | SAN BERNARDINO | 0.3 | 837420 | 3628820 | 3799374.54
CA1500585 | OASIS PROPERTY OWNERS ASSOCIATION | 39 | 39 | 46800 | 75800 | KERN | 0 | 0 | 75800 | 79362.6
CA3400433 | EDGEWATER MOBILE HOME PARK | 22 | 22 | 26400 | 55400 | SACRAMENTO | 0.32 | 17728 | 73128 | 76565.016
CA3301040 | RIVERDALE ESTATES | 186 | 186 | 223200 | 252200 | RIVERSIDE | 0.32 | 80704 | 332904 | 348550.488
CA4500107 | ZUFALL'S MOBILEHOME PARK | 78 | 78 | 93600 | 122600 | SHASTA | 0 | 0 | 122600 | 128362.2
CA3410007 | DEL PASO MANOR COUNTY WATER DI | 1796 | 1694 | 2032800 | 2061800 | SACRAMENTO | 0.32 | 659776 | 2721576 | 2849490.072
CA1100237 | WILLOWS MOBILE HOME COMMUNITY & RV PARK | 87 | 87 | 104400 | 133400 | GLENN | 0 | 0 | 133400 | 139669.8
CA0400036 | MOUNTAIN VIEW MHC LLC | 129 | 129 | 154800 | 183800 | BUTTE | 0 | 0 | 183800 | 192438.6
CA2702325 | FERNWOOD WS | 17 | 17 | 20400 | 49400 | MONTEREY | 0.3 | 14820 | 64220 | 67238.34
CA4500007 | VERDE VALE WATER COMPANY | 108 | 108 | 129600 | 158600 | SHASTA | 0 | 0 | 158600 | 166054.2
CA0500075 | LAKESIDE MOBILE ESTATES | 24 | 24 | 28800 | 57800 | CALAVERAS | 0 | 0 | 57800 | 60516.6
CA0410003 | DURHAM IRRIGATION DISTRICT | 479 | 137 | 164400 | 193400 | BUTTE | 0 | 0 | 193400 | 202489.8
CA1500409 | BROCK MUTUAL WATER COMPANY | 155 | 155 | 186000 | 215000 | KERN | 0 | 0 | 215000 | 225105
CA1000004 | BELMONT WATER CORPORATION | 40 | 40 | 48000 | 77000 | FRESNO | 0 | 0 | 77000 | 80619
CA1000472 | PG&E HELMS SUPPORT FACILITY | 22 | 22 | 26400 | 55400 | FRESNO | 0 | 0 | 55400 | 58003.8
CA5401003 | EAST OROSI CSD | 103 | 103 | 123600 | 152600 | TULARE | 0 | 0 | 152600 | 159772.2
CA3400107 | RIVER'S EDGE MARINA & RESORT | 83 | 83 | 99600 | 128600 | SACRAMENTO | 0.32 | 41152 | 169752 | 177730.344
CA3600187 | OLIVE DELL RANCH | 100 | 100 | 120000 | 149000 | SAN BERNARDINO | 0.3 | 44700 | 193700 | 202803.9
CA3610701 | USMC NEBO (BARSTOW) | 419 | 417 | 500400 | 529400 | SAN BERNARDINO | 0.3 | 158820 | 688220 | 720566.34
CA5800572 | FAIRWAY DOWNS MUTUAL WATER CO | 27 | 27 | 32400 | 61400 | YUBA | 0 | 0 | 61400 | 64285.8
CA1800511 | LAKE FOREST MUTUAL W.C. | 220 | 220 | 264000 | 293000 | LASSEN | 0 | 0 | 293000 | 306771
CA4900639 | REDWOOD HEIGHTS MUTUAL WATER COMPANY | 18 | 18 | 21600 | 50600 | SONOMA | 0.3 | 15180 | 65780 | 68871.66
CA1000369 | ZONNEVELD DAIRY - CEDAR | 15 | 15 | 18000 | 47000 | FRESNO | 0 | 0 | 47000 | 49209
CA1400005 | OWENS VALLEY WATER COMPANY | 111 | 111 | 133200 | 162200 | INYO | 0 | 0 | 162200 | 169823.4
CA4200842 | SAINT MARIE MOBILE HOME PARK | 80 | 80 | 96000 | 125000 | SANTA BARBARA | 0.3 | 37500 | 162500 | 170137.5
CA2701423 | ECHO VALLEY RD WS #05 | 16 | 16 | 19200 | 48200 | MONTEREY | 0.3 | 14460 | 62660 | 65605.02
CA4200862 | MESA HILLS MUTUAL WATER COMPANY | 18 | 2 | 2400 | 31400 | SANTA BARBARA | 0.3 | 9420 | 40820 | 42738.54
CA1310800 | CALIPATRIA STATE PRISON | 2001 | 2001 | 2401200 | 2430200 | IMPERIAL | 0 | 0 | 2430200 | 2544419.4
CA5500353 | SIERRA VILLAGE MOBILE HOME PARK | 30 | 30 | 36000 | 65000 | TUOLUMNE | 0 | 0 | 65000 | 68055
CA0202503 | WOODFORDS MUTUAL WATER COMPANY | 16 | 16 | 19200 | 48200 | ALPINE | 0 | 0 | 48200 | 50465.4
CA5400536 | KINGS RIVER ESTATES MUTUAL WATER COMPANY | 38 | 38 | 45600 | 74600 | TULARE | 0 | 0 | 74600 | 78106.2
CA2700579 | ELKHORN RD WS #04 | 20 | 20 | 24000 | 53000 | MONTEREY | 0.3 | 15900 | 68900 | 72138.3
CA3900543 | MAURLAND MANOR WATER SYSTEM | 28 | 28 | 33600 | 62600 | SAN JOAQUIN | 0 | 0 | 62600 | 65542.2
CA3910010 | SAN JOAQUIN COUNTY - LINCOLN VILLAGE | 1815 | 1790 | 2148000 | 2177000 | SAN JOAQUIN | 0 | 0 | 2177000 | 2279319
CA3901113 | WALNUT ACRES | 32 | 32 | 38400 | 67400 | SAN JOAQUIN | 0 | 0 | 67400 | 70567.8
CA2701295 | ESALEN INSTITUTE WS | 42 | 42 | 50400 | 79400 | MONTEREY | 0.3 | 23820 | 103220 | 108071.34
CA3400137 | LINCOLN CHAN-HOME RANCH | 19 | 19 | 22800 | 51800 | SACRAMENTO | 0.32 | 16576 | 68376 | 71589.672
CA0400020 | PLEASANT GROVE MHP | 88 | 88 | 105600 | 134600 | BUTTE | 0 | 0 | 134600 | 140926.2
CA3500904 | HOLLISTER RANCH ESTATES | 37 | 37 | 44400 | 73400 | SAN BENITO | 0.3 | 22020 | 95420 | 99904.74
CA4500092 | RIVER BREEZE MOBILE HOME PARK | 32 | 32 | 38400 | 67400 | SHASTA | 0 | 0 | 67400 | 70567.8
CA1200706 | TRINIDAD EXTENDED STAY RV | 72 | 72 | 86400 | 115400 | HUMBOLDT | 0 | 0 | 115400 | 120823.8
CA1400004 | CHARLES BROWN WATER COMPANY | 31 | 31 | 37200 | 66200 | INYO | 0 | 0 | 66200 | 69311.4
CA1000378 | SUNSET WEST COMMUNITY LLC | 159 | 159 | 190800 | 219800 | FRESNO | 0 | 0 | 219800 | 230130.6
CA4900871 | DE ANZA MOON VALLEY WATER COMPANY | 247 | 247 | 296400 | 325400 | SONOMA | 0.3 | 97620 | 423020 | 442901.94
CA3900721 | WOODBRIDGE MOBILE ESTATES | 37 | 37 | 44400 | 73400 | SAN JOAQUIN | 0 | 0 | 73400 | 76849.8
CA5601116 | SAN CAYETANO MUTUAL WATER CO | 50 | 7 | 8400 | 37400 | VENTURA | 0.32 | 11968 | 49368 | 51688.296
CA1400144 | SUNLAND VILLAGE MOBILE HOME PARK | 26 | 26 | 31200 | 60200 | INYO | 0 | 0 | 60200 | 63029.4
CA1610001 | ARMONA COMMUNITY SERVICES DIST | 1246 | 1 | 1200 | 30200 | KINGS | 0 | 0 | 30200 | 31619.4
CA3100043 | GOLD HILL MOBILEHOME PARK | 32 | 32 | 38400 | 67400 | PLACER | 0 | 0 | 67400 | 70567.8
CA1009023 | BRITZ/COLUSA | 15 | 15 | 18000 | 47000 | FRESNO | 0 | 0 | 47000 | 49209
CA2910011 | PLAVADA COMMUNITY ASSOCIATION | 255 | 100 | 120000 | 149000 | NEVADA | 0 | 0 | 149000 | 156003
CA1000056 | MEADOW LAKES CLUB | 120 | 120 | 144000 | 173000 | FRESNO | 0 | 0 | 173000 | 181131
CA1910147 | SATIVA WATER SYSTEM | 1643 | 1643 | 1971600 | 2000600 | LOS ANGELES | 0.32 | 640192 | 2640792 | 2764909.224
CA1510002 | BORON CSD | 627 | 3 | 3600 | 32600 | KERN | 0 | 0 | 32600 | 34132.2
CA1310700 | NAF EL CENTRO | 386 | 337 | 404400 | 433400 | IMPERIAL | 0 | 0 | 433400 | 453769.8
CA2701658 | ARROYO CENTER WC | 60 | 60 | 72000 | 101000 | MONTEREY | 0.3 | 30300 | 131300 | 137471.1
CA3400103 | B & W RESORT MARINA | 37 | 37 | 44400 | 73400 | SACRAMENTO | 0.32 | 23488 | 96888 | 101441.736
CA4500255 | SACRAMENTO RIVER RV PARK | 156 | 156 | 187200 | 216200 | SHASTA | 0 | 0 | 216200 | 226361.4
CA5000067 | TULLY MOBILE ESTATES | 15 | 5 | 6000 | 35000 | STANISLAUS | 0 | 0 | 35000 | 36645
CA3600158 | LYTLE SPRINGS WC | 141 | 53 | 63600 | 92600 | SAN BERNARDINO | 0.3 | 27780 | 120380 | 126037.86
CA3900563 | GAYLA MANOR PWS | 54 | 54 | 64800 | 93800 | SAN JOAQUIN | 0 | 0 | 93800 | 98208.6
CA2300708 | RIDGEWOOD WATER SYSTEM | 167 | 167 | 200400 | 229400 | MENDOCINO | 0 | 0 | 229400 | 240181.8
CA3910017 | SAN JOAQUIN COUNTY-MOKELUMNE ACRES | 1151 | 1147 | 1376400 | 1405400 | SAN JOAQUIN | 0 | 0 | 1405400 | 1471453.8
CA3900722 | MORADA ESTATES PWS | 88 | 88 | 105600 | 134600 | SAN JOAQUIN | 0 | 0 | 134600 | 140926.2
CA5200510 | RIVER RANCH MOBILE HOME PARK | 109 | 109 | 130800 | 159800 | TEHAMA | 0 | 0 | 159800 | 167310.6
CA4900687 | BROOKWOOD MOBILE HOME PARK | 202 | 202 | 242400 | 271400 | SONOMA | 0.3 | 81420 | 352820 | 369402.54
CA1900721 | TERRA NOVA MOBILE HOME PARK | 75 | 75 | 90000 | 119000 | LOS ANGELES | 0.32 | 38080 | 157080 | 164462.76
CA1300572 | VALLEY MOBILE HOME PARK | 22 | 4 | 4800 | 33800 | IMPERIAL | 0 | 0 | 33800 | 35388.6
CA4200827 | SANTA YNEZ ROBLAR MOBILE HOME PARK | 19 | 19 | 22800 | 51800 | SANTA BARBARA | 0.3 | 15540 | 67340 | 70504.98
CA5500149 | COLUMBIA MOBILE HOME PARK | 63 | 63 | 75600 | 104600 | TUOLUMNE | 0 | 0 | 104600 | 109516.2
CA4800753 | VINEYARD RV PARK | 360 | 358 | 429600 | 458600 | SOLANO | 0.3 | 137580 | 596180 | 624200.46
CA4300994 | COYOTE VALLEY RV RESORT | 129 | 129 | 154800 | 183800 | SANTA CLARA | 0.32 | 58816 | 242616 | 254018.952
CA3301018 | ANZA PINES MOBILE HOME PARK | 47 | 47 | 56400 | 85400 | RIVERSIDE | 0.32 | 27328 | 112728 | 118026.216
CA4900675 | ROSELAND MOBILE HOME PARK | 70 | 70 | 84000 | 113000 | SONOMA | 0.3 | 33900 | 146900 | 153804.3
CA5100112 | TIERRA BUENA MHP #1 | 17 | 17 | 20400 | 49400 | SUTTER | 0 | 0 | 49400 | 51721.8
CA1310801 | CENTINELA STATE PRISON | 2001 | 2001 | 2401200 | 2430200 | IMPERIAL | 0 | 0 | 2430200 | 2544419.4
CA2700842 | BAUMANN RD WS #01 | 17 | 17 | 20400 | 49400 | MONTEREY | 0.3 | 14820 | 64220 | 67238.34
CA2210905 | MCCLURE BOAT CLUB, INC. | 66 | 65 | 78000 | 107000 | MARIPOSA | 0 | 0 | 107000 | 112029
CA3301863 | OLIVET UNIVERSITY | 48 | 24 | 28800 | 57800 | RIVERSIDE | 0.32 | 18496 | 76296 | 79881.912
CA5201147 | GOLDEN MEADOWS CSD | 49 | 49 | 58800 | 87800 | TEHAMA | 0 | 0 | 87800 | 91926.6
CA1000260 | SANDY CREEK VILLAGE MHP | 45 | 45 | 54000 | 83000 | FRESNO | 0 | 0 | 83000 | 86901
CA5400567 | TOOLEVILLE MUTUAL NON PROFIT WATER ASSOC | 77 | 77 | 92400 | 121400 | TULARE | 0 | 0 | 121400 | 127105.8
CA3301528 | OAK HAVEN ASSOCIATION | 36 | 36 | 43200 | 72200 | RIVERSIDE | 0.32 | 23104 | 95304 | 99783.288
CA1010339 | CALIFORNIA STATE UNIVERSITY FRESNO | 159 | 159 | 190800 | 219800 | FRESNO | 0 | 0 | 219800 | 230130.6
CA3900682 | LOCKEFORD MOBILE HOME PARK WTR SYS | 43 | 43 | 51600 | 80600 | SAN JOAQUIN | 0 | 0 | 80600 | 84388.2
CA1100405 | BLACK BUTTE MOBILE H.P. | 49 | 49 | 58800 | 87800 | GLENN | 0 | 0 | 87800 | 91926.6
CA1900542 | LOS ANGELES, CITY OF - POWER PLANT #2 | 16 | 14 | 16800 | 45800 | LOS ANGELES | 0.32 | 14656 | 60456 | 63297.432
CA0410001 | CITY OF BIGGS | 715 | 247 | 296400 | 325400 | BUTTE | 0 | 0 | 325400 | 340693.8
CA4200531 | RANCHO MARCELINO WATER | 87 | 81 | 97200 | 126200 | SANTA BARBARA | 0.3 | 37860 | 164060 | 171770.82
CA1500535 | MANON MANOR MUTUAL WATER COMPANY | 55 | 55 | 66000 | 95000 | KERN | 0 | 0 | 95000 | 99465
CA0202504 | MARKLEEVILLE WATER CO. | 167 | 167 | 200400 | 229400 | ALPINE | 0 | 0 | 229400 | 240181.8
CA2702405 | JENSEN MHP WS | 26 | 26 | 31200 | 60200 | MONTEREY | 0.3 | 18060 | 78260 | 81938.22
CA4000506 | WOODLAND PARK MUTUAL WATER CO | 162 | 5 | 6000 | 35000 | SAN LUIS OBISPO | 0.3 | 10500 | 45500 | 47638.5
CA5800828 | COUNTRYSIDE MOBILE HOME PARK | 86 | 86 | 103200 | 132200 | YUBA | 0 | 0 | 132200 | 138413.4
CA2702299 | POST RANCH INN WS | 58 | 58 | 69600 | 98600 | MONTEREY | 0.3 | 29580 | 128180 | 134204.46
CA5601106 | FILLMORE WEST MOBILE HOME PARK | 33 | 33 | 39600 | 68600 | VENTURA | 0.32 | 21952 | 90552 | 94807.944
CA2100565 | GREEN GULCH FARM | 17 | 17 | 20400 | 49400 | MARIN | 0.3 | 14820 | 64220 | 67238.34
CA5610700 | NAVAL BASE VENTURA COUNTY, POINT MUGU | 928 | 928 | 1113600 | 1142600 | VENTURA | 0.32 | 365632 | 1508232 | 1579118.904
CA1900062 | LOS ANGELES RESIDENTIAL COMMUNITY FOUNDA | 22 | 22 | 26400 | 55400 | LOS ANGELES | 0.32 | 17728 | 73128 | 76565.016
CA3400106 | EAST WALNUT GROVE [SWS] | 166 | 3 | 3600 | 32600 | SACRAMENTO | 0.32 | 10432 | 43032 | 45054.504
CA3910014 | SAN JOAQUIN COUNTY-RAYMUS VILLAGE | 329 | 328 | 393600 | 422600 | SAN JOAQUIN | 0 | 0 | 422600 | 442462.2
CA3900927 | SPRING CREEK ESTATES PWS | 36 | 36 | 43200 | 72200 | SAN JOAQUIN | 0 | 0 | 72200 | 75593.4
CA3900714 | SUNNYSIDE ESTATES WATER SYSTEM | 21 | 21 | 25200 | 54200 | SAN JOAQUIN | 0 | 0 | 54200 | 56747.4
CA5000066 | MODESTO MOBILE HOME PARK | 150 | 150 | 180000 | 209000 | STANISLAUS | 0 | 0 | 209000 | 218823
CA3900606 | A1 WINSTONS MOBILE HOME PARK | 30 | 30 | 36000 | 65000 | SAN JOAQUIN | 0 | 0 | 65000 | 68055
CA5510016 | SIERRA PARK WATER COMPANY, INC. | 347 | 347 | 416400 | 445400 | TUOLUMNE | 0 | 0 | 445400 | 466333.8
CA2702073 | SAN MIGUEL WS #22 | 31 | 31 | 37200 | 66200 | MONTEREY | 0.3 | 19860 | 86060 | 90104.82
CA1000257 | MT ARARAT MOBILE HOME PARK | 36 | 36 | 43200 | 72200 | FRESNO | 0 | 0 | 72200 | 75593.4
CA4901221 | GRATON MUTUAL (GREEN VALLEY HOA) | 16 | 16 | 19200 | 48200 | SONOMA | 0.3 | 14460 | 62660 | 65605.02
CA3301283 | GLEN EDEN SUN CLUB | 407 | 132 | 158400 | 187400 | RIVERSIDE | 0.32 | 59968 | 247368 | 258994.296
CA1210012 | RIO DELL, CITY OF | 1290 | 1222 | 1466400 | 1495400 | HUMBOLDT | 0 | 0 | 1495400 | 1565683.8
CA3910800 | DEUEL VOCATIONAL INSTITUTION | 1688 | 1687 | 2024400 | 2053400 | SAN JOAQUIN | 0 | 0 | 2053400 | 2149909.8
CA0800552 | NORTHCREST TRAILER CITY | 89 | 89 | 106800 | 135800 | DEL NORTE | 0 | 0 | 135800 | 142182.6
CA2700534 | COLONIAL OAK WC INC | 66 | 66 | 79200 | 108200 | MONTEREY | 0.3 | 32460 | 140660 | 147271.02
CA3400397 | LAGUNA VILLAGE RV PARK | 28 | 28 | 33600 | 62600 | SACRAMENTO | 0.32 | 20032 | 82632 | 86515.704
CA4900634 | HUCKLEBERRY MUTUAL WATER COMPANY | 29 | 29 | 34800 | 63800 | SONOMA | 0.3 | 19140 | 82940 | 86838.18
CA2900523 | WASHINGTON WATER DISTRICT | 115 | 3 | 3600 | 32600 | NEVADA | 0 | 0 | 32600 | 34132.2
CA5400523 | EL MONTE VILLAGE MHP | 47 | 2 | 2400 | 31400 | TULARE | 0 | 0 | 31400 | 32875.8
CA0707556 | SANDMOUND MUTUAL | 103 | 103 | 123600 | 152600 | CONTRA COSTA | 0.3 | 45780 | 198380 | 207703.86
CA2610002 | JUNE LAKE PUD VILLAGE | 293 | 1 | 1200 | 30200 | MONO | 0 | 0 | 30200 | 31619.4
CA4300573 | GREEN ACRES MUTUAL WATER | 19 | 19 | 22800 | 51800 | SANTA CLARA | 0.32 | 16576 | 68376 | 71589.672
CA5200555 | RIO RANCH COMMUNITY SVCS DIST | 30 | 30 | 36000 | 65000 | TEHAMA | 0 | 0 | 65000 | 68055
CA2500911 | I'SOT WELL #3 & #15 | 53 | 53 | 63600 | 92600 | MODOC | 0 | 0 | 92600 | 96952.2
CA4500012 | CASCADE RACQUET CLUB MUTUAL WATER | 27 | 27 | 32400 | 61400 | SHASTA | 0 | 0 | 61400 | 64285.8
CA5500019 | JENNESS PARK CHRISTIAN CAMP | 43 | 43 | 51600 | 80600 | TUOLUMNE | 0 | 0 | 80600 | 84388.2
CA5200527 | HUNTER'S FISHING RESORT | 47 | 47 | 56400 | 85400 | TEHAMA | 0 | 0 | 85400 | 89413.8
CA1000069 | SHAVER LAKE HEIGHTS PROP ASSN | 201 | 201 | 241200 | 270200 | FRESNO | 0 | 0 | 270200 | 282899.4
CA3901276 | HANOT FOUNDATION INC | 15 | 15 | 18000 | 47000 | SAN JOAQUIN | 0 | 0 | 47000 | 49209
CA1500493 | EL ADOBE POA, INC. | 80 | 80 | 96000 | 125000 | KERN | 0 | 0 | 125000 | 130875
CA5101009 | WILDWOOD EAST MUTUAL | 48 | 48 | 57600 | 86600 | SUTTER | 0 | 0 | 86600 | 90670.2
CA5400880 | THE LAKES ASSOCIATION | 161 | 161 | 193200 | 222200 | TULARE | 0 | 0 | 222200 | 232643.4
CA2700634 | CHETMOORE ACRES WA | 25 | 25 | 30000 | 59000 | MONTEREY | 0.3 | 17700 | 76700 | 80304.9
CA3500556 | MISSION FARM R.V. PARK | 173 | 173 | 207600 | 236600 | SAN BENITO | 0.3 | 70980 | 307580 | 322036.26
CA3900835 | WAYSIDE MOTEL APARTMENTS WTR SYS | 25 | 25 | 30000 | 59000 | SAN JOAQUIN | 0 | 0 | 59000 | 61773
CA5000317 | OID #51 - SUNSET OAKS #10 | 82 | 82 | 98400 | 127400 | STANISLAUS | 0 | 0 | 127400 | 133387.8
CA1400045 | PRIMROSE LANE APARTMENTS | 26 | 26 | 31200 | 60200 | INYO | 0 | 0 | 60200 | 63029.4
CA1500560 | KRANENBURG WATER SYSTEM | 15 | 15 | 18000 | 47000 | KERN | 0 | 0 | 47000 | 49209
CA1000021 | FCSA #05/WILDWOOD ISLAND | 149 | 149 | 178800 | 207800 | FRESNO | 0 | 0 | 207800 | 217566.6
CA1400007 | SIERRA HIGHLAND CSD | 215 | 215 | 258000 | 287000 | INYO | 0 | 0 | 287000 | 300489
CA3901304 | ENCLAVE AT THE DELTA | 15 | 15 | 18000 | 47000 | SAN JOAQUIN | 0 | 0 | 47000 | 49209
CA1010030 | TRANQUILLITY IRRIGATION DISTRICT | 340 | 340 | 408000 | 437000 | FRESNO | 0 | 0 | 437000 | 457539
CA1000265 | MARY LOU MOBILE HOME PARK | 34 | 34 | 40800 | 69800 | FRESNO | 0 | 0 | 69800 | 73080.6
CA0300053 | RANCHO DEL ORO | 24 | 24 | 28800 | 57800 | AMADOR | 0 | 0 | 57800 | 60516.6
CA3600446 | UPPER LITTLE BEAR MOUNTAIN CLUB | 36 | 36 | 43200 | 72200 | SAN BERNARDINO | 0.3 | 21660 | 93860 | 98271.42
CA2000538 | CEDAR VALLEY MUTUAL WATER CO | 67 | 67 | 80400 | 109400 | MADERA | 0 | 0 | 109400 | 114541.8
CA0707577 | RIVERVIEW WATER ASSOCIATION | 89 | 89 | 106800 | 135800 | CONTRA COSTA | 0.3 | 40740 | 176540 | 184837.38
CA0707588 | BIG OAK MOBILE HOME PARK WATER | 66 | 66 | 79200 | 108200 | CONTRA COSTA | 0.3 | 32460 | 140660 | 147271.02
CA3301877 | BLOCK 77 WATER COMPANY | 18 | 18 | 21600 | 50600 | RIVERSIDE | 0.32 | 16192 | 66792 | 69931.224
CA1009027 | HARRIS FARMS HEADQUARTERS | 69 | 69 | 82800 | 111800 | FRESNO | 0 | 0 | 111800 | 117054.6
CA1710012 | COBB AREA COUNTY WATER DISTRICT | 1004 | 26 | 31200 | 60200 | LAKE | 0 | 0 | 60200 | 63029.4
CA2410002 | CITY OF DOS PALOS | 2521 | 4 | 4800 | 33800 | MERCED | 0 | 0 | 33800 | 35388.6
CA4900577 | RIO LINDO ADVENTIST ACADEMY | 54 | 54 | 64800 | 93800 | SONOMA | 0.3 | 28140 | 121940 | 127671.18
CA2000775 | OAK CREEK MOBILE HOME PARK | 198 | 198 | 237600 | 266600 | MADERA | 0 | 0 | 266600 | 279130.2
CA1500290 | NORTH MUROC MUTUAL WATER COMPANY | 198 | 198 | 237600 | 266600 | KERN | 0 | 0 | 266600 | 279130.2
CA5800821 | HERITAGE PARK | 20 | 20 | 24000 | 53000 | YUBA | 0 | 0 | 53000 | 55491
CA3400191 | ELEVEN OAKS MOBILE HOME COMMUNITY | 136 | 136 | 163200 | 192200 | SACRAMENTO | 0.32 | 61504 | 253704 | 265628.088
CA4200891 | BOBCAT SPRINGS MUTUAL WATER COMPANY | 47 | 4 | 4800 | 33800 | SANTA BARBARA | 0.3 | 10140 | 43940 | 46005.18
CA2600547 | CROWLEY LAKE TRAILER PARK | 108 | 108 | 129600 | 158600 | MONO | 0 | 0 | 158600 | 166054.2
CA1400027 | CARTAGO MUTUAL WATER COMPANY | 40 | 40 | 48000 | 77000 | INYO | 0 | 0 | 77000 | 80619
CA2010003 | BASS LAKE WATER COMPANY | 1013 | 969 | 1162800 | 1191800 | MADERA | 0 | 0 | 1191800 | 1247814.6
CA5400816 | BEDEL MUTUAL WATER CO | 66 | 66 | 79200 | 108200 | TULARE | 0 | 0 | 108200 | 113285.4
CA1510054 | PINON PINES MWC | 275 | 171 | 205200 | 234200 | KERN | 0 | 0 | 234200 | 245207.4
CA5200012 | VISTA GRANDE WATER SYSTEM | 141 | 141 | 169200 | 198200 | TEHAMA | 0 | 0 | 198200 | 207515.4
CA4400850 | THE WILLOWS RESORT | 69 | 69 | 82800 | 111800 | SANTA CRUZ | 0.3 | 33540 | 145340 | 152170.98
CA3400401 | PLANTATION MOBILE HOME PARK | 44 | 44 | 52800 | 81800 | SACRAMENTO | 0.32 | 26176 | 107976 | 113050.872
CA0707589 | BELLA VISTA WATER SYS | 33 | 33 | 39600 | 68600 | CONTRA COSTA | 0.3 | 20580 | 89180 | 93371.46
CA3901215 | SAN JUAN VISTA | 72 | 72 | 86400 | 115400 | SAN JOAQUIN | 0 | 0 | 115400 | 120823.8
CA5200547 | GATEWAY MOBILE HOME PARK | 32 | 32 | 38400 | 67400 | TEHAMA | 0 | 0 | 67400 | 70567.8
CA3900586 | B&G MOBILE HOME PARK LLC WS | 22 | 22 | 26400 | 55400 | SAN JOAQUIN | 0 | 0 | 55400 | 58003.8
CA3100041 | ALPINE MEADOWS PROPERTY OWNERS ASSO | 129 | 9 | 10800 | 39800 | PLACER | 0 | 0 | 39800 | 41670.6
CA2700766 | STRAWBERRY RD WS #06 | 27 | 27 | 32400 | 61400 | MONTEREY | 0.3 | 18420 | 79820 | 83571.54
CA3900724 | ELKHORN ESTATES WATER SYSTEM | 71 | 70 | 84000 | 113000 | SAN JOAQUIN | 0 | 0 | 113000 | 118311
CA0707594 | CASA MEDANOS WATER SYSTEM | 16 | 16 | 19200 | 48200 | CONTRA COSTA | 0.3 | 14460 | 62660 | 65605.02
CA1502600 | WEGIS MUTUAL WATER COMPANY | 23 | 23 | 27600 | 56600 | KERN | 0 | 0 | 56600 | 59260.2
CA3200189 | VALIVU ESTATES MHP | 19 | 19 | 22800 | 51800 | PLUMAS | 0 | 0 | 51800 | 54234.6
CA0300062 | HOPE FOUNDATION/MORIAH HEIGHTS | 21 | 21 | 25200 | 54200 | AMADOR | 0 | 0 | 54200 | 56747.4
CA4710002 | DUNSMUIR, CITY OF | 1187 | 10 | 12000 | 41000 | SISKIYOU | 0 | 0 | 41000 | 42927
CA3901348 | FAIROAKS PWS #44 | 355 | 113 | 135600 | 164600 | SAN JOAQUIN | 0 | 0 | 164600 | 172336.2
CA0500019 | MINERAL MOUNTAIN MUTUAL WATER | 38 | 38 | 45600 | 74600 | CALAVERAS | 0 | 0 | 74600 | 78106.2
CA0400013 | MERRY MOUNTAIN MUTUAL | 97 | 97 | 116400 | 145400 | BUTTE | 0 | 0 | 145400 | 152233.8
CA3600107 | FOREST PARK MWC | 93 | 93 | 111600 | 140600 | SAN BERNARDINO | 0.3 | 42180 | 182780 | 191370.66
CA1300664 | RIVERFRONT MUTUAL WATER COMPANY | 42 | 15 | 18000 | 47000 | IMPERIAL | 0 | 0 | 47000 | 49209
CA5303002 | INDIAN CREEK TRAILER PARK | 35 | 35 | 42000 | 71000 | TRINITY | 0 | 0 | 71000 | 74337
CA4500027 | BIG SPRINGS MUTUAL WATER SYSTEM | 42 | 42 | 50400 | 79400 | SHASTA | 0 | 0 | 79400 | 83131.8
CA2000533 | SUGAR PINE HOMEOWNERS ASSOC | 58 | 58 | 69600 | 98600 | MADERA | 0 | 0 | 98600 | 103234.2
CA4200572 | LAS POSITAS MUTUAL WATER COMPANY | 62 | 62 | 74400 | 103400 | SANTA BARBARA | 0.3 | 31020 | 134420 | 140737.74
CA2110008 | LAWSON S LANDING | 66 | 66 | 79200 | 108200 | MARIN | 0.3 | 32460 | 140660 | 147271.02
CA5800805 | LAKE FRANCIS MUTUAL WATER COMPANY | 19 | 19 | 22800 | 51800 | YUBA | 0 | 0 | 51800 | 54234.6
CA4400605 | CRESTWOOD HEIGHTS WATER ASSN | 45 | 45 | 54000 | 83000 | SANTA CRUZ | 0.3 | 24900 | 107900 | 112971.3
CA0300024 | TABEAU MOBILE HOME PARK | 22 | 22 | 26400 | 55400 | AMADOR | 0 | 0 | 55400 | 58003.8
CA1010005 | FIREBAUGH CITY | 1642 | 159 | 190800 | 219800 | FRESNO | 0 | 0 | 219800 | 230130.6
CA3901081 | MOBILE VILLAS TRAILER PARK | 36 | 35 | 42000 | 71000 | SAN JOAQUIN | 0 | 0 | 71000 | 74337
CA3400101 | HOOD WATER MAINTENCE DIST [SWS] | 82 | 8 | 9600 | 38600 | SACRAMENTO | 0.32 | 12352 | 50952 | 53346.744
CA1100711 | BUTTE CITY COMMUNITY S.D. | 48 | 48 | 57600 | 86600 | GLENN | 0 | 0 | 86600 | 90670.2
CA4000771 | RANCHO NIPOMO WATER COMPANY | 44 | 11 | 13200 | 42200 | SAN LUIS OBISPO | 0.3 | 12660 | 54860 | 57438.42
CA5610001 | DEMPSEY ROAD MUTUAL WATER CO | 301 | 301 | 361200 | 390200 | VENTURA | 0.32 | 124864 | 515064 | 539272.008
CA3810700 | PRESIDIO OF SAN FRANCISCO | 1219 | 13 | 15600 | 44600 | SAN FRANCISCO | 0.32 | 14272 | 58872 | 61638.984
CA4900547 | END-O-VALLEY MUTUAL WATER COMPANY | 39 | 39 | 46800 | 75800 | SONOMA | 0.3 | 22740 | 98540 | 103171.38
CA3301171 | BRADFORD RUN RV | 59 | 59 | 70800 | 99800 | RIVERSIDE | 0.32 | 31936 | 131736 | 137927.592
CA1700630 | PIER 1900 HOMEOWNER S ASSOCIATION | 54 | 54 | 64800 | 93800 | LAKE | 0 | 0 | 93800 | 98208.6
CA5200645 | SADDLEBACK MUTUAL WATER CO. | 38 | 38 | 45600 | 74600 | TEHAMA | 0 | 0 | 74600 | 78106.2
CA5410001 | CUTLER PUD | 1218 | 1204 | 1444800 | 1473800 | TULARE | 0 | 0 | 1473800 | 1543068.6
CA3000618 | LIBERTY PARK WATER ASSOCIATION | 27 | 27 | 32400 | 61400 | ORANGE | 0.3 | 18420 | 79820 | 83571.54
CA3900964 | SAHARA MOBILE COURT | 162 | 162 | 194400 | 223400 | SAN JOAQUIN | 0 | 0 | 223400 | 233899.8
CA3610082 | SAN ANTONIO CANYON MSC | 64 | 62 | 74400 | 103400 | SAN BERNARDINO | 0.3 | 31020 | 134420 | 140737.74
CA5601144 | RANCHO SESPE WORKERS IMP ASSOC | 109 | 108 | 129600 | 158600 | VENTURA | 0.32 | 50752 | 209352 | 219191.544
CA1900975 | CALI LAKE RV RESORT | 47 | 47 | 56400 | 85400 | LOS ANGELES | 0.32 | 27328 | 112728 | 118026.216
CA4900510 | SOUTH CLOVERDALE WATER COMPANY | 39 | 39 | 46800 | 75800 | SONOMA | 0.3 | 22740 | 98540 | 103171.38
CA3901303 | ACAMPO WATER SYSTEM | 70 | 70 | 84000 | 113000 | SAN JOAQUIN | 0 | 0 | 113000 | 118311
CA1900843 | CALIFORNIAN MOBILE HOME PARK | 133 | 133 | 159600 | 188600 | LOS ANGELES | 0.32 | 60352 | 248952 | 260652.744
CA2800527 | LINDA FALLS TERRACE MUTUAL | 17 | 1 | 1200 | 30200 | NAPA | 0.3 | 9060 | 39260 | 41105.22
CA5000218 | COUNTRY VILLA APTS | 23 | 23 | 27600 | 56600 | STANISLAUS | 0 | 0 | 56600 | 59260.2
CA3400122 | EL DORADO WEST MHP | 128 | 128 | 153600 | 182600 | SACRAMENTO | 0.32 | 58432 | 241032 | 252360.504
CA3410026 | CALIFORNIA STATE FAIR | 269 | 269 | 322800 | 351800 | SACRAMENTO | 0.32 | 112576 | 464376 | 486201.672
CA1400037 | FOOTHILL MOBILE HOME PARK | 48 | 48 | 57600 | 86600 | INYO | 0 | 0 | 86600 | 90670.2
CA1000298 | WOODWARD BLUFFS MHP | 172 | 172 | 206400 | 235400 | FRESNO | 0 | 0 | 235400 | 246463.8
CA3400181 | LAGUNA DEL SOL INC | 112 | 112 | 134400 | 163400 | SACRAMENTO | 0.32 | 52288 | 215688 | 225825.336
CA0400081 | FEATHER RIDGE ESTATES WATER CO | 32 | 32 | 38400 | 67400 | BUTTE | 0 | 0 | 67400 | 70567.8
CA3000825 | SOUTH MIDWAY CITY MUTUAL WATER CO. | 56 | 56 | 67200 | 96200 | ORANGE | 0.3 | 28860 | 125060 | 130937.82
CA3110048 | PLACER CSA - SHERIDAN | 196 | 196 | 235200 | 264200 | PLACER | 0 | 0 | 264200 | 276617.4
CA5200526 | HIDDEN HARBOR MARINA & RVP | 70 | 70 | 84000 | 113000 | TEHAMA | 0 | 0 | 113000 | 118311
CA2700535 | JOST POST WA | 20 | 20 | 24000 | 53000 | MONTEREY | 0.3 | 15900 | 68900 | 72138.3
CA1500542 | WILLOW SPRINGS MOBILE HOME PARK | 104 | 104 | 124800 | 153800 | KERN | 0 | 0 | 153800 | 161028.6
CA2700503 | ASSISI MWC | 42 | 41 | 49200 | 78200 | MONTEREY | 0.3 | 23460 | 101660 | 106438.02
CA3710707 | USN SAN CLEMENTE ISLAND | 267 | 113 | 135600 | 164600 | SAN DIEGO | 0.32 | 52672 | 217272 | 227483.784
CA2010010 | MADERA VALLEY WATER COMPANY | 1944 | 1891 | 2269200 | 2298200 | MADERA | 0 | 0 | 2298200 | 2406215.4
CA4300909 | LICK OBSERVATORY-UCSC | 32 | 32 | 38400 | 67400 | SANTA CLARA | 0.32 | 21568 | 88968 | 93149.496
CA5010031 | CITY OF MODESTO - WALNUT MANOR | 53 | 6 | 7200 | 36200 | STANISLAUS | 0 | 0 | 36200 | 37901.4
CA4700503 | CALLAHAN WATER DISTRICT | 34 | 34 | 40800 | 69800 | SISKIYOU | 0 | 0 | 69800 | 73080.6
CA1010013 | HUME LAKE CHRISTIAN CAMPS, INC | 388 | 388 | 465600 | 494600 | FRESNO | 0 | 0 | 494600 | 517846.2
CA0300037 | JACKSON VALLEY IRRIGATION DISTRICT | 331 | 191 | 229200 | 258200 | AMADOR | 0 | 0 | 258200 | 270335.4
CA4700531 | TENNANT C.S.D. | 102 | 102 | 122400 | 151400 | SISKIYOU | 0 | 0 | 151400 | 158515.8
CA3110022 | MCKINNEY WATER DISTRICT | 253 | 253 | 303600 | 332600 | PLACER | 0 | 0 | 332600 | 348232.2
CA4400625 | VISTA ROBLES ASSOCIATION | 19 | 1 | 1200 | 30200 | SANTA CRUZ | 0.3 | 9060 | 39260 | 41105.22
CA5400542 | DUCOR CSD | 166 | 166 | 199200 | 228200 | TULARE | 0 | 0 | 228200 | 238925.4
CA1700674 | WALNUT COVE MOBILE ESTATES | 60 | 60 | 72000 | 101000 | LAKE | 0 | 0 | 101000 | 105747
CA4700626 | COVE MOBILE VILLA | 47 | 47 | 56400 | 85400 | SISKIYOU | 0 | 0 | 85400 | 89413.8
CA0400001 | YOUTH WITH A MISSION-SPRINGS OF LIVING W | 52 | 52 | 62400 | 91400 | BUTTE | 0 | 0 | 91400 | 95695.8
CA1502056 | CLARK STREET COMMUNITY WELL | 20 | 20 | 24000 | 53000 | KERN | 0 | 0 | 53000 | 55491
CA1700508 | GLENHAVEN MUTUAL WATER COMPANY | 131 | 131 | 157200 | 186200 | LAKE | 0 | 0 | 186200 | 194951.4
CA4710001 | DORRIS, CITY OF | 420 | 410 | 492000 | 521000 | SISKIYOU | 0 | 0 | 521000 | 545487
CA4700872 | MONTE SHASTA M.W.C. | 46 | 1 | 1200 | 30200 | SISKIYOU | 0 | 0 | 30200 | 31619.4
CA5200521 | ANTELOPE CREEK MHP | 60 | 60 | 72000 | 101000 | TEHAMA | 0 | 0 | 101000 | 105747
CA1000229 | GREEN ACRES MOBILE HOME ESTATE | 113 | 113 | 135600 | 164600 | FRESNO | 0 | 0 | 164600 | 172336.2
CA2700738 | SAN MIGUEL WS #01 | 34 | 34 | 40800 | 69800 | MONTEREY | 0.3 | 20940 | 90740 | 95004.78
CA4900552 | MICHELE MUTUAL WATER COMPANY | 62 | 62 | 74400 | 103400 | SONOMA | 0.3 | 31020 | 134420 | 140737.74
CA2300646 | BELLA SHORES MOBILE HOME PARK | 60 | 60 | 72000 | 101000 | MENDOCINO | 0 | 0 | 101000 | 105747
CA2000506 | SIERRA LINDA MUTUAL WATER CO | 89 | 89 | 106800 | 135800 | MADERA | 0 | 0 | 135800 | 142182.6
CA2410007 | PLANADA CSD | 1097 | 22 | 26400 | 55400 | MERCED | 0 | 0 | 55400 | 58003.8
CA4900795 | STONEGATE MOBILE HOME PARK | 75 | 75 | 90000 | 119000 | SONOMA | 0.3 | 35700 | 154700 | 161970.9
CA3900661 | MAPACHE TRAILER PARK | 99 | 99 | 118800 | 147800 | SAN JOAQUIN | 0 | 0 | 147800 | 154746.6
CA0900300 | KYBURZ MUTUAL WATER COMPANY | 118 | 118 | 141600 | 170600 | EL DORADO | 0.3 | 51180 | 221780 | 232203.66
CA3601045 | BEAR VALLEY MHP | 98 | 68 | 81600 | 110600 | SAN BERNARDINO | 0.3 | 33180 | 143780 | 150537.66
CA4400582 | PINE TREE LANE MUTUAL WATER CO | 36 | 35 | 42000 | 71000 | SANTA CRUZ | 0.3 | 21300 | 92300 | 96638.1
CA3600308 | FREEDOM ACRES THE RESORT | 100 | 100 | 120000 | 149000 | SAN BERNARDINO | 0.3 | 44700 | 193700 | 202803.9
CA2410700 | CASTLE AIRPORT | 134 | 5 | 6000 | 35000 | MERCED | 0 | 0 | 35000 | 36645
CA3410032 | FOLSOM STATE PRISON | 2790 | 2790 | 3348000 | 3377000 | SACRAMENTO | 0.32 | 1080640 | 4457640 | 4667149.08
CA3010071 | JOINT REGIONAL WATER SUPPLY SYSTEM | 42 | 2 | 2400 | 31400 | ORANGE | 0.3 | 9420 | 40820 | 42738.54
CA2600532 | LUNDY MUTUAL WATER COMPANY | 32 | 32 | 38400 | 67400 | MONO | 0 | 0 | 67400 | 70567.8
CA1400072 | NORTH LONE PINE MUTUAL WATER COMPANY | 33 | 33 | 39600 | 68600 | INYO | 0 | 0 | 68600 | 71824.2
CA4400665 | MEADOWRIDGE MUTUAL WATER CO | 18 | 18 | 21600 | 50600 | SANTA CRUZ | 0.3 | 15180 | 65780 | 68871.66
CA0707519 | DUTCH SLOUGH WATER WORKS | 58 | 49 | 58800 | 87800 | CONTRA COSTA | 0.3 | 26340 | 114140 | 119504.58
CA3901172 | PAR COUNTRY ESTATES CSA-16 | 54 | 51 | 61200 | 90200 | SAN JOAQUIN | 0 | 0 | 90200 | 94439.4
CA5400631 | LINNELL FARM LABOR CENTER | 195 | 195 | 234000 | 263000 | TULARE | 0 | 0 | 263000 | 275361
CA5400792 | WOODVILLE FARM LABOR CENTER | 177 | 177 | 212400 | 241400 | TULARE | 0 | 0 | 241400 | 252745.8
CA2702055 | VIERRA KNOLLS MWC | 22 | 22 | 26400 | 55400 | MONTEREY | 0.3 | 16620 | 72020 | 75404.94
CA5401038 | AKIN WATER CO | 26 | 26 | 31200 | 60200 | TULARE | 0 | 0 | 60200 | 63029.4
CA1500553 | RANCHOS DEL RIO | 24 | 24 | 28800 | 57800 | KERN | 0 | 0 | 57800 | 60516.6
CA3110049 | TAHOE PARK WATER CO - SKYLAND/NIELSEN | 92 | 89 | 106800 | 135800 | PLACER | 0 | 0 | 135800 | 142182.6
CA1000018 | EASTON ESTATES WATER COMPANY | 108 | 107 | 128400 | 157400 | FRESNO | 0 | 0 | 157400 | 164797.8
CA1805007 | HERLONG PUBLIC UTILITY DISTRICT | 297 | 8 | 9600 | 38600 | LASSEN | 0 | 0 | 38600 | 40414.2
CA1700536 | SUNRISE SHORE MUTUAL WATER COMPANY | 42 | 42 | 50400 | 79400 | LAKE | 0 | 0 | 79400 | 83131.8
CA4500254 | ANDERSON PARK VILLAGE | 45 | 45 | 54000 | 83000 | SHASTA | 0 | 0 | 83000 | 86901
CA0800861 | RESERVATION RANCH | 20 | 20 | 24000 | 53000 | DEL NORTE | 0 | 0 | 53000 | 55491
CA1400518 | VAN LOON WATER ASSOCIATION | 15 | 15 | 18000 | 47000 | INYO | 0 | 0 | 47000 | 49209
CA1000063 | NEW AUBERRY WATER ASSOCIATION | 35 | 35 | 42000 | 71000 | FRESNO | 0 | 0 | 71000 | 74337
CA3600388 | DESERT VIEW MOBILE PARK | 28 | 28 | 33600 | 62600 | SAN BERNARDINO | 0.3 | 18780 | 81380 | 85204.86
CA3400179 | MC CLELLAN MHP | 199 | 199 | 238800 | 267800 | SACRAMENTO | 0.32 | 85696 | 353496 | 370110.312
CA0500068 | DUNROVIN MOBILE HOME VILLAGE | 42 | 42 | 50400 | 79400 | CALAVERAS | 0 | 0 | 79400 | 83131.8
CA5301008 | PINE COVE RV PARK | 81 | 81 | 97200 | 126200 | TRINITY | 0 | 0 | 126200 | 132131.4
CA1000405 | PIEDRA PARK ASSOCIATION | 15 | 15 | 18000 | 47000 | FRESNO | 0 | 0 | 47000 | 49209
CA3301247 | ELMS MOBILE PARK | 47 | 47 | 56400 | 85400 | RIVERSIDE | 0.32 | 27328 | 112728 | 118026.216
CA3900720 | SHADED TERRACE PWS | 72 | 72 | 86400 | 115400 | SAN JOAQUIN | 0 | 0 | 115400 | 120823.8
CA5500092 | PONDEROSA MOBILE HOME PARK | 58 | 58 | 69600 | 98600 | TUOLUMNE | 0 | 0 | 98600 | 103234.2
CA5400682 | PLAINVIEW MWC - CENTRAL WATER | 42 | 42 | 50400 | 79400 | TULARE | 0 | 0 | 79400 | 83131.8
CA3900561 | LODI LAKE MOBILE HOME PARK | 52 | 52 | 62400 | 91400 | SAN JOAQUIN | 0 | 0 | 91400 | 95695.8
CA3400192 | TUNNEL TRAILER PARK | 21 | 21 | 25200 | 54200 | SACRAMENTO | 0.32 | 17344 | 71544 | 74906.568
CA4700803 | SHADOW MOUNTAIN MHP | 73 | 73 | 87600 | 116600 | SISKIYOU | 0 | 0 | 116600 | 122080.2
CA1200544 | REDCREST WATER WORKS | 35 | 35 | 42000 | 71000 | HUMBOLDT | 0 | 0 | 71000 | 74337
CA4500023 | HAT CREEK HIGHLANDS MUTUAL WATER CO | 44 | 44 | 52800 | 81800 | SHASTA | 0 | 0 | 81800 | 85644.6
CA2010008 | MADERA CO MD10A-MADERA RANCHOS | 944 | 926 | 1111200 | 1140200 | MADERA | 0 | 0 | 1140200 | 1193789.4
CA4900832 | LEISURE MOBILE HOME PARK | 186 | 1 | 1200 | 30200 | SONOMA | 0.3 | 9060 | 39260 | 41105.22
CA4400624 | RANCHO CORRALITOS | 31 | 2 | 2400 | 31400 | SANTA CRUZ | 0.3 | 9420 | 40820 | 42738.54
CA5500053 | LEISURE PINES MUTUAL WATER CO | 103 | 103 | 123600 | 152600 | TUOLUMNE | 0 | 0 | 152600 | 159772.2
CA2701705 | TASSAJARA SPRINGS WS | 70 | 70 | 84000 | 113000 | MONTEREY | 0.3 | 33900 | 146900 | 153804.3
CA1010001 | BAKMAN WATER COMPANY | 2608 | 93 | 111600 | 140600 | FRESNO | 0 | 0 | 140600 | 147208.2
CA5400529 | SHADY GROVE MHP, LLC | 42 | 42 | 50400 | 79400 | TULARE | 0 | 0 | 79400 | 83131.8
CA2710851 | SALINAS VALLEY STATE PRISON | 2208 | 2208 | 2649600 | 2678600 | MONTEREY | 0.3 | 803580 | 3482180 | 3645842.46
CA1009078 | HARRIS FEEDING COMPANY | 30 | 20 | 24000 | 53000 | FRESNO | 0 | 0 | 53000 | 55491
CA3901031 | 132 INVESTMENTS WATER SYSTEM | 93 | 93 | 111600 | 140600 | SAN JOAQUIN | 0 | 0 | 140600 | 147208.2
CA4300924 | PARKWAY LAKES RV PARK | 121 | 121 | 145200 | 174200 | SANTA CLARA | 0.32 | 55744 | 229944 | 240751.368
CA2702520 | ARROYO SECO ESTATES MWS | 27 | 5 | 6000 | 35000 | MONTEREY | 0.3 | 10500 | 45500 | 47638.5
CA5400819 | MOUNTAIN VIEW MHP | 24 | 24 | 28800 | 57800 | TULARE | 0 | 0 | 57800 | 60516.6
CA1700592 | KONOCTI SHORES | 99 | 99 | 118800 | 147800 | LAKE | 0 | 0 | 147800 | 154746.6
CA4500089 | PINE RIDGE PARK ESTATES | 27 | 27 | 32400 | 61400 | SHASTA | 0 | 0 | 61400 | 64285.8
CA5000071 | TWIN CYPRESS MOBILE HOME PARK | 45 | 45 | 54000 | 83000 | STANISLAUS | 0 | 0 | 83000 | 86901
CA1610006 | STRATFORD PUD | 364 | 2 | 2400 | 31400 | KINGS | 0 | 0 | 31400 | 32875.8
CA5800924 | CAMPTONVILLE COMMUNITY SERV DIST | 85 | 2 | 2400 | 31400 | YUBA | 0 | 0 | 31400 | 32875.8
CA5200556 | MAYWOOD MOBILE HOME PARK | 50 | 50 | 60000 | 89000 | TEHAMA | 0 | 0 | 89000 | 93183
CA0706004 | OAKLEY MUTUAL WATER COMPANY | 50 | 50 | 60000 | 89000 | CONTRA COSTA | 0.3 | 26700 | 115700 | 121137.9
CA3110015 | FULTON WATER COMPANY | 923 | 923 | 1107600 | 1136600 | PLACER | 0 | 0 | 1136600 | 1190020.2
CA3910002 | SAN JOAQUIN COUNTY - COLONIAL HEIGHTS | 558 | 555 | 666000 | 695000 | SAN JOAQUIN | 0 | 0 | 695000 | 727665
CA4200618 | MIDLAND SCHOOL | 48 | 48 | 57600 | 86600 | SANTA BARBARA | 0.3 | 25980 | 112580 | 117871.26
CA2710850 | CORRECTIONAL TRAINING FACILITY - SOLEDAD | 2769 | 2769 | 3322800 | 3351800 | MONTEREY | 0.3 | 1005540 | 4357340 | 4562134.98
CA3600094 | DOGWOOD BLUE JAY CYN IMP | 81 | 81 | 97200 | 126200 | SAN BERNARDINO | 0.3 | 37860 | 164060 | 171770.82
CA3210005 | GRAEAGLE WATER COMPANY | 935 | 176 | 211200 | 240200 | PLUMAS | 0 | 0 | 240200 | 251489.4
CA3700422 | LAGUNA MOUNTIAN MUTUAL WATER CO. | 28 | 28 | 33600 | 62600 | SAN DIEGO | 0.32 | 20032 | 82632 | 86515.704
CA3200155 | FRCCSD HOT SPRINGS | 17 | 15 | 18000 | 47000 | PLUMAS | 0 | 0 | 47000 | 49209
CA2700691 | PESANTE RD WS #06 | 16 | 16 | 19200 | 48200 | MONTEREY | 0.3 | 14460 | 62660 | 65605.02
CA3400296 | SAC CITY MOBILE HOME COMMUNITY LP | 164 | 164 | 196800 | 225800 | SACRAMENTO | 0.32 | 72256 | 298056 | 312064.632
CA0707613 | WILLOW MOBILE HOME PARK | 172 | 172 | 206400 | 235400 | CONTRA COSTA | 0.3 | 70620 | 306020 | 320402.94
CA5500115 | SUGAR PINE RV RESORT | 87 | 87 | 104400 | 133400 | TUOLUMNE | 0 | 0 | 133400 | 139669.8
CA5400732 | PIERPOINT SPRINGS WATER CO. | 84 | 84 | 100800 | 129800 | TULARE | 0 | 0 | 129800 | 135900.6
CA5500060 | MI WUK HEIGHTS MWC | 158 | 158 | 189600 | 218600 | TUOLUMNE | 0 | 0 | 218600 | 228874.2
CA3110018 | TAHOE PARK WATER COMPANY | 445 | 406 | 487200 | 516200 | PLACER | 0 | 0 | 516200 | 540461.4
CA4400723 | MISSION SPRINGS CONFERENCE CENTER | 141 | 67 | 80400 | 109400 | SANTA CRUZ | 0.3 | 32820 | 142220 | 148904.34
CA3600372 | PALMS RIVER RESORT | 205 | 53 | 63600 | 92600 | SAN BERNARDINO | 0.3 | 27780 | 120380 | 126037.86
CA1000267 | KINGS CANYON MOBILE HOME PARK | 26 | 26 | 31200 | 60200 | FRESNO | 0 | 0 | 60200 | 63029.4
CA2000828 | SHADY OAKS MOBILE HOME PARK LLC | 21 | 21 | 25200 | 54200 | MADERA | 0 | 0 | 54200 | 56747.4
CA3301800 | STONEWOOD CANYON ESTATES | 26 | 26 | 31200 | 60200 | RIVERSIDE | 0.32 | 19264 | 79464 | 83198.808
CA5000015 | OID #22 - WILLIAMS TRACT | 53 | 53 | 63600 | 92600 | STANISLAUS | 0 | 0 | 92600 | 96952.2
CA1900100 | METTLER VALLEY MUTUAL | 98 | 9 | 10800 | 39800 | LOS ANGELES | 0.32 | 12736 | 52536 | 55005.192
CA4200807 | WOODSTOCK RANCH | 117 | 1 | 1200 | 30200 | SANTA BARBARA | 0.3 | 9060 | 39260 | 41105.22
CA5200551 | WOODSON BRIDGE MHP | 104 | 104 | 124800 | 153800 | TEHAMA | 0 | 0 | 153800 | 161028.6
CA2000511 | MD 85 VALETA | 20 | 20 | 24000 | 53000 | MADERA | 0 | 0 | 53000 | 55491
CA1700561 | BLUE LAKES IMPROVEMENT CLUB | 41 | 30 | 36000 | 65000 | LAKE | 0 | 0 | 65000 | 68055
CA1502320 | LERDO SHERIFF S FACILITY | 110 | 110 | 132000 | 161000 | KERN | 0 | 0 | 161000 | 168567
CA3900607 | COUNTRY SQUIRE MOBILE ESTATES & WATER SY | 49 | 49 | 58800 | 87800 | SAN JOAQUIN | 0 | 0 | 87800 | 91926.6
CA5400744 | EAST THREE RIVERS MUTUAL WATER CORP | 15 | 15 | 18000 | 47000 | TULARE | 0 | 0 | 47000 | 49209
CA5400824 | SULTANA CSD | 249 | 249 | 298800 | 327800 | TULARE | 0 | 0 | 327800 | 343206.6
CA0900112 | CANDLELIGHT VILLAGE MUTUAL WATER CO. | 32 | 19 | 22800 | 51800 | EL DORADO | 0.3 | 15540 | 67340 | 70504.98
CA2700687 | PESANTE RD WS #02 | 40 | 40 | 48000 | 77000 | MONTEREY | 0.3 | 23100 | 100100 | 104804.7
CA2300717 | CREEKSIDE CABINS & RV RESORT | 55 | 55 | 66000 | 95000 | MENDOCINO | 0 | 0 | 95000 | 99465
CA1000426 | RIVERBEND MOBILE HOME & RV PARK | 49 | 49 | 58800 | 87800 | FRESNO | 0 | 0 | 87800 | 91926.6
CA3400155 | SEQUOIA WATER ASSOC | 18 | 18 | 21600 | 50600 | SACRAMENTO | 0.32 | 16192 | 66792 | 69931.224
CA3400138 | LOCKE WATER WORKS CO [SWS] | 44 | 44 | 52800 | 81800 | SACRAMENTO | 0.32 | 26176 | 107976 | 113050.872
CA3303087 | SAN JOSE COMMUNITY WATER SYSTEM | 15 | 15 | 18000 | 47000 | RIVERSIDE | 0.32 | 15040 | 62040 | 64955.88
CA2701633 | PARADISE RD WS #21 | 16 | 16 | 19200 | 48200 | MONTEREY | 0.3 | 14460 | 62660 | 65605.02
CA1500364 | KERNVALE MUTUAL WATER CO | 32 | 32 | 38400 | 67400 | KERN | 0 | 0 | 67400 | 70567.8
CA3600386 | FOOTHILL ESTATES MHP | 33 | 33 | 39600 | 68600 | SAN BERNARDINO | 0.3 | 20580 | 89180 | 93371.46
CA5400550 | SEVILLE WATER COMPANY | 90 | 90 | 108000 | 137000 | TULARE | 0 | 0 | 137000 | 143439
CA4900793 | VINEHILL VISTAS MUTUAL WATER COMPANY | 29 | 29 | 34800 | 63800 | SONOMA | 0.3 | 19140 | 82940 | 86838.18
CA3303035 | THERMAL PARK | 22 | 22 | 26400 | 55400 | RIVERSIDE | 0.32 | 17728 | 73128 | 76565.016
CA4200733 | MONTECITO SEA MEADOWS | 28 | 28 | 33600 | 62600 | SANTA BARBARA | 0.3 | 18780 | 81380 | 85204.86
CA3910024 | SAN JOAQUIN COUNTY - WILKINSON MANOR | 258 | 193 | 231600 | 260600 | SAN JOAQUIN | 0 | 0 | 260600 | 272848.2
CA5403212 | MONSON WATER SYSTEM | 32 | 32 | 38400 | 67400 | TULARE | 0 | 0 | 67400 | 70567.8
CA1900130 | DEL RIO MUTUAL | 250 | 168 | 201600 | 230600 | LOS ANGELES | 0.32 | 73792 | 304392 | 318698.424
CA4500290 | PINE GROVE MOBILEHOME PARK | 19 | 19 | 22800 | 51800 | SHASTA | 0 | 0 | 51800 | 54234.6
CA1502653 | BELLA VISTA MUTUAL WATER COMPANY | 46 | 46 | 55200 | 84200 | KERN | 0 | 0 | 84200 | 88157.4
CA3900512 | MORADA ACRES WATER SYSTEM | 32 | 32 | 38400 | 67400 | SAN JOAQUIN | 0 | 0 | 67400 | 70567.8
CA2700733 | SAN JUAN RD WS #01 | 15 | 15 | 18000 | 47000 | MONTEREY | 0.3 | 14100 | 61100 | 63971.7
CA3901159 | WILKINSON MANOR A-ZONE PWS | 38 | 38 | 45600 | 74600 | SAN JOAQUIN | 0 | 0 | 74600 | 78106.2
CA1400006 | PINE CREEK VILLAGE | 89 | 89 | 106800 | 135800 | INYO | 0 | 0 | 135800 | 142182.6
CA1000295 | KINGS PARK APARTMENTS | 41 | 41 | 49200 | 78200 | FRESNO | 0 | 0 | 78200 | 81875.4
CA1500483 | ALLEN ROAD MUTUAL WATER SYSTEM | 59 | 59 | 70800 | 99800 | KERN | 0 | 0 | 99800 | 104490.6
CA5400735 | RODRIGUEZ LABOR CAMP | 35 | 35 | 42000 | 71000 | TULARE | 0 | 0 | 71000 | 74337
CA5000014 | OID #46 - SUNSET OAKS | 79 | 79 | 94800 | 123800 | STANISLAUS | 0 | 0 | 123800 | 129618.6
CA5410039 | PLAINVIEW MUTUAL WATER COMPANY | 187 | 187 | 224400 | 253400 | TULARE | 0 | 0 | 253400 | 265309.8
CA1400109 | SIERRA NORTH COMMUNITY SERVICE DISTRICT | 16 | 16 | 19200 | 48200 | INYO | 0 | 0 | 48200 | 50465.4
CA1900849 | LLANO DEL RIO WATER COMPANY | 186 | 1 | 1200 | 30200 | LOS ANGELES | 0.32 | 9664 | 39864 | 41737.608
CA0500027 | LILI VALLEY WATER CO. | 70 | 70 | 84000 | 113000 | CALAVERAS | 0 | 0 | 113000 | 118311
CA1000627 | ZONNEVELD DAIRY - CERINI | 17 | 17 | 20400 | 49400 | FRESNO | 0 | 0 | 49400 | 51721.8
CA1700609 | LAZY S MOBILE RANCH | 24 | 24 | 28800 | 57800 | LAKE | 0 | 0 | 57800 | 60516.6
CA3900907 | BEL AIR MOBILE ESTATE | 116 | 116 | 139200 | 168200 | SAN JOAQUIN | 0 | 0 | 168200 | 176105.4
CA4400755 | MONTEREY BAY ACADEMY | 78 | 26 | 31200 | 60200 | SANTA CRUZ | 0.3 | 18060 | 78260 | 81938.22
CA2610004 | JUNE LAKE PUD - DOWN CANYON | 389 | 1 | 1200 | 30200 | MONO | 0 | 0 | 30200 | 31619.4
CA0707553 | RIVERVIEW MOBILE HOMES | 45 | 45 | 54000 | 83000 | CONTRA COSTA | 0.3 | 24900 | 107900 | 112971.3
CA5400660 | LAKE SUCCESS MOBILE LODGE | 19 | 1 | 1200 | 30200 | TULARE | 0 | 0 | 30200 | 31619.4
CA2210925 | YOSEMITE TERRACE ESTATES | 53 | 52 | 62400 | 91400 | MARIPOSA | 0 | 0 | 91400 | 95695.8
CA5400903 | TRACT 92 CSD | 93 | 93 | 111600 | 140600 | TULARE | 0 | 0 | 140600 | 147208.2
CA2700629 | MANZANITA HILLS WA | 31 | 31 | 37200 | 66200 | MONTEREY | 0.3 | 19860 | 86060 | 90104.82
CA0910015 | TAHOE KEYS WATER COMPANY | 1566 | 1537 | 1844400 | 1873400 | EL DORADO | 0.3 | 562020 | 2435420 | 2549884.74
CA1900154 | TIERRA BONITA MUTUAL WATER | 32 | 9 | 10800 | 39800 | LOS ANGELES | 0.32 | 12736 | 52536 | 55005.192
CA3400121 | EL DORADO MOBILE HOME PARK | 128 | 128 | 153600 | 182600 | SACRAMENTO | 0.32 | 58432 | 241032 | 252360.504
CA5400934 | PONDEROSA CSD | 146 | 36 | 43200 | 72200 | TULARE | 0 | 0 | 72200 | 75593.4
CA1400025 | VALLEY VISTA MUTUAL WATER COMPANY | 25 | 25 | 30000 | 59000 | INYO | 0 | 0 | 59000 | 61773
CA3700962 | OAKVALE PARK | 70 | 10 | 12000 | 41000 | SAN DIEGO | 0.32 | 13120 | 54120 | 56663.64
CA5610008 | PLEASANT VALLEY MUTUAL WATER CO | 1630 | 1630 | 1956000 | 1985000 | VENTURA | 0.32 | 635200 | 2620200 | 2743349.4
CA3900558 | RANCHO SAN JOAQUIN WATER SYS | 52 | 52 | 62400 | 91400 | SAN JOAQUIN | 0 | 0 | 91400 | 95695.8
CA1009120 | RAU DAIRY | 43 | 43 | 51600 | 80600 | FRESNO | 0 | 0 | 80600 | 84388.2
CA0707601 | RUSSOS MOBILE PARK | 20 | 20 | 24000 | 53000 | CONTRA COSTA | 0.3 | 15900 | 68900 | 72138.3
CA1502383 | NORD ROAD WATER ASSOCIATION | 16 | 16 | 19200 | 48200 | KERN | 0 | 0 | 48200 | 50465.4
CA1400511 | MEADOW LAKE APARTMENTS | 16 | 16 | 19200 | 48200 | INYO | 0 | 0 | 48200 | 50465.4
CA1009111 | SCE/BIG CREEK POWERHOUSE #1 | 76 | 76 | 91200 | 120200 | FRESNO | 0 | 0 | 120200 | 125849.4
CA1400036 | KEELER COMMUNITY SERVICE DISTRICT | 83 | 82 | 98400 | 127400 | INYO | 0 | 0 | 127400 | 133387.8
CA4200918 | LOS PRIETOS COMPLEX | 39 | 39 | 46800 | 75800 | SANTA BARBARA | 0.3 | 22740 | 98540 | 103171.38
CA3600397 | MOSS MOBILE MANOR | 43 | 43 | 51600 | 80600 | SAN BERNARDINO | 0.3 | 24180 | 104780 | 109704.66
CA0400042 | FOREST VILLAGE LLC | 21 | 21 | 25200 | 54200 | BUTTE | 0 | 0 | 54200 | 56747.4
CA2600733 | COLD WATER CANYON MWC | 45 | 45 | 54000 | 83000 | MONO | 0 | 0 | 83000 | 86901
CA4900674 | PINE HILL TERRACE MOBILE HOME PARK | 23 | 23 | 27600 | 56600 | SONOMA | 0.3 | 16980 | 73580 | 77038.26
CA3900762 | RIVERSIDE MOBILE HOME PARK | 58 | 58 | 69600 | 98600 | SAN JOAQUIN | 0 | 0 | 98600 | 103234.2
CA3900702 | CORRAL HOLLOW PWS | 44 | 44 | 52800 | 81800 | SAN JOAQUIN | 0 | 0 | 81800 | 85644.6
CA2310013 | POINT ARENA WATER WORKS | 234 | 30 | 36000 | 65000 | MENDOCINO | 0 | 0 | 65000 | 68055
CA5000080 | COUNTRY WESTERN MOBILE HOME PARK | 55 | 55 | 66000 | 95000 | STANISLAUS | 0 | 0 | 95000 | 99465
CA3601015 | IRONWOOD CAMP | 74 | 60 | 72000 | 101000 | SAN BERNARDINO | 0.3 | 30300 | 131300 | 137471.1
CA5000013 | OID #45 | 51 | 51 | 61200 | 90200 | STANISLAUS | 0 | 0 | 90200 | 94439.4
CA4500054 | BALLS FERRY FISHING RESORT | 75 | 75 | 90000 | 119000 | SHASTA | 0 | 0 | 119000 | 124593
CA1900868 | RIVERS END TRAILER PARK | 45 | 45 | 54000 | 83000 | LOS ANGELES | 0.32 | 26560 | 109560 | 114709.32
CA1610007 | HOME GARDEN CSD | 467 | 467 | 560400 | 589400 | KINGS | 0 | 0 | 589400 | 617101.8
CA5410021 | EARLIMART PUD | 1545 | 1522 | 1826400 | 1855400 | TULARE | 0 | 0 | 1855400 | 1942603.8
CA3600400 | APPLE VALLEY VILLAGE MHE | 93 | 93 | 111600 | 140600 | SAN BERNARDINO | 0.3 | 42180 | 182780 | 191370.66
CA3600297 | GORDON ACRES WATER CO | 66 | 6 | 7200 | 36200 | SAN BERNARDINO | 0.3 | 10860 | 47060 | 49271.82
CA1910158 | STERLING MUTUAL WATER COMPANY | 201 | 201 | 241200 | 270200 | LOS ANGELES | 0.32 | 86464 | 356664 | 373427.208
CA4300542 | SAN MARTIN COUNTY WATER DISTRICT | 185 | 2 | 2400 | 31400 | SANTA CLARA | 0.32 | 10048 | 41448 | 43396.056
CA4200579 | ROSARIO PARK | 19 | 19 | 22800 | 51800 | SANTA BARBARA | 0.3 | 15540 | 67340 | 70504.98
CA1500296 | FULLER ACRES MUTUAL WATER COMPANY | 165 | 165 | 198000 | 227000 | KERN | 0 | 0 | 227000 | 237669
CA1500344 | SOUTH KERN MUTUAL WATER COMPANY | 15 | 15 | 18000 | 47000 | KERN | 0 | 0 | 47000 | 49209
CA1000407 | GEORGE COX WATER SYSTEM | 20 | 20 | 24000 | 53000 | FRESNO | 0 | 0 | 53000 | 55491
CA4200633 | LINGATE MUTUAL WATER COMPANY | 20 | 2 | 2400 | 31400 | SANTA BARBARA | 0.3 | 9420 | 40820 | 42738.54
CA5301001 | BUCKTAIL MUTUAL WATER COMPANY | 42 | 42 | 50400 | 79400 | TRINITY | 0 | 0 | 79400 | 83131.8
CA5400655 | CENTRAL MUTUAL WATER CO | 41 | 41 | 49200 | 78200 | TULARE | 0 | 0 | 78200 | 81875.4
CA1500578 | LONG CANYON WATER COMPANY CORP. | 64 | 53 | 63600 | 92600 | KERN | 0 | 0 | 92600 | 96952.2
CA5403043 | YETTEM WATER SYSTEM | 66 | 66 | 79200 | 108200 | TULARE | 0 | 0 | 108200 | 113285.4
CA1206002 | PALOMINO ESTATES WATER COMPANY | 19 | 19 | 22800 | 51800 | HUMBOLDT | 0 | 0 | 51800 | 54234.6
CA1500442 | SUNSET APARTMENTS WS | 20 | 20 | 24000 | 53000 | KERN | 0 | 0 | 53000 | 55491
CA3400156 | SOUTHWEST TRACT W M D [SWS] | 33 | 2 | 2400 | 31400 | SACRAMENTO | 0.32 | 10048 | 41448 | 43396.056
CA3900523 | MORADA MANOR WATER SYSTEM | 34 | 34 | 40800 | 69800 | SAN JOAQUIN | 0 | 0 | 69800 | 73080.6
CA4400557 | ST FRANCIS TRACT WATER SYSTEM | 29 | 29 | 34800 | 63800 | SANTA CRUZ | 0.3 | 19140 | 82940 | 86838.18
CA2800593 | R RANCH AT THE LAKE | 16 | 16 | 19200 | 48200 | NAPA | 0.3 | 14460 | 62660 | 65605.02
CA1502164 | LLANAS CAMP FOUR WATER SYSTEM | 55 | 55 | 66000 | 95000 | KERN | 0 | 0 | 95000 | 99465
CA1200687 | RIVERBEND MOBILE HOME PARK | 28 | 28 | 33600 | 62600 | HUMBOLDT | 0 | 0 | 62600 | 65542.2
CA2400128 | COUNTRY CLUB COUNTY WD | 23 | 23 | 27600 | 56600 | MERCED | 0 | 0 | 56600 | 59260.2
CA3000519 | HYNES ESTATES MUTUAL WATER CO. | 42 | 42 | 50400 | 79400 | ORANGE | 0.3 | 23820 | 103220 | 108071.34
CA0610001 | ARBUCKLE PUBLIC UTILITY DISTRICT | 1024 | 1000 | 1200000 | 1229000 | COLUSA | 0 | 0 | 1229000 | 1286763
CA1500413 | TEJON RANCH MAIN HEADQUARTERS | 33 | 19 | 22800 | 51800 | KERN | 0 | 0 | 51800 | 54234.6
CA1700595 | CAL 20 VILLAGE AND MEADOW POINTE PARK | 93 | 2 | 2400 | 31400 | LAKE | 0 | 0 | 31400 | 32875.8
CA5301101 | TREASURE CREEK WOODS MWC | 32 | 32 | 38400 | 67400 | TRINITY | 0 | 0 | 67400 | 70567.8
CA3600301 | STRAWBERRY LODGE MWC | 137 | 135 | 162000 | 191000 | SAN BERNARDINO | 0.3 | 57300 | 248300 | 259970.1
CA0707575 | FRANKS MARINA | 66 | 66 | 79200 | 108200 | CONTRA COSTA | 0.3 | 32460 | 140660 | 147271.02
CA0800603 | BUTTE COURT MOBILE HOME PARK | 23 | 23 | 27600 | 56600 | DEL NORTE | 0 | 0 | 56600 | 59260.2
CA3200150 | HAMILTON BRANCH MWC | 113 | 24 | 28800 | 57800 | PLUMAS | 0 | 0 | 57800 | 60516.6
CA0900308 | QUINTETTE SERVICE CORP WATER | 52 | 3 | 3600 | 32600 | EL DORADO | 0.3 | 9780 | 42380 | 44371.86
CA2610005 | LEE VINING PUBLIC UTILITY | 68 | 68 | 81600 | 110600 | MONO | 0 | 0 | 110600 | 115798.2
CA4000501 | HALCYON WATER SYSTEM | 46 | 46 | 55200 | 84200 | SAN LUIS OBISPO | 0.3 | 25260 | 109460 | 114604.62
CA4900943 | ALLIANCE REDWOODS CONFERENCE GROUNDS | 73 | 73 | 87600 | 116600 | SONOMA | 0.3 | 34980 | 151580 | 158704.26
CA5400504 | PORTERVILLE MOBILE VILLAGE | 62 | 62 | 74400 | 103400 | TULARE | 0 | 0 | 103400 | 108259.8
CA5400805 | SOULTS MUTUAL WATER CO | 36 | 36 | 43200 | 72200 | TULARE | 0 | 0 | 72200 | 75593.4
CA4610001 | CITY OF LOYALTON | 360 | 354 | 424800 | 453800 | SIERRA | 0 | 0 | 453800 | 475128.6
CA0707574 | SANTIAGO ISLAND VILLAGE | 211 | 211 | 253200 | 282200 | CONTRA COSTA | 0.3 | 84660 | 366860 | 384102.42
CA5400881 | SUNRISE MUTUAL WATER CO. | 39 | 39 | 46800 | 75800 | TULARE | 0 | 0 | 75800 | 79362.6
CA0600013 | COLUSA CO. WWD #2 - PRINCETON | 120 | 120 | 144000 | 173000 | COLUSA | 0 | 0 | 173000 | 181131
CA1000247 | SHERWOOD FOREST MHP | 48 | 48 | 57600 | 86600 | FRESNO | 0 | 0 | 86600 | 90670.2
CA1000238 | CAMDEN TRAILER PARK | 26 | 26 | 31200 | 60200 | FRESNO | 0 | 0 | 60200 | 63029.4
CA3200148 | FEATHER RIVER RV & MHP | 21 | 21 | 25200 | 54200 | PLUMAS | 0 | 0 | 54200 | 56747.4
CA2701553 | POND-DEROSA OAKS WC | 75 | 2 | 2400 | 31400 | MONTEREY | 0.3 | 9420 | 40820 | 42738.54
CA0610003 | MAXWELL PUBLIC UTILITY DISTRICT | 393 | 393 | 471600 | 500600 | COLUSA | 0 | 0 | 500600 | 524128.2
CA1400059 | BROOKSIDE MOBILE HOME PARK | 45 | 45 | 54000 | 83000 | INYO | 0 | 0 | 83000 | 86901
CA2210921 | WHISPERING PINES APARTMENTS | 28 | 28 | 33600 | 62600 | MARIPOSA | 0 | 0 | 62600 | 65542.2
CA0707597 | SANDY POINT MOBILE HOME PARK | 24 | 24 | 28800 | 57800 | CONTRA COSTA | 0.3 | 17340 | 75140 | 78671.58
CA4400754 | MONTE VISTA CHRISTIAN SCHOOL | 43 | 43 | 51600 | 80600 | SANTA CRUZ | 0.3 | 24180 | 104780 | 109704.66
CA1800524 | LASSEN MOBILE HOME PARK | 30 | 30 | 36000 | 65000 | LASSEN | 0 | 0 | 65000 | 68055
CA5400647 | YOKOHL MUTUAL WATER CO | 32 | 32 | 38400 | 67400 | TULARE | 0 | 0 | 67400 | 70567.8
CA3610021 | FALLSVALE SERVICE COMPANY | 492 | 492 | 590400 | 619400 | SAN BERNARDINO | 0.3 | 185820 | 805220 | 843065.34
CA0706005 | FARRAR PARK PROPERTY OWNERS | 70 | 70 | 84000 | 113000 | CONTRA COSTA | 0.3 | 33900 | 146900 | 153804.3
CA1500544 | ENOS LANE PUBLIC UTILITY DISTRICT | 89 | 88 | 105600 | 134600 | KERN | 0 | 0 | 134600 | 140926.2
CA1500455 | WILLIAM FISHER MEMORIAL WATER COMPANY | 16 | 16 | 19200 | 48200 | KERN | 0 | 0 | 48200 | 50465.4
CA3400172 | TOKAY PARK WATER CO | 198 | 196 | 235200 | 264200 | SACRAMENTO | 0.32 | 84544 | 348744 | 365134.968
CA4200885 | CHALK HILL ESTATES HOA | 15 | 15 | 18000 | 47000 | SANTA BARBARA | 0.3 | 14100 | 61100 | 63971.7
CA5301201 | SEYMOUR'S MUTUAL WATER SYSTEM | 27 | 27 | 32400 | 61400 | TRINITY | 0 | 0 | 61400 | 64285.8
CA4500102 | NORTH REDDING RV VILLAGE | 100 | 100 | 120000 | 149000 | SHASTA | 0 | 0 | 149000 | 156003
CA3901216 | SANTOS RANCH PWS #5-CSA #35 | 97 | 96 | 115200 | 144200 | SAN JOAQUIN | 0 | 0 | 144200 | 150977.4
CA5200535 | LIVE OAK ACRES MWC INC. | 40 | 40 | 48000 | 77000 | TEHAMA | 0 | 0 | 77000 | 80619
CA4900720 | MOBILE HOME ESTATES | 150 | 150 | 180000 | 209000 | SONOMA | 0.3 | 62700 | 271700 | 284469.9
CA5400728 | GRIER MUTUAL WATER COMPANY | 99 | 99 | 118800 | 147800 | TULARE | 0 | 0 | 147800 | 154746.6
CA4900620 | AUSTIN ACRES MUTUAL WATER COMPANY | 24 | 24 | 28800 | 57800 | SONOMA | 0.3 | 17340 | 75140 | 78671.58
CA2010800 | CENTRAL CA WOMENS FACILITY | 656 | 656 | 787200 | 816200 | MADERA | 0 | 0 | 816200 | 854561.4
CA3910803 | CDCR CALIFORNIA HEALTH CARE FACILITY | 81 | 81 | 97200 | 126200 | SAN JOAQUIN | 0 | 0 | 126200 | 132131.4
CA0800700 | LAS PALMAS MOBILE HOME PARK | 60 | 60 | 72000 | 101000 | DEL NORTE | 0 | 0 | 101000 | 105747
CA5601134 | ELKINS RANCH | 43 | 37 | 44400 | 73400 | VENTURA | 0.32 | 23488 | 96888 | 101441.736
CA1500231 | VICTORY MUTUAL WATER COMPANY | 173 | 173 | 207600 | 236600 | KERN | 0 | 0 | 236600 | 247720.2
CA5200600 | GURNSEY AVENUE MUTUAL WATER SYSTEM | 15 | 15 | 18000 | 47000 | TEHAMA | 0 | 0 | 47000 | 49209
CA0400078 | FOREST KNOLLS MUTUAL WATER CO | 21 | 21 | 25200 | 54200 | BUTTE | 0 | 0 | 54200 | 56747.4
CA2210906 | MARIPOSA PINES MUTUAL | 87 | 87 | 104400 | 133400 | MARIPOSA | 0 | 0 | 133400 | 139669.8
CA4300996 | VALLEY VIEW RANCHES | 16 | 16 | 19200 | 48200 | SANTA CLARA | 0.32 | 15424 | 63624 | 66614.328
CA0707608 | MARINA MOBILE MANOR | 24 | 24 | 28800 | 57800 | CONTRA COSTA | 0.3 | 17340 | 75140 | 78671.58
CA2702328 | VENTANA BIG SUR INN WS | 26 | 26 | 31200 | 60200 | MONTEREY | 0.3 | 18060 | 78260 | 81938.22
CA5400718 | WILLIAMS MUTUAL WATER CO | 50 | 50 | 60000 | 89000 | TULARE | 0 | 0 | 89000 | 93183
CA0707523 | FLAMINGO MOBILE MANOR | 62 | 62 | 74400 | 103400 | CONTRA COSTA | 0.3 | 31020 | 134420 | 140737.74
CA0103041 | TRAILER HAVEN MOBILE HOME PARK | 191 | 191 | 229200 | 258200 | ALAMEDA | 0.3 | 77460 | 335660 | 351436.02
CA0400007 | BUTTE CREEK ESTATES MUTUAL WATER CO | 168 | 168 | 201600 | 230600 | BUTTE | 0 | 0 | 230600 | 241438.2
CA2701820 | CORDA RD WS | 19 | 19 | 22800 | 51800 | MONTEREY | 0.3 | 15540 | 67340 | 70504.98
CA5400602 | EAGLE'S NEST RESORT | 78 | 78 | 93600 | 122600 | TULARE | 0 | 0 | 122600 | 128362.2
CA2701701 | BRADLEY-LOCKWOOD RD WS | 16 | 16 | 19200 | 48200 | MONTEREY | 0.3 | 14460 | 62660 | 65605.02
CA2701687 | VALLEY OAKS MHP WS | 46 | 46 | 55200 | 84200 | MONTEREY | 0.3 | 25260 | 109460 | 114604.62
CA4000834 | ANZA VINEYARD ESTATES MUTUAL WATER CO | 16 | 16 | 19200 | 48200 | SAN LUIS OBISPO | 0.3 | 14460 | 62660 | 65605.02
CA4500160 |  | 2 | 1 | 1200 | 30200 | SHASTA | 0 | 0 | 30200 | 31619.4
CA4500162 |  | 1 | 1 | 1200 | 30200 | SHASTA | 0 | 0 | 30200 | 31619.4
CA4500180 |  | 2 | 1 | 1200 | 30200 | SHASTA | 0 | 0 | 30200 | 31619.4
CA4500181 |  | 2 | 2 | 2400 | 31400 | SHASTA | 0 | 0 | 31400 | 32875.8
CA4700559 |  | 2 | 1 | 1200 | 30200 | SISKIYOU | 0 | 0 | 30200 | 31619.4
CA4700577 |  | 2 | 2 | 2400 | 31400 | SISKIYOU | 0 | 0 | 31400 | 32875.8
CA4700582 |  | 1 | 1 | 1200 | 30200 | SISKIYOU | 0 | 0 | 30200 | 31619.4
CA4700585 |  | 1 | 1 | 1200 | 30200 | SISKIYOU | 0 | 0 | 30200 | 31619.4
CA4700591 |  | 1 | 1 | 1200 | 30200 | SISKIYOU | 0 | 0 | 30200 | 31619.4
CA2100538 |  | 2 | 2 | 2400 | 31400 | MARIN | 0.3 | 9420 | 40820 | 42738.54
CA2100560 |  | 4 | 4 | 4800 | 33800 | MARIN | 0.3 | 10140 | 43940 | 46005.18
CA2100582 |  | 5 | 5 | 6000 | 35000 | MARIN | 0.3 | 10500 | 45500 | 47638.5
CA2210907 |  | 9 | 9 | 10800 | 39800 | MARIPOSA | 0 | 0 | 39800 | 41670.6
CA2210908 |  | 6 | 1 | 1200 | 30200 | MARIPOSA | 0 | 0 | 30200 | 31619.4
CA2210909 |  | 20 | 20 | 24000 | 53000 | MARIPOSA | 0 | 0 | 53000 | 55491
CA2210910 |  | 24 | 24 | 28800 | 57800 | MARIPOSA | 0 | 0 | 57800 | 60516.6
CA4200618 |  | 48 | 48 | 57600 | 86600 | SANTA BARBARA | 0.3 | 25980 | 112580 | 117871.26
CA4200747 |  | 2 | 1 | 1200 | 30200 | SANTA BARBARA | 0.3 | 9060 | 39260 | 41105.22
CA2300755 |  | 36 | 35 | 42000 | 71000 | MENDOCINO | 0 | 0 | 71000 | 74337
CA2300764 |  | 8 | 8 | 9600 | 38600 | MENDOCINO | 0 | 0 | 38600 | 40414.2
CA2300770 |  | 11 | 11 | 13200 | 42200 | MENDOCINO | 0 | 0 | 42200 | 44183.4
CA2300847 |  | 1 | 1 | 1200 | 30200 | MENDOCINO | 0 | 0 | 30200 | 31619.4
CA4200879 |  | 1 | 1 | 1200 | 30200 | SANTA BARBARA | 0.3 | 9060 | 39260 | 41105.22
CA2702317 |  | 1 | 1 | 1200 | 30200 | MONTEREY | 0.3 | 9060 | 39260 | 41105.22
CA0105009 |  | 1 | 1 | 1200 | 30200 | ALAMEDA | 0.3 | 9060 | 39260 | 41105.22
CA1502607 |  | 5 | 5 | 6000 | 35000 | KERN | 0 | 0 | 35000 | 36645
CA3702364 |  | 5 | 5 | 6000 | 35000 | SAN DIEGO | 0.32 | 11200 | 46200 | 48371.4
CA0202501 |  | 5 | 5 | 6000 | 35000 | ALPINE | 0 | 0 | 35000 | 36645
CA0707620 |  | 1 | 1 | 1200 | 30200 | CONTRA COSTA | 0.3 | 9060 | 39260 | 41105.22
CA0800647 |  | 1 | 1 | 1200 | 30200 | DEL NORTE | 0 | 0 | 30200 | 31619.4
CA0800649 |  | 1 | 1 | 1200 | 30200 | DEL NORTE | 0 | 0 | 30200 | 31619.4
CA1503683 |  | 3 | 3 | 3600 | 32600 | KERN | 0 | 0 | 32600 | 34132.2
CA0400060 |  | 3 | 3 | 3600 | 32600 | BUTTE | 0 | 0 | 32600 | 34132.2
CA0400063 |  | 3 | 3 | 3600 | 32600 | BUTTE | 0 | 0 | 32600 | 34132.2
CA0400064 |  | 11 | 11 | 13200 | 42200 | BUTTE | 0 | 0 | 42200 | 44183.4
CA0400067 |  | 2 | 2 | 2400 | 31400 | BUTTE | 0 | 0 | 31400 | 32875.8
CA0400068 |  | 6 | 6 | 7200 | 36200 | BUTTE | 0 | 0 | 36200 | 37901.4
CA0400073 |  | 5 | 5 | 6000 | 35000 | BUTTE | 0 | 0 | 35000 | 36645
CA0400079 |  | 4 | 4 | 4800 | 33800 | BUTTE | 0 | 0 | 33800 | 35388.6
CA0900111 |  | 19 | 19 | 22800 | 51800 | EL DORADO | 0.3 | 15540 | 67340 | 70504.98
CA0500085 |  | 6 | 6 | 7200 | 36200 | CALAVERAS | 0 | 0 | 36200 | 37901.4
CA0500091 |  | 13 | 13 | 15600 | 44600 | CALAVERAS | 0 | 0 | 44600 | 46696.2
CA0900304 |  | 2 | 1 | 1200 | 30200 | EL DORADO | 0.3 | 9060 | 39260 | 41105.22
CA0900309 |  | 8 | 8 | 9600 | 38600 | EL DORADO | 0.3 | 11580 | 50180 | 52538.46
CA0900410 |  | 5 | 5 | 6000 | 35000 | EL DORADO | 0.3 | 10500 | 45500 | 47638.5
CA0706028 |  | 4 | 4 | 4800 | 33800 | CONTRA COSTA | 0.3 | 10140 | 43940 | 46005.18
CA0706029 |  | 2 | 2 | 2400 | 31400 | CONTRA COSTA | 0.3 | 9420 | 40820 | 42738.54
CA3900748 |  | 1 | 1 | 1200 | 30200 | SAN JOAQUIN | 0 | 0 | 30200 | 31619.4
CA3900848 |  | 2 | 2 | 2400 | 31400 | SAN JOAQUIN | 0 | 0 | 31400 | 32875.8
CA3900849 |  | 1 | 1 | 1200 | 30200 | SAN JOAQUIN | 0 | 0 | 30200 | 31619.4
CA3900850 |  | 4 | 4 | 4800 | 33800 | SAN JOAQUIN | 0 | 0 | 33800 | 35388.6
CA5100138 |  | 1 | 1 | 1200 | 30200 | SUTTER | 0 | 0 | 30200 | 31619.4
CA5100142 |  | 1 | 1 | 1200 | 30200 | SUTTER | 0 | 0 | 30200 | 31619.4
CA5100143 |  | 1 | 1 | 1200 | 30200 | SUTTER | 0 | 0 | 30200 | 31619.4
CA5100145 |  | 2 | 2 | 2400 | 31400 | SUTTER | 0 | 0 | 31400 | 32875.8
CA5200506 |  | 1 | 1 | 1200 | 30200 | TEHAMA | 0 | 0 | 30200 | 31619.4
CA5200513 |  | 8 | 6 | 7200 | 36200 | TEHAMA | 0 | 0 | 36200 | 37901.4
CA5200518 |  | 2 | 2 | 2400 | 31400 | TEHAMA | 0 | 0 | 31400 | 32875.8
CA1000204 |  | 33 | 33 | 39600 | 68600 | FRESNO | 0 | 0 | 68600 | 71824.2
CA1000206 |  | 4 | 4 | 4800 | 33800 | FRESNO | 0 | 0 | 33800 | 35388.6
CA1000208 |  | 12 | 12 | 14400 | 43400 | FRESNO | 0 | 0 | 43400 | 45439.8
CA1000217 |  | 10 | 10 | 12000 | 41000 | FRESNO | 0 | 0 | 41000 | 42927
CA1000221 |  | 23 | 23 | 27600 | 56600 | FRESNO | 0 | 0 | 56600 | 59260.2
CA1000280 |  | 26 | 26 | 31200 | 60200 | FRESNO | 0 | 0 | 60200 | 63029.4
CA3400267 |  | 10 | 10 | 12000 | 41000 | SACRAMENTO | 0.32 | 13120 | 54120 | 56663.64
CA3400268 |  | 2 | 2 | 2400 | 31400 | SACRAMENTO | 0.32 | 10048 | 41448 | 43396.056
CA3400273 |  | 5 | 5 | 6000 | 35000 | SACRAMENTO | 0.32 | 11200 | 46200 | 48371.4
CA1000315 |  | 5 | 5 | 6000 | 35000 | FRESNO | 0 | 0 | 35000 | 36645
CA1000367 |  | 21 | 21 | 25200 | 54200 | FRESNO | 0 | 0 | 54200 | 56747.4
CA1000476 |  | 12 | 12 | 14400 | 43400 | FRESNO | 0 | 0 | 43400 | 45439.8
CA3500507 |  | 2 | 2 | 2400 | 31400 | SAN BENITO | 0.3 | 9420 | 40820 | 42738.54
CA3500521 |  | 2 | 2 | 2400 | 31400 | SAN BENITO | 0.3 | 9420 | 40820 | 42738.54
CA3500571 |  | 61 | 61 | 73200 | 102200 | SAN BENITO | 0.3 | 30660 | 132860 | 139104.42
CA2701221 |  | 2 | 2 | 2400 | 31400 | MONTEREY | 0.3 | 9420 | 40820 | 42738.54
CA3500801 |  | 4 | 4 | 4800 | 33800 | SAN BENITO | 0.3 | 10140 | 43940 | 46005.18
CA3500905 |  | 9 | 9 | 10800 | 39800 | SAN BENITO | 0.3 | 11940 | 51740 | 54171.78
CA3901085 |  | 1 | 1 | 1200 | 30200 | SAN JOAQUIN | 0 | 0 | 30200 | 31619.4
CA3901090 |  | 1 | 1 | 1200 | 30200 | SAN JOAQUIN | 0 | 0 | 30200 | 31619.4
CA3901107 |  | 1 | 1 | 1200 | 30200 | SAN JOAQUIN | 0 | 0 | 30200 | 31619.4
CA1000104 |  | 11 | 11 | 13200 | 42200 | FRESNO | 0 | 0 | 42200 | 44183.4
CA1000105 |  | 8 | 8 | 9600 | 38600 | FRESNO | 0 | 0 | 38600 | 40414.2
CA1000111 |  | 13 | 12 | 14400 | 43400 | FRESNO | 0 | 0 | 43400 | 45439.8
CA3901163 |  | 3 | 3 | 3600 | 32600 | SAN JOAQUIN | 0 | 0 | 32600 | 34132.2
CA3901167 |  | 1 | 1 | 1200 | 30200 | SAN JOAQUIN | 0 | 0 | 30200 | 31619.4
CA3901169 |  | 3 | 3 | 3600 | 32600 | SAN JOAQUIN | 0 | 0 | 32600 | 34132.2
CA1000181 |  | 8 | 8 | 9600 | 38600 | FRESNO | 0 | 0 | 38600 | 40414.2
CA1000182 |  | 2 | 2 | 2400 | 31400 | FRESNO | 0 | 0 | 31400 | 32875.8
CA1000186 |  | 11 | 11 | 13200 | 42200 | FRESNO | 0 | 0 | 42200 | 44183.4
CA1000187 |  | 10 | 10 | 12000 | 41000 | FRESNO | 0 | 0 | 41000 | 42927
CA1000190 |  | 6 | 6 | 7200 | 36200 | FRESNO | 0 | 0 | 36200 | 37901.4
CA1000192 |  | 3 | 3 | 3600 | 32600 | FRESNO | 0 | 0 | 32600 | 34132.2
CA1000194 |  | 1 | 1 | 1200 | 30200 | FRESNO | 0 | 0 | 30200 | 31619.4
CA1000198 |  | 25 | 25 | 30000 | 59000 | FRESNO | 0 | 0 | 59000 | 61773
CA3901209 |  | 11 | 11 | 13200 | 42200 | SAN JOAQUIN | 0 | 0 | 42200 | 44183.4
CA3901331 |  | 1 | 1 | 1200 | 30200 | SAN JOAQUIN | 0 | 0 | 30200 | 31619.4
CA2800970 |  | 2 | 1 | 1200 | 30200 | NAPA | 0.3 | 9060 | 39260 | 41105.22
CA4900577 |  | 54 | 54 | 64800 | 93800 | SONOMA | 0.3 | 28140 | 121940 | 127671.18
CA1800575 |  | 1 | 1 | 1200 | 30200 | LASSEN | 0 | 0 | 30200 | 31619.4
CA1800576 |  | 1 | 1 | 1200 | 30200 | LASSEN | 0 | 0 | 30200 | 31619.4
CA2810012 |  | 313 | 198 | 237600 | 266600 | NAPA | 0.3 | 79980 | 346580 | 362869.26
CA4900680 |  | 4 | 4 | 4800 | 33800 | SONOMA | 0.3 | 10140 | 43940 | 46005.18
CA4900693 |  | 2 | 2 | 2400 | 31400 | SONOMA | 0.3 | 9420 | 40820 | 42738.54
CA4900694 |  | 11 | 11 | 13200 | 42200 | SONOMA | 0.3 | 12660 | 54860 | 57438.42
CA4900695 |  | 1 | 1 | 1200 | 30200 | SONOMA | 0.3 | 9060 | 39260 | 41105.22
CA4900699 |  | 6 | 6 | 7200 | 36200 | SONOMA | 0.3 | 10860 | 47060 | 49271.82
CA4900703 |  | 7 | 7 | 8400 | 37400 | SONOMA | 0.3 | 11220 | 48620 | 50905.14
CA4900704 |  | 5 | 5 | 6000 | 35000 | SONOMA | 0.3 | 10500 | 45500 | 47638.5
CA4900707 |  | 2 | 2 | 2400 | 31400 | SONOMA | 0.3 | 9420 | 40820 | 42738.54
CA4900708 |  | 7 | 7 | 8400 | 37400 | SONOMA | 0.3 | 11220 | 48620 | 50905.14
CA4900711 |  | 1 | 1 | 1200 | 30200 | SONOMA | 0.3 | 9060 | 39260 | 41105.22
CA4900714 |  | 3 | 3 | 3600 | 32600 | SONOMA | 0.3 | 9780 | 42380 | 44371.86
CA2900536 |  | 8 | 1 | 1200 | 30200 | NEVADA | 0 | 0 | 30200 | 31619.4
CA4900716 |  | 2 | 1 | 1200 | 30200 | SONOMA | 0.3 | 9060 | 39260 | 41105.22
CA4900719 |  | 5 | 5 | 6000 | 35000 | SONOMA | 0.3 | 10500 | 45500 | 47638.5
CA4900739 |  | 2 | 2 | 2400 | 31400 | SONOMA | 0.3 | 9420 | 40820 | 42738.54
CA2900578 |  | 11 | 11 | 13200 | 42200 | NEVADA | 0 | 0 | 42200 | 44183.4
CA2900587 |  | 10 | 10 | 12000 | 41000 | NEVADA | 0 | 0 | 41000 | 42927
CA2900593 |  | 8 | 8 | 9600 | 38600 | NEVADA | 0 | 0 | 38600 | 40414.2
CA2901208 |  | 1 | 1 | 1200 | 30200 | NEVADA | 0 | 0 | 30200 | 31619.4
CA4900907 |  | 13 | 13 | 15600 | 44600 | SONOMA | 0.3 | 13380 | 57980 | 60705.06
CA4900945 |  | 4 | 4 | 4800 | 33800 | SONOMA | 0.3 | 10140 | 43940 | 46005.18
CA1900707 |  | 6 | 6 | 7200 | 36200 | LOS ANGELES | 0.32 | 11584 | 47784 | 50029.848
CA1900751 |  | 18 | 18 | 21600 | 50600 | LOS ANGELES | 0.32 | 16192 | 66792 | 69931.224
CA1900886 |  | 2 | 1 | 1200 | 30200 | LOS ANGELES | 0.32 | 9664 | 39864 | 41737.608
CA4901156 |  | 5 | 5 | 6000 | 35000 | SONOMA | 0.3 | 10500 | 45500 | 47638.5
CA4901168 |  | 14 | 14 | 16800 | 45800 | SONOMA | 0.3 | 13740 | 59540 | 62338.38
CA4901215 |  | 1 | 1 | 1200 | 30200 | SONOMA | 0.3 | 9060 | 39260 | 41105.22
CA5400624 |  | 9 | 9 | 10800 | 39800 | TULARE | 0 | 0 | 39800 | 41670.6
CA5400636 |  | 8 | 1 | 1200 | 30200 | TULARE | 0 | 0 | 30200 | 31619.4
CA5400709 |  | 26 | 26 | 31200 | 60200 | TULARE | 0 | 0 | 60200 | 63029.4
CA5400711 |  | 5 | 5 | 6000 | 35000 | TULARE | 0 | 0 | 35000 | 36645
CA5400713 |  | 10 | 10 | 12000 | 41000 | TULARE | 0 | 0 | 41000 | 42927
CA5400714 |  | 11 | 11 | 13200 | 42200 | TULARE | 0 | 0 | 42200 | 44183.4
CA1502068 |  | 1 | 1 | 1200 | 30200 | KERN | 0 | 0 | 30200 | 31619.4
CA1502154 |  | 1 | 1 | 1200 | 30200 | KERN | 0 | 0 | 30200 | 31619.4
CA5400795 |  | 7 | 7 | 8400 | 37400 | TULARE | 0 | 0 | 37400 | 39157.8
CA1502221 |  | 2 | 2 | 2400 | 31400 | KERN | 0 | 0 | 31400 | 32875.8
CA1502229 |  | 16 | 16 | 19200 | 48200 | KERN | 0 | 0 | 48200 | 50465.4
CA5400844 |  | 11 | 11 | 13200 | 42200 | TULARE | 0 | 0 | 42200 | 44183.4
CA5400846 |  | 3 | 3 | 3600 | 32600 | TULARE | 0 | 0 | 32600 | 34132.2
CA5400873 |  | 1 | 1 | 1200 | 30200 | TULARE | 0 | 0 | 30200 | 31619.4
CA5400886 |  | 8 | 8 | 9600 | 38600 | TULARE | 0 | 0 | 38600 | 40414.2
CA5400919 |  | 9 | 9 | 10800 | 39800 | TULARE | 0 | 0 | 39800 | 41670.6
CA5400994 |  | 7 | 7 | 8400 | 37400 | TULARE | 0 | 0 | 37400 | 39157.8
CA1910022 |  | 148 | 91 | 109200 | 138200 | LOS ANGELES | 0.32 | 44224 | 182424 | 190997.928
CA5403130 |  | 5 | 5 | 6000 | 35000 | TULARE | 0 | 0 | 35000 | 36645
CA5403146 |  | 5 | 5 | 6000 | 35000 | TULARE | 0 | 0 | 35000 | 36645
CA2600568 |  | 2 | 1 | 1200 | 30200 | MONO | 0 | 0 | 30200 | 31619.4
CA2600570 |  | 4 | 4 | 4800 | 33800 | MONO | 0 | 0 | 33800 | 35388.6
CA4901436 |  | 1 | 1 | 1200 | 30200 | SONOMA | 0.3 | 9060 | 39260 | 41105.22
CA2700552 |  | 1 | 1 | 1200 | 30200 | MONTEREY | 0.3 | 9060 | 39260 | 41105.22
CA2700577 |  | 1 | 1 | 1200 | 30200 | MONTEREY | 0.3 | 9060 | 39260 | 41105.22
CA2000567 |  | 32 | 32 | 38400 | 67400 | MADERA | 0 | 0 | 67400 | 70567.8
CA4910027 |  | 93 | 65 | 78000 | 107000 | SONOMA | 0.3 | 32100 | 139100 | 145637.7
CA2000597 |  | 8 | 8 | 9600 | 38600 | MADERA | 0 | 0 | 38600 | 40414.2
CA2000612 |  | 18 | 17 | 20400 | 49400 | MADERA | 0 | 0 | 49400 | 51721.8
CA2000616 |  | 5 | 5 | 6000 | 35000 | MADERA | 0 | 0 | 35000 | 36645
CA1010339 |  | 159 | 159 | 190800 | 219800 | FRESNO | 0 | 0 | 219800 | 230130.6
CA5000109 |  | 1 | 1 | 1200 | 30200 | STANISLAUS | 0 | 0 | 30200 | 31619.4
CA5000132 |  | 1 | 1 | 1200 | 30200 | STANISLAUS | 0 | 0 | 30200 | 31619.4
CA5000133 |  | 4 | 4 | 4800 | 33800 | STANISLAUS | 0 | 0 | 33800 | 35388.6
CA5000249 |  | 1 | 1 | 1200 | 30200 | STANISLAUS | 0 | 0 | 30200 | 31619.4
CA5000273 |  | 2 | 2 | 2400 | 31400 | STANISLAUS | 0 | 0 | 31400 | 32875.8
CA5000274 |  | 4 | 4 | 4800 | 33800 | STANISLAUS | 0 | 0 | 33800 | 35388.6
CA5000277 |  | 1 | 1 | 1200 | 30200 | STANISLAUS | 0 | 0 | 30200 | 31619.4
CA2700705 |  | 1 | 1 | 1200 | 30200 | MONTEREY | 0.3 | 9060 | 39260 | 41105.22
CA2700727 |  | 1 | 1 | 1200 | 30200 | MONTEREY | 0.3 | 9060 | 39260 | 41105.22
CA3601057 |  | 4 | 4 | 4800 | 33800 | SAN BERNARDINO | 0.3 | 10140 | 43940 | 46005.18
CA5000404 |  | 2 | 2 | 2400 | 31400 | STANISLAUS | 0 | 0 | 31400 | 32875.8
CA3601095 |  | 11 | 11 | 13200 | 42200 | SAN BERNARDINO | 0.3 | 12660 | 54860 | 57438.42
CA2000844 |  | 9 | 9 | 10800 | 39800 | MADERA | 0 | 0 | 39800 | 41670.6
CA2000846 |  | 23 | 23 | 27600 | 56600 | MADERA | 0 | 0 | 56600 | 59260.2
CA3601179 |  | 9 | 9 | 10800 | 39800 | SAN BERNARDINO | 0.3 | 11940 | 51740 | 54171.78
CA5000568 |  | 9 | 9 | 10800 | 39800 | STANISLAUS | 0 | 0 | 39800 | 41670.6
CA2000947 |  | 17 | 16 | 19200 | 48200 | MADERA | 0 | 0 | 48200 | 50465.4
CA2702490 |  | 1 | 1 | 1200 | 30200 | MONTEREY | 0.3 | 9060 | 39260 | 41105.22
CA3301308 |  | 7 | 7 | 8400 | 37400 | RIVERSIDE | 0.32 | 11968 | 49368 | 51688.296
CA3301309 |  | 20 | 20 | 24000 | 53000 | RIVERSIDE | 0.32 | 16960 | 69960 | 73248.12
CA5710009 |  | 686 | 401 | 481200 | 510200 | YOLO | 0 | 0 | 510200 | 534179.4
CA3600432 |  | 15 | 15 | 18000 | 47000 | SAN BERNARDINO | 0.3 | 14100 | 61100 | 63971.7
CA5800006 |  | 1 | 1 | 1200 | 30200 | YUBA | 0 | 0 | 30200 | 31619.4
CA4300593 |  | 1 | 1 | 1200 | 30200 | SANTA CLARA | 0.32 | 9664 | 39864 | 41737.608
CA5800844 |  | 5 | 5 | 6000 | 35000 | YUBA | 0 | 0 | 35000 | 36645
CA4300610 |  | 1 | 1 | 1200 | 30200 | SANTA CLARA | 0.32 | 9664 | 39864 | 41737.608
CA4300721 |  | 8 | 8 | 9600 | 38600 | SANTA CLARA | 0.32 | 12352 | 50952 | 53346.744
CA4300779 |  | 4 | 4 | 4800 | 33800 | SANTA CLARA | 0.32 | 10816 | 44616 | 46712.952
CA1200546 |  | 1 | 1 | 1200 | 30200 | HUMBOLDT | 0 | 0 | 30200 | 31619.4
CA1200681 |  | 1 | 1 | 1200 | 30200 | HUMBOLDT | 0 | 0 | 30200 | 31619.4
CA1200684 |  | 1 | 1 | 1200 | 30200 | HUMBOLDT | 0 | 0 | 30200 | 31619.4
CA1300553 |  | 1 | 1 | 1200 | 30200 | IMPERIAL | 0 | 0 | 30200 | 31619.4
CA1300554 |  | 6 | 6 | 7200 | 36200 | IMPERIAL | 0 | 0 | 36200 | 37901.4
CA4400750 |  | 6 | 6 | 7200 | 36200 | SANTA CRUZ | 0.3 | 10860 | 47060 | 49271.82
CA4400751 |  | 10 | 10 | 12000 | 41000 | SANTA CRUZ | 0.3 | 12300 | 53300 | 55805.1
CA4400754 |  | 43 | 43 | 51600 | 80600 | SANTA CRUZ | 0.3 | 24180 | 104780 | 109704.66
CA4400755 |  | 78 | 26 | 31200 | 60200 | SANTA CRUZ | 0.3 | 18060 | 78260 | 81938.22
CA4400757 |  | 3 | 3 | 3600 | 32600 | SANTA CRUZ | 0.3 | 9780 | 42380 | 44371.86
CA4400758 |  | 2 | 1 | 1200 | 30200 | SANTA CRUZ | 0.3 | 9060 | 39260 | 41105.22
CA4400875 |  | 2 | 1 | 1200 | 30200 | SANTA CRUZ | 0.3 | 9060 | 39260 | 41105.22
CA1400019 |  | 2 | 2 | 2400 | 31400 | INYO | 0 | 0 | 31400 | 32875.8
CA1400522 |  | 7 | 7 | 8400 | 37400 | INYO | 0 | 0 | 37400 | 39157.8
CA3700117 |  | 12 | 12 | 14400 | 43400 | SAN DIEGO | 0.32 | 13888 | 57288 | 59980.536
CA3700118 |  | 4 | 4 | 4800 | 33800 | SAN DIEGO | 0.32 | 10816 | 44616 | 46712.952
CA3700963 |  | 19 | 19 | 22800 | 51800 | SAN DIEGO | 0.32 | 16576 | 68376 | 71589.672
CA3701005 |  | 4 | 4 | 4800 | 33800 | SAN DIEGO | 0.32 | 10816 | 44616 | 46712.952
CA3701010 |  | 15 | 15 | 18000 | 47000 | SAN DIEGO | 0.32 | 15040 | 62040 | 64955.88
CA5200520 |  | 4 | 4 | 4800 | 33800 | TEHAMA | 0 | 0 | 33800 | 35388.6
CA5200544 |  | 2 | 2 | 2400 | 31400 | TEHAMA | 0 | 0 | 31400 | 32875.8
CA5500171 |  | 19 | 19 | 22800 | 51800 | TUOLUMNE | 0 | 0 | 51800 | 54234.6
CA2400062 |  | 4 | 4 | 4800 | 33800 | MERCED | 0 | 0 | 33800 | 35388.6
CA5200565 |  | 9 | 9 | 10800 | 39800 | TEHAMA | 0 | 0 | 39800 | 41670.6
CA5500242 |  | 17 | 17 | 20400 | 49400 | TUOLUMNE | 0 | 0 | 49400 | 51721.8
CA2400065 |  | 5 | 5 | 6000 | 35000 | MERCED | 0 | 0 | 35000 | 36645
CA2400071 |  | 4 | 4 | 4800 | 33800 | MERCED | 0 | 0 | 33800 | 35388.6
CA2400075 |  | 2 | 2 | 2400 | 31400 | MERCED | 0 | 0 | 31400 | 32875.8
CA2400079 |  | 24 | 24 | 28800 | 57800 | MERCED | 0 | 0 | 57800 | 60516.6
CA2400097 |  | 7 | 7 | 8400 | 37400 | MERCED | 0 | 0 | 37400 | 39157.8
CA2400099 |  | 1 | 1 | 1200 | 30200 | MERCED | 0 | 0 | 30200 | 31619.4
CA2400113 |  | 9 | 9 | 10800 | 39800 | MERCED | 0 | 0 | 39800 | 41670.6
CA2400134 |  | 3 | 3 | 3600 | 32600 | MERCED | 0 | 0 | 32600 | 34132.2
CA1600009 |  | 14 | 14 | 16800 | 45800 | KINGS | 0 | 0 | 45800 | 47952.6
CA1600011 |  | 6 | 6 | 7200 | 36200 | KINGS | 0 | 0 | 36200 | 37901.4
CA1600013 |  | 5 | 5 | 6000 | 35000 | KINGS | 0 | 0 | 35000 | 36645
CA1600015 |  | 7 | 7 | 8400 | 37400 | KINGS | 0 | 0 | 37400 | 39157.8
CA5205007 |  | 5 | 3 | 3600 | 32600 | TEHAMA | 0 | 0 | 32600 | 34132.2
CA5304105 |  | 2 | 1 | 1200 | 30200 | TRINITY | 0 | 0 | 30200 | 31619.4
CA5305107 |  | 6 | 3 | 3600 | 32600 | TRINITY | 0 | 0 | 32600 | 34132.2
CA5400519 |  | 26 | 26 | 31200 | 60200 | TULARE | 0 | 0 | 60200 | 63029.4
CA5400538 |  | 10 | 9 | 10800 | 39800 | TULARE | 0 | 0 | 39800 | 41670.6
CA5400558 |  | 11 | 11 | 13200 | 42200 | TULARE | 0 | 0 | 42200 | 44183.4
CA5700509 |  | 3 | 3 | 3600 | 32600 | YOLO | 0 | 0 | 32600 | 34132.2
CA5700510 |  | 7 | 7 | 8400 | 37400 | YOLO | 0 | 0 | 37400 | 39157.8
CA5700643 |  | 17 | 16 | 19200 | 48200 | YOLO | 0 | 0 | 48200 | 50465.4

## Backup Source_Intertie
Joining_systems PWSID | Joining_systems Name | Joining_COUNTY | Joining_POPULATION | Joining_SERVICE_CO | Receiving_System PWSID | Receiving_system Name | Receiving-System_COUNTY | Receiving System-POPULATION | Receiving System-Service Connection | Distance_Miles | Pipeline Cost | Service Line | Conn_Fee | Admin/Legal/CEQA | Subtotal_SL_Conn_Pipe_Admin | 20% Contingency | 25% Planning and Construction | Total Merger Cost | County Multiplier | Cost with Multiplier | Cost before inflation ($) | Final Cost with inflation ($)
CA0400036 | MOUNTAIN VIEW MHC LLC | BUTTE | 230 | 129 | CA0410002 | CAL-WATER SERVICE CO.-CHICO | BUTTE | 104908 | 29610 | 1000 | 155000 | 5000 | 851400 | 285000 | 1296400 | 259280 | 324100 | 1879780 | 0 | 0 | 1879780 | 1968129.66
CA0400040 | ALMOND GROVE MOBILE PARK | BUTTE | 250 | 175 | CA0410002 | CAL-WATER SERVICE CO.-CHICO | BUTTE | 104908 | 29610 | 1000 | 155000 | 5000 | 1155000 | 285000 | 1600000 | 320000 | 400000 | 2320000 | 0 | 0 | 2320000 | 2429040
CA0706005 | FARRAR PARK PROPERTY OWNERS | CONTRA COSTA | 140 | 70 | CA0710003 | CONTRA COSTA WATER DISTRICT | CONTRA COSTA | 198000 | 60529 | 1000 | 155000 | 5000 | 462000 | 285000 | 907000 | 181400 | 226750 | 1315150 | 0.3 | 272100 | 1587250 | 1661850.75
CA0707547 | KNIGHTSEN COMMUNITY WATER SYSTEM | CONTRA COSTA | 250 | 18 | CA0710003 | CONTRA COSTA WATER DISTRICT | CONTRA COSTA | 198000 | 60529 | 1000 | 155000 | 5000 | 118800 | 285000 | 563800 | 112760 | 140950 | 817510 | 0.3 | 169140 | 986650 | 1033022.55
CA0707553 | RIVERVIEW MOBILE HOMES | CONTRA COSTA | 216 | 45 | CA0710003 | CONTRA COSTA WATER DISTRICT | CONTRA COSTA | 198000 | 60529 | 1000 | 155000 | 5000 | 297000 | 285000 | 742000 | 148400 | 185500 | 1075900 | 0.3 | 222600 | 1298500 | 1359529.5
CA0707572 | BETHEL ISLAND MUTUAL WATER CO | CONTRA COSTA | 149 | 45 | CA0710003 | CONTRA COSTA WATER DISTRICT | CONTRA COSTA | 198000 | 60529 | 1000 | 155000 | 5000 | 297000 | 285000 | 742000 | 148400 | 185500 | 1075900 | 0.3 | 222600 | 1298500 | 1359529.5
CA0707574 | SANTIAGO ISLAND VILLAGE | CONTRA COSTA | 400 | 211 | CA0710003 | CONTRA COSTA WATER DISTRICT | CONTRA COSTA | 198000 | 60529 | 1000 | 155000 | 5000 | 1392600 | 285000 | 1837600 | 367520 | 459400 | 2664520 | 0.3 | 551280 | 3215800 | 3366942.6
CA0707589 | BELLA VISTA WATER SYS | CONTRA COSTA | 93 | 33 | CA0710008 | CITY OF PITTSBURG | CONTRA COSTA | 62500 | 19023 | 1000 | 155000 | 5000 | 217800 | 285000 | 662800 | 132560 | 165700 | 961060 | 0.3 | 198840 | 1159900 | 1214415.3
CA0707594 | CASA MEDANOS WATER SYSTEM | CONTRA COSTA | 45 | 16 | CA0710003 | CONTRA COSTA WATER DISTRICT | CONTRA COSTA | 198000 | 60529 | 1000 | 155000 | 5000 | 105600 | 285000 | 550600 | 110120 | 137650 | 798370 | 0.3 | 165180 | 963550 | 1008836.85
CA0707623 | WILCOX STATION RANCH | CONTRA COSTA | 90 | 15 | CA0110005 | EAST BAY MUD | ALAMEDA | 1405000 | 390779 | 1000 | 155000 | 5000 | 99000 | 285000 | 544000 | 108800 | 136000 | 788800 | 0.3 | 163200 | 952000 | 996744
CA1000105 | MADISON ELEMENTARY SCHOOL | FRESNO | 900 | 8 | CA1010007 | CITY OF FRESNO | FRESNO | 541990 | 136972 | 1000 | 155000 | 5000 | 52800 | 285000 | 497800 | 99560 | 124450 | 721810 | 0 | 0 | 721810 | 755735.07
CA1000229 | GREEN ACRES MOBILE HOME ESTATE | FRESNO | 350 | 113 | CA1010007 | CITY OF FRESNO | FRESNO | 541990 | 136972 | 1000 | 155000 | 5000 | 745800 | 285000 | 1190800 | 238160 | 297700 | 1726660 | 0 | 0 | 1726660 | 1807813.02
CA1000298 | WOODWARD BLUFFS MHP | FRESNO | 300 | 172 | CA1010007 | CITY OF FRESNO | FRESNO | 541990 | 136972 | 1000 | 155000 | 5000 | 1135200 | 285000 | 1580200 | 316040 | 395050 | 2291290 | 0 | 0 | 2291290 | 2398980.63
CA1000299 | THREE PALMS MOBILEHOME PARK | FRESNO | 300 | 105 | CA1010007 | CITY OF FRESNO | FRESNO | 541990 | 136972 | 1000 | 155000 | 5000 | 693000 | 285000 | 1138000 | 227600 | 284500 | 1650100 | 0 | 0 | 1650100 | 1727654.7
CA1009039 | PAPPAS & CO (MENDOTA) | FRESNO | 25 | 13 | CA1010007 | CITY OF FRESNO | FRESNO | 541990 | 136972 | 1000 | 155000 | 5000 | 85800 | 285000 | 530800 | 106160 | 132700 | 769660 | 0 | 0 | 769660 | 805834.02
CA1500096 | OLD RIVER MUTUAL WATER COMPANY | KERN | 128 | 14 | CA1510031 | BAKERSFIELD, CITY OF | KERN | 149796 | 48076 | 1000 | 155000 | 5000 | 92400 | 285000 | 537400 | 107480 | 134350 | 779230 | 0 | 0 | 779230 | 815853.81
CA1500340 | WEST TEHACHAPI MUTUAL | KERN | 150 | 36 | CA1510020 | TEHACHAPI, CITY OF | KERN | 8839 | 3393 | 1000 | 155000 | 5000 | 237600 | 285000 | 682600 | 136520 | 170650 | 989770 | 0 | 0 | 989770 | 1036289.19
CA1500344 | SOUTH KERN MUTUAL WATER COMPANY | KERN | 32 | 15 | CA1510031 | BAKERSFIELD, CITY OF | KERN | 149796 | 48076 | 1000 | 155000 | 5000 | 99000 | 285000 | 544000 | 108800 | 136000 | 788800 | 0 | 0 | 788800 | 825873.6
CA1500557 | STOCKDALE RANCHOS MUTUAL WATER CO | KERN | 393 | 95 | CA1510031 | BAKERSFIELD, CITY OF | KERN | 149796 | 48076 | 1000 | 155000 | 5000 | 627000 | 285000 | 1072000 | 214400 | 268000 | 1554400 | 0 | 0 | 1554400 | 1627456.8
CA1500564 | HOMETOWN WATER ASSOCIATION | KERN | 25 | 12 | CA1510017 | INDIAN WELLS VALLEY W.D. | KERN | 39478 | 11963 | 1000 | 155000 | 5000 | 79200 | 285000 | 524200 | 104840 | 131050 | 760090 | 0 | 0 | 760090 | 795814.23
CA1502164 | LLANAS CAMP FOUR WATER SYSTEM | KERN | 54 | 55 | CA1510019 | SHAFTER, CITY OF | KERN | 20500 | 4847 | 1000 | 155000 | 5000 | 363000 | 285000 | 808000 | 161600 | 202000 | 1171600 | 0 | 0 | 1171600 | 1226665.2
CA1502569 | FIRST MUTUAL WATER SYSTEM | KERN | 35 | 13 | CA1510018 | ROSAMOND CSD | KERN | 16905 | 5264 | 1000 | 155000 | 5000 | 85800 | 285000 | 530800 | 106160 | 132700 | 769660 | 0 | 0 | 769660 | 805834.02
CA1600002 | SUNSET VISTA ESTATES MHP | KINGS | 400 | 108 | CA3410017 | CALAM - PARKWAY | SACRAMENTO | 48738 | 14779 | 1000 | 155000 | 5000 | 712800 | 285000 | 1157800 | 231560 | 289450 | 1678810 | 0 | 0 | 1678810 | 1757714.07
CA1800523 | PINEVIEW MOBILE HOME PARK | LASSEN | 113 | 52 | CA1810001 | CITY OF SUSANVILLE | LASSEN | 16403 | 3781 | 1000 | 155000 | 5000 | 343200 | 285000 | 788200 | 157640 | 197050 | 1142890 | 0 | 0 | 1142890 | 1196605.83
CA1900055 | BLUE SKIES TRAILOR PARK | LOS ANGELES | 40 | 20 | CA1910102 | PALMDALE WATER DIST. | LOS ANGELES | 115525 | 26797 | 1000 | 155000 | 5000 | 132000 | 285000 | 577000 | 115400 | 144250 | 836650 | 0.32 | 184640 | 1021290 | 1069290.63
CA1900130 | DEL RIO MUTUAL | LOS ANGELES | 700 | 250 | CA1910039 | SAN GABRIEL VALLEY WATER CO.-EL MONTE | LOS ANGELES | 254000 | 46080 | 1000 | 155000 | 5000 | 1650000 | 285000 | 2095000 | 419000 | 523750 | 3037750 | 0.32 | 670400 | 3708150 | 3882433.05
CA1900520 | THE VILLAGE MOBILE HOME PARK | LOS ANGELES | 50 | 34 | CA1910070 | LOS ANGELES CWWD 40,REG 4 & 34-LANCASTER | LOS ANGELES | 187372 | 51516 | 1000 | 155000 | 5000 | 224400 | 285000 | 669400 | 133880 | 167350 | 970630 | 0.32 | 214208 | 1184838 | 1240525.386
CA1900636 | EL RANCHO MOBILE HOME PARK | LOS ANGELES | 215 | 76 | CA1910070 | LOS ANGELES CWWD 40,REG 4 & 34-LANCASTER | LOS ANGELES | 187372 | 51516 | 1000 | 155000 | 5000 | 501600 | 285000 | 946600 | 189320 | 236650 | 1372570 | 0.32 | 302912 | 1675482 | 1754229.654
CA1900649 | GOLDEN SANDS MOBILE HOME PARK | LOS ANGELES | 450 | 152 | CA1910070 | LOS ANGELES CWWD 40,REG 4 & 34-LANCASTER | LOS ANGELES | 187372 | 51516 | 1000 | 155000 | 5000 | 1003200 | 285000 | 1448200 | 289640 | 362050 | 2099890 | 0.32 | 463424 | 2563314 | 2683789.758
CA1900693 | DESERT PALMS MOBILE HOME PARK | LOS ANGELES | 140 | 56 | CA3310009 | EASTERN MUNICIPAL WD | RIVERSIDE | 608232 | 155877 | 1000 | 155000 | 5000 | 369600 | 285000 | 814600 | 162920 | 203650 | 1181170 | 0.32 | 260672 | 1441842 | 1509608.574
CA1900721 | TERRA NOVA MOBILE HOME PARK | LOS ANGELES | 140 | 75 | CA1910070 | LOS ANGELES CWWD 40,REG 4 & 34-LANCASTER | LOS ANGELES | 187372 | 51516 | 1000 | 155000 | 5000 | 495000 | 285000 | 940000 | 188000 | 235000 | 1363000 | 0.32 | 300800 | 1663800 | 1741998.6
CA1900804 | EVERGREEN MUTUAL WATER COMPANY | LOS ANGELES | 95 | 46 | CA1910070 | LOS ANGELES CWWD 40,REG 4 & 34-LANCASTER | LOS ANGELES | 187372 | 51516 | 1000 | 155000 | 5000 | 303600 | 285000 | 748600 | 149720 | 187150 | 1085470 | 0.32 | 239552 | 1325022 | 1387298.034
CA1900809 | LANDALE MUTUAL WATER COMPANY | LOS ANGELES | 752 | 172 | CA1910070 | LOS ANGELES CWWD 40,REG 4 & 34-LANCASTER | LOS ANGELES | 187372 | 51516 | 1000 | 155000 | 5000 | 1135200 | 285000 | 1580200 | 316040 | 395050 | 2291290 | 0.32 | 505664 | 2796954 | 2928410.838
CA1900817 | CLEAR SKIES MOBILE HOME PARK | LOS ANGELES | 131 | 47 | CA1910070 | LOS ANGELES CWWD 40,REG 4 & 34-LANCASTER | LOS ANGELES | 187372 | 51516 | 1000 | 155000 | 5000 | 310200 | 285000 | 755200 | 151040 | 188800 | 1095040 | 0.32 | 241664 | 1336704 | 1399529.088
CA1900843 | CALIFORNIAN MOBILE HOME PARK | LOS ANGELES | 372 | 133 | CA1910070 | LOS ANGELES CWWD 40,REG 4 & 34-LANCASTER | LOS ANGELES | 187372 | 51516 | 1000 | 155000 | 5000 | 877800 | 285000 | 1322800 | 264560 | 330700 | 1918060 | 0.32 | 423296 | 2341356 | 2451399.732
CA1900936 | AQUA J. MUTUAL WATER COMPANY | LOS ANGELES | 165 | 48 | CA1910070 | LOS ANGELES CWWD 40,REG 4 & 34-LANCASTER | LOS ANGELES | 187372 | 51516 | 1000 | 155000 | 5000 | 316800 | 285000 | 761800 | 152360 | 190450 | 1104610 | 0.32 | 243776 | 1348386 | 1411760.142
CA1900942 | ALPINE SPRINGS MOBILE HOME PARK | LOS ANGELES | 175 | 53 | CA1910102 | PALMDALE WATER DIST. | LOS ANGELES | 115525 | 26797 | 1000 | 155000 | 5000 | 349800 | 285000 | 794800 | 158960 | 198700 | 1152460 | 0.32 | 254336 | 1406796 | 1472915.412
CA2000595 | MADERA MH & RV PARK | MADERA | 450 | 99 | CA2010002 | CITY OF MADERA | MADERA | 66225 | 13913 | 1000 | 155000 | 5000 | 653400 | 285000 | 1098400 | 219680 | 274600 | 1592680 | 0 | 0 | 1592680 | 1667535.96
CA2010004 | MADERA CO CMD19-PARKWOOD | MADERA | 1637 | 496 | CA2010002 | CITY OF MADERA | MADERA | 66225 | 13913 | 1000 | 155000 | 5000 | 3273600 | 285000 | 3718600 | 743720 | 929650 | 5391970 | 0 | 0 | 5391970 | 5645392.59
CA2100560 | TOMALES ELEM & MIDDLE SCHOOL | MARIN | 265 | 4 | CA2110003 | NORTH MARIN WATER DISTRICT | MARIN | 61500 | 20071 | 1000 | 155000 | 5000 | 26400 | 285000 | 471400 | 94280 | 117850 | 683530 | 0.3 | 141420 | 824950 | 863722.65
CA2701034 | APPLE AVE WS #02 | MONTEREY | 75 | 18 | CA2710008 | GREENFIELD, CITY OF | MONTEREY | 17517 | 3772 | 1000 | 155000 | 5000 | 118800 | 285000 | 563800 | 112760 | 140950 | 817510 | 0.3 | 169140 | 986650 | 1033022.55
CA2701036 | APPLE AVE WS #03 | MONTEREY | 60 | 20 | CA2710008 | GREENFIELD, CITY OF | MONTEREY | 17517 | 3772 | 1000 | 155000 | 5000 | 132000 | 285000 | 577000 | 115400 | 144250 | 836650 | 0.3 | 173100 | 1009750 | 1057208.25
CA2701403 | PINE ST WS #01 | MONTEREY | 36 | 17 | CA2710011 | SOLEDAD, CITY OF | MONTEREY | 16729 | 3948 | 1000 | 155000 | 5000 | 112200 | 285000 | 557200 | 111440 | 139300 | 807940 | 0.3 | 167160 | 975100 | 1020929.7
CA2701959 | TIERRA VISTA MWC | MONTEREY | 54 | 18 | CA2710004 | CAL AM WATER COMPANY - MONTEREY | MONTEREY | 91884 | 37706 | 1000 | 155000 | 5000 | 118800 | 285000 | 563800 | 112760 | 140950 | 817510 | 0.3 | 169140 | 986650 | 1033022.55
CA2800530 | MEYERS WATER CO. | NAPA | 250 | 92 | CA2810003 | NAPA, CITY OF | NAPA | 87386 | 25264 | 1000 | 155000 | 5000 | 607200 | 285000 | 1052200 | 210440 | 263050 | 1525690 | 0.3 | 315660 | 1841350 | 1927893.45
CA2800531 | MOORE'S RESORT | NAPA | 70 | 20 | CA2810003 | NAPA, CITY OF | NAPA | 87386 | 25264 | 1000 | 155000 | 5000 | 132000 | 285000 | 577000 | 115400 | 144250 | 836650 | 0.3 | 173100 | 1009750 | 1057208.25
CA2801020 | ESPINOZA WATER SYSTEM | NAPA | 30 | 11 | CA2810003 | NAPA, CITY OF | NAPA | 87386 | 25264 | 1000 | 155000 | 5000 | 72600 | 285000 | 517600 | 103520 | 129400 | 750520 | 0.3 | 155280 | 905800 | 948372.6
CA2801080 | MILTON ROAD WATER COMPANY | NAPA | 55 | 24 | CA2810003 | NAPA, CITY OF | NAPA | 87386 | 25264 | 1000 | 155000 | 5000 | 158400 | 285000 | 603400 | 120680 | 150850 | 874930 | 0.3 | 181020 | 1055950 | 1105579.65
CA2910001 | CITY OF GRASS VALLEY | NEVADA | 4947 | 2486 | CA2910004 | NEVADA ID - E. GEORGE, BANNER MOUNTAIN | NEVADA | 17233 | 6068 | 1000 | 155000 | 5000 | 16407600 | 285000 | 16852600 | 3370520 | 4213150 | 24436270 | 0 | 0 | 24436270 | 25584774.69
CA2910002 | CITY OF NEVADA CITY | NEVADA | 3001 | 1252 | CA2910004 | NEVADA ID - E. GEORGE, BANNER MOUNTAIN | NEVADA | 17233 | 6068 | 1000 | 155000 | 5000 | 8263200 | 285000 | 8708200 | 1741640 | 2177050 | 12626890 | 0 | 0 | 12626890 | 13220353.83
CA2910010 | TRUCKEE-DONNER PUD - HIRSCHDALE | NEVADA | 85 | 26 | CA2910003 | TRUCKEE-DONNER PUD, MAIN | NEVADA | 36730 | 13293 | 1000 | 155000 | 5000 | 171600 | 285000 | 616600 | 123320 | 154150 | 894070 | 0 | 0 | 894070 | 936091.29
CA3000618 | LIBERTY PARK WATER ASSOCIATION | ORANGE | 89 | 27 | CA3010053 | CITY OF HUNTINGTON BEACH | ORANGE | 201000 | 54117 | 1000 | 155000 | 5000 | 178200 | 285000 | 623200 | 124640 | 155800 | 903640 | 0.3 | 186960 | 1090600 | 1141858.2
CA3100061 | SIERRA MEADOWS APARTMENT | PLACER | 52 | 28 | CA3110025 | PLACER CWA - FOOTHILL | PLACER | 83546 | 26728 | 1000 | 155000 | 5000 | 184800 | 285000 | 629800 | 125960 | 157450 | 913210 | 0 | 0 | 913210 | 956130.87
CA3100069 | AUBURN RIDGE WOODS | PLACER | 131 | 54 | CA3110005 | PLACER CWA - AUBURN/BOWMAN | PLACER | 27902 | 8448 | 1000 | 155000 | 5000 | 356400 | 285000 | 801400 | 160280 | 200350 | 1162030 | 0 | 0 | 1162030 | 1216645.41
CA3110023 | NORTH TAHOE PUD - CARNELIAN WOODS | PLACER | 524 | 269 | CA3110001 | NORTH TAHOE PUD - MAIN | PLACER | 5300 | 3260 | 1000 | 155000 | 5000 | 1775400 | 285000 | 2220400 | 444080 | 555100 | 3219580 | 0 | 0 | 3219580 | 3370900.26
CA3110034 | CHRISTIAN VALLEY PARK CSD | PLACER | 1800 | 627 | CA3110005 | PLACER CWA - AUBURN/BOWMAN | PLACER | 27902 | 8448 | 1000 | 155000 | 5000 | 4138200 | 285000 | 4583200 | 916640 | 1145800 | 6645640 | 0 | 0 | 6645640 | 6957985.08
CA3301040 | RIVERDALE ESTATES | RIVERSIDE | 300 | 186 | CA3310001 | COACHELLA VWD: COVE COMMUNITY | RIVERSIDE | 297500 | 106916 | 1000 | 155000 | 5000 | 1227600 | 285000 | 1672600 | 334520 | 418150 | 2425270 | 0.32 | 535232 | 2960502 | 3099645.594
CA3301107 | CARVER TRACT MUTUAL WATER COMP | RIVERSIDE | 300 | 188 | CA3310001 | COACHELLA VWD: COVE COMMUNITY | RIVERSIDE | 297500 | 106916 | 1000 | 155000 | 5000 | 1240800 | 285000 | 1685800 | 337160 | 421450 | 2444410 | 0.32 | 539456 | 2983866 | 3124107.702
CA3301169 | MURRIETA PALMS MOBILE HOME PARK | RIVERSIDE | 237 | 71 | CA3310038 | RANCHO CALIFORNIA WATER DISTRICT | RIVERSIDE | 144088 | 43762 | 1000 | 155000 | 5000 | 468600 | 285000 | 913600 | 182720 | 228400 | 1324720 | 0.32 | 292352 | 1617072 | 1693074.384
CA3301209 | DESERT VIEW TRAILER PARK | RIVERSIDE | 60 | 22 | CA3310001 | COACHELLA VWD: COVE COMMUNITY | RIVERSIDE | 297500 | 106916 | 1000 | 155000 | 5000 | 145200 | 285000 | 590200 | 118040 | 147550 | 855790 | 0.32 | 188864 | 1044654 | 1093752.738
CA3301247 | ELMS MOBILE PARK | RIVERSIDE | 100 | 47 | CA3310001 | COACHELLA VWD: COVE COMMUNITY | RIVERSIDE | 297500 | 106916 | 1000 | 155000 | 5000 | 310200 | 285000 | 755200 | 151040 | 188800 | 1095040 | 0.32 | 241664 | 1336704 | 1399529.088
CA3301380 | SAINT ANTHONY TRAILER PARK | RIVERSIDE | 340 | 68 | CA3310001 | COACHELLA VWD: COVE COMMUNITY | RIVERSIDE | 297500 | 106916 | 1000 | 155000 | 5000 | 448800 | 285000 | 893800 | 178760 | 223450 | 1296010 | 0.32 | 286016 | 1582026 | 1656381.222
CA3301512 | PINYON PINES COUNTY WATER DIST | RIVERSIDE | 160 | 82 | CA3310005 | DESERT WATER AGENCY | RIVERSIDE | 89232 | 22860 | 1000 | 155000 | 5000 | 541200 | 285000 | 986200 | 197240 | 246550 | 1429990 | 0.32 | 315584 | 1745574 | 1827615.978
CA3301717 | VALLEY VIEW TRAILER PARK | RIVERSIDE | 135 | 37 | CA3310001 | COACHELLA VWD: COVE COMMUNITY | RIVERSIDE | 297500 | 106916 | 1000 | 155000 | 5000 | 244200 | 285000 | 689200 | 137840 | 172300 | 999340 | 0.32 | 220544 | 1219884 | 1277218.548
CA3301877 | BLOCK 77 WATER COMPANY | RIVERSIDE | 50 | 18 | CA3310049 | WESTERN MWD | RIVERSIDE | 86595 | 21181 | 1000 | 155000 | 5000 | 118800 | 285000 | 563800 | 112760 | 140950 | 817510 | 0.32 | 180416 | 997926 | 1044828.522
CA3301990 | AMEZCUA - GARCIA WATER | RIVERSIDE | 316 | 113 | CA3310001 | COACHELLA VWD: COVE COMMUNITY | RIVERSIDE | 297500 | 106916 | 1000 | 155000 | 5000 | 745800 | 285000 | 1190800 | 238160 | 297700 | 1726660 | 0.32 | 381056 | 2107716 | 2206778.652
CA3303003 | GALINDO HOUSING FACILITY | RIVERSIDE | 50 | 38 | CA3310001 | COACHELLA VWD: COVE COMMUNITY | RIVERSIDE | 297500 | 106916 | 1000 | 155000 | 5000 | 250800 | 285000 | 695800 | 139160 | 173950 | 1008910 | 0.32 | 222656 | 1231566 | 1289449.602
CA3303035 | THERMAL PARK | RIVERSIDE | 73 | 22 | CA3310001 | COACHELLA VWD: COVE COMMUNITY | RIVERSIDE | 297500 | 106916 | 1000 | 155000 | 5000 | 145200 | 285000 | 590200 | 118040 | 147550 | 855790 | 0.32 | 188864 | 1044654 | 1093752.738
CA3310801 | BAUTISTA CC NO. 36 | RIVERSIDE | 84 | 1 | CA3310009 | EASTERN MUNICIPAL WD | RIVERSIDE | 608232 | 155877 | 1000 | 155000 | 5000 | 6600 | 285000 | 451600 | 90320 | 112900 | 654820 | 0.32 | 144512 | 799332 | 836900.604
CA3400122 | EL DORADO WEST MHP | SACRAMENTO | 172 | 128 | CA3410017 | CALAM - PARKWAY | SACRAMENTO | 48738 | 14779 | 1000 | 155000 | 5000 | 844800 | 285000 | 1289800 | 257960 | 322450 | 1870210 | 0.32 | 412736 | 2282946 | 2390244.462
CA3400401 | PLANTATION MOBILE HOME PARK | SACRAMENTO | 44 | 44 | CA3410017 | CALAM - PARKWAY | SACRAMENTO | 48738 | 14779 | 1000 | 155000 | 5000 | 290400 | 285000 | 735400 | 147080 | 183850 | 1066330 | 0.32 | 235328 | 1301658 | 1362835.926
CA3500552 | VENTURE ESTATES MWC | SAN BENITO | 60 | 18 | CA3510003 | SUNNYSLOPE COUNTY WATER DIST | SAN BENITO | 22902 | 6579 | 1000 | 155000 | 5000 | 118800 | 285000 | 563800 | 112760 | 140950 | 817510 | 0.3 | 169140 | 986650 | 1033022.55
CA3600215 | GILBERT STREET COMPLEX | SAN BERNARDINO | 1000 | 1 | CA3610039 | SAN BERNARDINO CITY | SAN BERNARDINO | 204870 | 45413 | 1000 | 155000 | 5000 | 6600 | 285000 | 451600 | 90320 | 112900 | 654820 | 0.3 | 135480 | 790300 | 827444.1
CA3600385 | BROOKSIDE MHP | SAN BERNARDINO | 65 | 19 | CA3610037 | REDLANDS CITY MUD-WATER DIV | SAN BERNARDINO | 78025 | 23644 | 1000 | 155000 | 5000 | 125400 | 285000 | 570400 | 114080 | 142600 | 827080 | 0.3 | 171120 | 998200 | 1045115.4
CA3600391 | HILLCREST MOBILE ESTATES | SAN BERNARDINO | 900 | 180 | CA3610055 | YUCAIPA VALLEY WATER DISTRICT | SAN BERNARDINO | 51558 | 13462 | 1000 | 155000 | 5000 | 1188000 | 285000 | 1633000 | 326600 | 408250 | 2367850 | 0.3 | 489900 | 2857750 | 2992064.25
CA3600400 | APPLE VALLEY VILLAGE MHE | SAN BERNARDINO | 180 | 93 | CA3610003 | LIBERTY UTILITIES (AV RANCHOS) CORP. | SAN BERNARDINO | 62602 | 21059 | 1000 | 155000 | 5000 | 613800 | 285000 | 1058800 | 211760 | 264700 | 1535260 | 0.3 | 317640 | 1852900 | 1939986.3
CA3701988 | ALPINE OAKS ESTATES LLC | SAN DIEGO | 125 | 68 | CA3710037 | PADRE DAM MWD | SAN DIEGO | 92045 | 23163 | 1000 | 155000 | 5000 | 448800 | 285000 | 893800 | 178760 | 223450 | 1296010 | 0.32 | 286016 | 1582026 | 1656381.222
CA3900561 | LODI LAKE MOBILE HOME PARK | SAN JOAQUIN | 104 | 52 | CA3910004 | LODI, CITY OF | SAN JOAQUIN | 68272 | 26124 | 1000 | 155000 | 5000 | 343200 | 285000 | 788200 | 157640 | 197050 | 1142890 | 0 | 0 | 1142890 | 1196605.83
CA3900732 | V & P TRAILER COURT WATER SYSTEM | SAN JOAQUIN | 35 | 15 | CA3910001 | CALIFORNIA WATER SERVICE - STOCKTON | SAN JOAQUIN | 173272 | 43871 | 1000 | 155000 | 5000 | 99000 | 285000 | 544000 | 108800 | 136000 | 788800 | 0 | 0 | 788800 | 825873.6
CA3900927 | SPRING CREEK ESTATES PWS | SAN JOAQUIN | 90 | 36 | CA3910007 | RIPON, CITY OF | SAN JOAQUIN | 16292 | 5126 | 1000 | 155000 | 5000 | 237600 | 285000 | 682600 | 136520 | 170650 | 989770 | 0 | 0 | 989770 | 1036289.19
CA3900964 | SAHARA MOBILE COURT | SAN JOAQUIN | 300 | 162 | CA3910001 | CALIFORNIA WATER SERVICE - STOCKTON | SAN JOAQUIN | 173272 | 43871 | 1000 | 155000 | 5000 | 1069200 | 285000 | 1514200 | 302840 | 378550 | 2195590 | 0 | 0 | 2195590 | 2298782.73
CA3900991 | LA TORRES PARK | SAN JOAQUIN | 40 | 14 | CA3910011 | TRACY, CITY OF | SAN JOAQUIN | 96345 | 24694 | 1000 | 155000 | 5000 | 92400 | 285000 | 537400 | 107480 | 134350 | 779230 | 0 | 0 | 779230 | 815853.81
CA3901215 | SAN JUAN VISTA | SAN JOAQUIN | 100 | 72 | CA3910001 | CALIFORNIA WATER SERVICE - STOCKTON | SAN JOAQUIN | 173272 | 43871 | 1000 | 155000 | 5000 | 475200 | 285000 | 920200 | 184040 | 230050 | 1334290 | 0 | 0 | 1334290 | 1397001.63
CA3901474 | HESKETT, JOE WATER SYSTEM | SAN JOAQUIN | 39 | 15 | CA3910001 | CALIFORNIA WATER SERVICE - STOCKTON | SAN JOAQUIN | 173272 | 43871 | 1000 | 155000 | 5000 | 99000 | 285000 | 544000 | 108800 | 136000 | 788800 | 0 | 0 | 788800 | 825873.6
CA4000501 | HALCYON WATER SYSTEM | SAN LUIS OBISPO | 105 | 46 | CA4010001 | ARROYO GRANDE, WATER DEPARTMENT | SAN LUIS OBISPO | 17641 | 6834 | 1000 | 155000 | 5000 | 303600 | 285000 | 748600 | 149720 | 187150 | 1085470 | 0.3 | 224580 | 1310050 | 1371622.35
CA4000631 | ALMIRA WATER ASSOCIATION | SAN LUIS OBISPO | 40 | 20 | CA4010007 | PASO ROBLES WATER DEPARTMENT | SAN LUIS OBISPO | 32212 | 10727 | 1000 | 155000 | 5000 | 132000 | 285000 | 577000 | 115400 | 144250 | 836650 | 0.3 | 173100 | 1009750 | 1057208.25
CA4000648 | KEN MAR GARDENS | SAN LUIS OBISPO | 84 | 45 | CA4010001 | ARROYO GRANDE, WATER DEPARTMENT | SAN LUIS OBISPO | 17641 | 6834 | 1000 | 155000 | 5000 | 297000 | 285000 | 742000 | 148400 | 185500 | 1075900 | 0.3 | 222600 | 1298500 | 1359529.5
CA4000775 | MUSTANG SPRINGS MUTUAL WATER | SAN LUIS OBISPO | 30 | 16 | CA4010007 | PASO ROBLES WATER DEPARTMENT | SAN LUIS OBISPO | 32212 | 10727 | 1000 | 155000 | 5000 | 105600 | 285000 | 550600 | 110120 | 137650 | 798370 | 0.3 | 165180 | 963550 | 1008836.85
CA4200556 | FOSTER ROAD MUTUAL WATER COMPANY | SANTA BARBARA | 150 | 49 | CA4210016 | GOLDEN STATE WATER COMPANY - ORCUTT | SANTA BARBARA | 32157 | 11710 | 1000 | 155000 | 5000 | 323400 | 285000 | 768400 | 153680 | 192100 | 1114180 | 0.3 | 230520 | 1344700 | 1407900.9
CA4200572 | LAS POSITAS MUTUAL WATER COMPANY | SANTA BARBARA | 200 | 62 | CA4210004 | GOLETA WATER DISTRICT | SANTA BARBARA | 86721 | 16386 | 1000 | 155000 | 5000 | 409200 | 285000 | 854200 | 170840 | 213550 | 1238590 | 0.3 | 256260 | 1494850 | 1565107.95
CA4200633 | LINGATE MUTUAL WATER COMPANY | SANTA BARBARA | 55 | 20 | CA4210007 | MONTECITO WATER DIST | SANTA BARBARA | 11428 | 4632 | 1000 | 155000 | 5000 | 132000 | 285000 | 577000 | 115400 | 144250 | 836650 | 0.3 | 173100 | 1009750 | 1057208.25
CA4200684 | LINCOLNWOOD MUTUAL WATER COMPANY | SANTA BARBARA | 206 | 62 | CA4210010 | CITY OF SANTA BARBARA WATER DEPARTMENT | SANTA BARBARA | 94929 | 27252 | 1000 | 155000 | 5000 | 409200 | 285000 | 854200 | 170840 | 213550 | 1238590 | 0.3 | 256260 | 1494850 | 1565107.95
CA4200842 | SAINT MARIE MOBILE HOME PARK | SANTA BARBARA | 315 | 80 | CA4210011 | SANTA MARIA WATER DEPARTMENT | SANTA BARBARA | 107356 | 22634 | 1000 | 155000 | 5000 | 528000 | 285000 | 973000 | 194600 | 243250 | 1410850 | 0.3 | 291900 | 1702750 | 1782779.25
CA4300571 | SULLIVAN MUTUAL WATER | SANTA CLARA | 53 | 16 | CA4310022 | GREAT OAKS WC INC | SANTA CLARA | 103590 | 21399 | 1000 | 155000 | 5000 | 105600 | 285000 | 550600 | 110120 | 137650 | 798370 | 0.32 | 176192 | 974562 | 1020366.414
CA4300581 | VELLADAO MOBILE HOME PARK | SANTA CLARA | 75 | 27 | CA4310004 | CITY OF GILROY | SANTA CLARA | 57315 | 15220 | 1000 | 155000 | 5000 | 178200 | 285000 | 623200 | 124640 | 155800 | 903640 | 0.32 | 199424 | 1103064 | 1154908.008
CA4300593 | MORGAN HILL USD-MACHADO SCHOOL | SANTA CLARA | 60 | 1 | CA4310006 | CITY OF MORGAN HILL | SANTA CLARA | 46454 | 14593 | 1000 | 155000 | 5000 | 6600 | 285000 | 451600 | 90320 | 112900 | 654820 | 0.32 | 144512 | 799332 | 836900.604
CA4300912 | MECCHI WATER COMPANY | SANTA CLARA | 104 | 27 | CA4310006 | CITY OF MORGAN HILL | SANTA CLARA | 46454 | 14593 | 1000 | 155000 | 5000 | 178200 | 285000 | 623200 | 124640 | 155800 | 903640 | 0.32 | 199424 | 1103064 | 1154908.008
CA4400582 | PINE TREE LANE MUTUAL WATER CO | SANTA CRUZ | 80 | 36 | CA4410017 | SOQUEL CREEK WATER DISTRICT | SANTA CRUZ | 40644 | 14464 | 1000 | 155000 | 5000 | 237600 | 285000 | 682600 | 136520 | 170650 | 989770 | 0.3 | 204780 | 1194550 | 1250693.85
CA4400585 | RIDGEVIEW ESTATES MWC | SANTA CRUZ | 45 | 18 | CA4410014 | SAN LORENZO VALLEY WATER DIST | SANTA CRUZ | 21145 | 6469 | 1000 | 155000 | 5000 | 118800 | 285000 | 563800 | 112760 | 140950 | 817510 | 0.3 | 169140 | 986650 | 1033022.55
CA4400611 | JARVIS MUTUAL WATER SYSTEM | SANTA CRUZ | 125 | 38 | CA4410017 | SOQUEL CREEK WATER DISTRICT | SANTA CRUZ | 40644 | 14464 | 1000 | 155000 | 5000 | 250800 | 285000 | 695800 | 139160 | 173950 | 1008910 | 0.3 | 208740 | 1217650 | 1274879.55
CA4400613 | LAS COLINAS ROAD & WATER ASSN | SANTA CRUZ | 70 | 24 | CA4410011 | WATSONVILLE, CITY OF | SANTA CRUZ | 65384 | 14474 | 1000 | 155000 | 5000 | 158400 | 285000 | 603400 | 120680 | 150850 | 874930 | 0.3 | 181020 | 1055950 | 1105579.65
CA4400621 | RIVER GROVE MUTUAL WATER ASSN | SANTA CRUZ | 54 | 25 | CA4410014 | SAN LORENZO VALLEY WATER DIST | SANTA CRUZ | 21145 | 6469 | 1000 | 155000 | 5000 | 165000 | 285000 | 610000 | 122000 | 152500 | 884500 | 0.3 | 183000 | 1067500 | 1117672.5
CA4400692 | ALLAN LANE WATER ASSOCIATION | SANTA CRUZ | 68 | 17 | CA4410011 | WATSONVILLE, CITY OF | SANTA CRUZ | 65384 | 14474 | 1000 | 155000 | 5000 | 112200 | 285000 | 557200 | 111440 | 139300 | 807940 | 0.3 | 167160 | 975100 | 1020929.7
CA4410001 | BIG BASIN WATER COMPANY | SANTA CRUZ | 1120 | 482 | CA4410014 | SAN LORENZO VALLEY WATER DIST | SANTA CRUZ | 21145 | 6469 | 1000 | 155000 | 5000 | 3181200 | 285000 | 3626200 | 725240 | 906550 | 5257990 | 0.3 | 1087860 | 6345850 | 6644104.95
CA4500012 | CASCADE RACQUET CLUB MUTUAL WATER | SHASTA | 89 | 27 | CA4510005 | CITY OF REDDING | SHASTA | 87741 | 30073 | 1000 | 155000 | 5000 | 178200 | 285000 | 623200 | 124640 | 155800 | 903640 | 0 | 0 | 903640 | 946111.08
CA4500254 | ANDERSON PARK VILLAGE | SHASTA | 112 | 45 | CA4510001 | CITY OF ANDERSON | SHASTA | 11147 | 3586 | 1000 | 155000 | 5000 | 297000 | 285000 | 742000 | 148400 | 185500 | 1075900 | 0 | 0 | 1075900 | 1126467.3
CA4500313 | SHASTA CO CSA # 8 PALO CEDRO | SHASTA | 261 | 79 | CA4510014 | BELLA VISTA WATER DISTRICT | SHASTA | 19098 | 6420 | 1000 | 155000 | 5000 | 521400 | 285000 | 966400 | 193280 | 241600 | 1401280 | 0 | 0 | 1401280 | 1467140.16
CA4510013 | SHASTA C.S.D. | SHASTA | 1584 | 480 | CA4510005 | CITY OF REDDING | SHASTA | 87741 | 30073 | 1000 | 155000 | 5000 | 3168000 | 285000 | 3613000 | 722600 | 903250 | 5238850 | 0 | 0 | 5238850 | 5485075.95
CA4800531 | VACA VILLA APARTMENTS | SOLANO | 60 | 40 | CA4810008 | CITY OF VACAVILLE | SOLANO | 96735 | 29170 | 1000 | 155000 | 5000 | 264000 | 285000 | 709000 | 141800 | 177250 | 1028050 | 0.3 | 212700 | 1240750 | 1299065.25
CA4810011 | SID - ELMIRA | SOLANO | 314 | 88 | CA4810008 | CITY OF VACAVILLE | SOLANO | 96735 | 29170 | 1000 | 155000 | 5000 | 580800 | 285000 | 1025800 | 205160 | 256450 | 1487410 | 0.3 | 307740 | 1795150 | 1879522.05
CA4900510 | SOUTH CLOVERDALE WATER COMPANY | SONOMA | 90 | 39 | CA4910002 | CLOVERDALE, CITY OF | SONOMA | 9157 | 3266 | 1000 | 155000 | 5000 | 257400 | 285000 | 702400 | 140480 | 175600 | 1018480 | 0.3 | 210720 | 1229200 | 1286972.4
CA4900547 | END-O-VALLEY MUTUAL WATER COMPANY | SONOMA | 129 | 39 | CA4910009 | SANTA ROSA, CITY OF | SONOMA | 173648 | 53106 | 1000 | 155000 | 5000 | 257400 | 285000 | 702400 | 140480 | 175600 | 1018480 | 0.3 | 210720 | 1229200 | 1286972.4
CA4900551 | MELITA HEIGHTS MUTUAL WATER COMPANY | SONOMA | 64 | 25 | CA4910009 | SANTA ROSA, CITY OF | SONOMA | 173648 | 53106 | 1000 | 155000 | 5000 | 165000 | 285000 | 610000 | 122000 | 152500 | 884500 | 0.3 | 183000 | 1067500 | 1117672.5
CA4900587 | BRAND WATER COMPANY | SONOMA | 112 | 34 | CA4910009 | SANTA ROSA, CITY OF | SONOMA | 173648 | 53106 | 1000 | 155000 | 5000 | 224400 | 285000 | 669400 | 133880 | 167350 | 970630 | 0.3 | 200820 | 1171450 | 1226508.15
CA4900720 | MOBILE HOME ESTATES | SONOMA | 210 | 150 | CA4910017 | WINDSOR, TOWN OF | SONOMA | 28397 | 8965 | 1000 | 155000 | 5000 | 990000 | 285000 | 1435000 | 287000 | 358750 | 2080750 | 0.3 | 430500 | 2511250 | 2629278.75
CA4900723 | SHAMROCK MOBILE HOME PARK | SONOMA | 188 | 127 | CA4910017 | WINDSOR, TOWN OF | SONOMA | 28397 | 8965 | 1000 | 155000 | 5000 | 838200 | 285000 | 1283200 | 256640 | 320800 | 1860640 | 0.3 | 384960 | 2245600 | 2351143.2
CA4900728 | EVERGREEN MOBILE ESTATES | SONOMA | 70 | 23 | CA4910017 | WINDSOR, TOWN OF | SONOMA | 28397 | 8965 | 1000 | 155000 | 5000 | 151800 | 285000 | 596800 | 119360 | 149200 | 865360 | 0.3 | 179040 | 1044400 | 1093486.8
CA4900794 | SUNSET PARK COMMUNITY | SONOMA | 141 | 42 | CA4910009 | SANTA ROSA, CITY OF | SONOMA | 173648 | 53106 | 1000 | 155000 | 5000 | 277200 | 285000 | 722200 | 144440 | 180550 | 1047190 | 0.3 | 216660 | 1263850 | 1323250.95
CA4900797 | NORTH STAR MOBILE HOME PARK | SONOMA | 75 | 79 | CA4910009 | SANTA ROSA, CITY OF | SONOMA | 173648 | 53106 | 1000 | 155000 | 5000 | 521400 | 285000 | 966400 | 193280 | 241600 | 1401280 | 0.3 | 289920 | 1691200 | 1770686.4
CA4900871 | DE ANZA MOON VALLEY WATER COMPANY | SONOMA | 691 | 247 | CA4910012 | SONOMA, CITY OF | SONOMA | 11923 | 4336 | 1000 | 155000 | 5000 | 1630200 | 285000 | 2075200 | 415040 | 518800 | 3009040 | 0.3 | 622560 | 3631600 | 3802285.2
CA4900901 | SOBRE VISTA WATER COMPANY | SONOMA | 80 | 26 | CA4910013 | VALLEY OF THE MOON WATER DISTRICT | SONOMA | 23077 | 6993 | 1000 | 155000 | 5000 | 171600 | 285000 | 616600 | 123320 | 154150 | 894070 | 0.3 | 184980 | 1079050 | 1129765.35
CA4900913 | ROBIN WAY WATER SYSTEM | SONOMA | 66 | 20 | CA4910009 | SANTA ROSA, CITY OF | SONOMA | 173648 | 53106 | 1000 | 155000 | 5000 | 132000 | 285000 | 577000 | 115400 | 144250 | 836650 | 0.3 | 173100 | 1009750 | 1057208.25
CA5000015 | OID #22 - WILLIAMS TRACT | STANISLAUS | 150 | 53 | CA5010014 | OAKDALE, CITY OF | STANISLAUS | 22348 | 7932 | 1000 | 155000 | 5000 | 349800 | 285000 | 794800 | 158960 | 198700 | 1152460 | 0 | 0 | 1152460 | 1206625.62
CA5000019 | RIVERDALE PARK TRACT CSD | STANISLAUS | 610 | 182 | CA5010010 | MODESTO, CITY OF | STANISLAUS | 219294 | 69918 | 1000 | 155000 | 5000 | 1201200 | 285000 | 1646200 | 329240 | 411550 | 2386990 | 0 | 0 | 2386990 | 2499178.53
CA5000066 | MODESTO MOBILE HOME PARK | STANISLAUS | 300 | 150 | CA5010010 | MODESTO, CITY OF | STANISLAUS | 219294 | 69918 | 1000 | 155000 | 5000 | 990000 | 285000 | 1435000 | 287000 | 358750 | 2080750 | 0 | 0 | 2080750 | 2178545.25
CA5000316 | HAKAM MISSON | STANISLAUS | 45 | 14 | CA5010019 | TURLOCK, CITY OF | STANISLAUS | 74297 | 19038 | 1000 | 155000 | 5000 | 92400 | 285000 | 537400 | 107480 | 134350 | 779230 | 0 | 0 | 779230 | 815853.81
CA5010031 | CITY OF MODESTO - WALNUT MANOR | STANISLAUS | 175 | 53 | CA5010028 | CERES, CITY OF | STANISLAUS | 48706 | 11777 | 1000 | 155000 | 5000 | 349800 | 285000 | 794800 | 158960 | 198700 | 1152460 | 0 | 0 | 1152460 | 1206625.62
CA5010034 | CITY OF MODESTO - NORTH TURLOCK | STANISLAUS | 145 | 52 | CA5010019 | TURLOCK, CITY OF | STANISLAUS | 74297 | 19038 | 1000 | 155000 | 5000 | 343200 | 285000 | 788200 | 157640 | 197050 | 1142890 | 0 | 0 | 1142890 | 1196605.83
CA5200007 | HOWELL'S LAKESIDE WATER CO. | TEHAMA | 75 | 55 | CA5210004 | CITY OF RED BLUFF | TEHAMA | 14076 | 4870 | 1000 | 155000 | 5000 | 363000 | 285000 | 808000 | 161600 | 202000 | 1171600 | 0 | 0 | 1171600 | 1226665.2
CA5200500 | REEDS CREEK ESTATES | TEHAMA | 70 | 25 | CA5210004 | CITY OF RED BLUFF | TEHAMA | 14076 | 4870 | 1000 | 155000 | 5000 | 165000 | 285000 | 610000 | 122000 | 152500 | 884500 | 0 | 0 | 884500 | 926071.5
CA5200535 | LIVE OAK ACRES MWC INC. | TEHAMA | 80 | 40 | CA4510005 | CITY OF REDDING | SHASTA | 87741 | 30073 | 1000 | 155000 | 5000 | 264000 | 285000 | 709000 | 141800 | 177250 | 1028050 | 0 | 0 | 1028050 | 1076368.35
CA5200545 | MODERN VILLAGE MWC | TEHAMA | 85 | 19 | CA5210004 | CITY OF RED BLUFF | TEHAMA | 14076 | 4870 | 1000 | 155000 | 5000 | 125400 | 285000 | 570400 | 114080 | 142600 | 827080 | 0 | 0 | 827080 | 865952.76
CA5200547 | GATEWAY MOBILE HOME PARK | TEHAMA | 75 | 32 | CA5210004 | CITY OF RED BLUFF | TEHAMA | 14076 | 4870 | 1000 | 155000 | 5000 | 211200 | 285000 | 656200 | 131240 | 164050 | 951490 | 0 | 0 | 951490 | 996210.03
CA5200548 | LASSEN VIEW WATER DISTRICT | TEHAMA | 85 | 30 | CA5210004 | CITY OF RED BLUFF | TEHAMA | 14076 | 4870 | 1000 | 155000 | 5000 | 198000 | 285000 | 643000 | 128600 | 160750 | 932350 | 0 | 0 | 932350 | 976170.45
CA5200571 | MOUNTAIN VALLEY APTS & RVP | TEHAMA | 131 | 47 | CA5210004 | CITY OF RED BLUFF | TEHAMA | 14076 | 4870 | 1000 | 155000 | 5000 | 310200 | 285000 | 755200 | 151040 | 188800 | 1095040 | 0 | 0 | 1095040 | 1146506.88
CA5200584 | LITTLE AVENUE WATER SYSTEM | TEHAMA | 53 | 16 | CA5210004 | CITY OF RED BLUFF | TEHAMA | 14076 | 4870 | 1000 | 155000 | 5000 | 105600 | 285000 | 550600 | 110120 | 137650 | 798370 | 0 | 0 | 798370 | 835893.39
CA5400529 | SHADY GROVE MHP, LLC | TULARE | 95 | 42 | CA5410010 | PORTERVILLE, CITY OF | TULARE | 65702 | 17063 | 1000 | 155000 | 5000 | 277200 | 285000 | 722200 | 144440 | 180550 | 1047190 | 0 | 0 | 1047190 | 1096407.93
CA5400655 | CENTRAL MUTUAL WATER CO | TULARE | 119 | 41 | CA5410010 | PORTERVILLE, CITY OF | TULARE | 65702 | 17063 | 1000 | 155000 | 5000 | 270600 | 285000 | 715600 | 143120 | 178900 | 1037620 | 0 | 0 | 1037620 | 1086388.14
CA5500080 | TWAIN HARTE VALLEY MWC | TUOLUMNE | 202 | 106 | CA5510012 | TUD - UPPER BASIN WATER SYSTEM | TUOLUMNE | 9744 | 4005 | 1000 | 155000 | 5000 | 699600 | 285000 | 1144600 | 228920 | 286150 | 1659670 | 0 | 0 | 1659670 | 1737674.49
CA5500115 | SUGAR PINE RV RESORT | TUOLUMNE | 244 | 87 | CA5510012 | TUD - UPPER BASIN WATER SYSTEM | TUOLUMNE | 9744 | 4005 | 1000 | 155000 | 5000 | 574200 | 285000 | 1019200 | 203840 | 254800 | 1477840 | 0 | 0 | 1477840 | 1547298.48
CA5700797 | MONROE/LEINBERGER CNTR - WATERS | YOLO | 800 | 10 | CA5710006 | CITY OF WOODLAND | YOLO | 60978 | 16767 | 1000 | 155000 | 5000 | 66000 | 285000 | 511000 | 102200 | 127750 | 740950 | 0 | 0 | 740950 | 775774.65
CA5800832 | CASTLEWOOD MOBILE HOME PARK | YUBA | 200 | 88 | CA5810002 | LINDA COUNTY WATER DISTRICT | YUBA | 19986 | 5051 | 1000 | 155000 | 5000 | 580800 | 285000 | 1025800 | 205160 | 256450 | 1487410 | 0 | 0 | 1487410 | 1557318.27
Total | [21 empty] | 259968405.954

## Backup Source_New Well
PWSID | WATER SYSTEM NAME | POPULATION | TOTAL SERVICE CONNECTIONS - | TOTAL SOURCE COUNT | TOTAL WELL COUNT | ADD (gpd) | MDD (GPM) | Well Drilling ($) | Well production | Well Development ($) | Well pump and motor ($) | Electrical +SCADA ($) | CEQA ($) | Sum Cost ($) | 25% Planning and Construction ($) | Sum Cost + planning and construction ($) | County | County Multiplier | Cost with Multiplier ($) | Cost before inflation ($) | Final Cost with inflation ($)
CA3200114 | EVERGREEN MOTEL & MHP | 28 | 40 | 1 | 1 | 4200 | 6.5625 | 1200000 | 6.5625 | 33219.6281 | 117345.2906 | 100000 | 85000 | 1535564.9187 | 383891.2297 | 1919456.1484 | PLUMAS | 0 | 0 | 1919456.1484 | 2009670.5874
CA5510503 | YOSEMITE NPS-HODGDON MEADOW | 51 | 51 | 1 | 1 | 7650 | 11.9531 | 1200000 | 11.9531 | 34001.3227 | 118082.3508 | 100000 | 85000 | 1537083.6734 | 384270.9184 | 1921354.5918 | TUOLUMNE | 0 | 0 | 1921354.5918 | 2011658.2576
CA1009051 | CANTUA CREEK VINEYARDS, IV, LLC. | 50 | 16 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | FRESNO | 0 | 0 | 1921272.0508 | 2011571.8372
CA4810012 | SID - QUAIL CANYON | 287 | 40 | 1 | 1 | 43050 | 67.2656 | 1200000 | 67.2656 | 42022.1883 | 125645.2289 | 100000 | 85000 | 1552667.4172 | 388166.8543 | 1940834.2715 | SOLANO | 0.3 | 465800.2252 | 2406634.4966 | 2519746.318
CA1500448 | HILLVIEW ACRES MUTUAL WATER COMPANY | 36 | 47 | 1 | 1 | 5400 | 8.4375 | 1200000 | 8.4375 | 33491.5219 | 117601.6594 | 100000 | 85000 | 1536093.1812 | 384023.2953 | 1920116.4766 | KERN | 0 | 0 | 1920116.4766 | 2010361.951
CA4200578 | PAINTED CAVE | 172 | 91 | 1 | 1 | 25800 | 40.3125 | 1200000 | 40.3125 | 38113.7156 | 121959.9281 | 100000 | 85000 | 1545073.6438 | 386268.4109 | 1931342.0547 | SANTA BARBARA | 0.3 | 463522.0931 | 2394864.1478 | 2507422.7628
CA2700678 | PARADISE RD WS #05 | 42 | 15 | 1 | 1 | 6300 | 9.8438 | 1200000 | 9.8438 | 33695.4422 | 117793.9359 | 100000 | 85000 | 1536489.3781 | 384122.3445 | 1920611.7227 | MONTEREY | 0.3 | 460946.8134 | 2381558.5361 | 2493491.7873
CA2701647 | GREEN ACRES WA | 50 | 20 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | MONTEREY | 0.3 | 461105.2922 | 2382377.343 | 2494349.0781
CA5500124 | MONO VISTA RANCH MHP | 105 | 30 | 1 | 1 | 15750 | 24.6094 | 1200000 | 24.6094 | 35836.6055 | 119812.8398 | 100000 | 85000 | 1540649.4453 | 385162.3613 | 1925811.8066 | TUOLUMNE | 0 | 0 | 1925811.8066 | 2016324.9616
CA0400021 | ROBINSON'S CORNER MHP | 20 | 22 | 1 | 1 | 3000 | 4.6875 | 1200000 | 4.6875 | 32947.7344 | 117088.9219 | 100000 | 85000 | 1535036.6562 | 383759.1641 | 1918795.8203 | BUTTE | 0 | 0 | 1918795.8203 | 2008979.2239
CA3400331 | WESTERNER MOBILE HOME PARK | 65 | 49 | 1 | 1 | 9750 | 15.2344 | 1200000 | 15.2344 | 34477.1367 | 118530.9961 | 100000 | 85000 | 1538008.1328 | 384502.0332 | 1922510.166 | SACRAMENTO | 0.32 | 492162.6025 | 2414672.7685 | 2528162.3886
CA3400130 | THE COURTLAND GROUP | 40 | 34 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | SACRAMENTO | 0.32 | 491634.34 | 2412080.9806 | 2525448.7867
CA3500511 | CASA DE FRUTA ORCHARDS | 53 | 20 | 1 | 1 | 7950 | 12.4219 | 1200000 | 12.4219 | 34069.2961 | 118146.443 | 100000 | 85000 | 1537215.7391 | 384303.9348 | 1921519.6738 | SAN BENITO | 0.3 | 461164.7217 | 2382684.3955 | 2494670.5621
CA1400020 | ABERDEEN WATER SYSTEM | 23 | 75 | 1 | 1 | 3450 | 5.3906 | 1200000 | 5.3906 | 33049.6945 | 117185.0602 | 100000 | 85000 | 1535234.7547 | 383808.6887 | 1919043.4434 | INYO | 0 | 0 | 1919043.4434 | 2009238.4852
CA1000023 | FCSA #14/BELMONT MANOR | 115 | 41 | 1 | 1 | 17250 | 26.9531 | 1200000 | 26.9531 | 36176.4727 | 120133.3008 | 100000 | 85000 | 1541309.7734 | 385327.4434 | 1926637.2168 | FRESNO | 0 | 0 | 1926637.2168 | 2017189.166
CA1000041 | FCWWD #38/SKY HARBOUR | 165 | 64 | 1 | 1 | 24750 | 38.6719 | 1200000 | 38.6719 | 37875.8086 | 121735.6055 | 100000 | 85000 | 1544611.4141 | 386152.8535 | 1930764.2676 | FRESNO | 0 | 0 | 1930764.2676 | 2021510.1882
CA3301630 | BLYTHE - HIDDEN BEACHES | 383 | 116 | 1 | 1 | 57450 | 89.7656 | 1200000 | 89.7656 | 45284.9133 | 128721.6539 | 100000 | 85000 | 1559006.5672 | 389751.6418 | 1948758.209 | RIVERSIDE | 0.32 | 498882.1015 | 2447640.3105 | 2562679.4051
CA4300792 | ABORN HEIGHTS WATER MUTUAL ASSOCIATION | 45 | 19 | 1 | 1 | 6750 | 10.5469 | 1200000 | 10.5469 | 33797.4023 | 117890.0742 | 100000 | 85000 | 1536687.4766 | 384171.8691 | 1920859.3457 | SANTA CLARA | 0.32 | 491739.9925 | 2412599.3382 | 2525991.5071
CA2000592 | TWO TWENTY FOUR MOBILE HOME PK | 35 | 15 | 1 | 1 | 5250 | 8.2031 | 1200000 | 8.2031 | 33457.5352 | 117569.6133 | 100000 | 85000 | 1536027.1484 | 384006.7871 | 1920033.9355 | MADERA | 0 | 0 | 1920033.9355 | 2010275.5305
CA1500475 | KRISTA MUTUAL WATER COMPANY | 501 | 179 | 1 | 1 | 75150 | 117.4219 | 1200000 | 117.4219 | 49295.3461 | 132503.093 | 100000 | 85000 | 1566798.4391 | 391699.6098 | 1958498.0488 | KERN | 0 | 0 | 1958498.0488 | 2050547.4571
CA3100023 | AUBURN MOBILE HOME VILLAGE | 59 | 23 | 1 | 1 | 8850 | 13.8281 | 1200000 | 13.8281 | 34273.2164 | 118338.7195 | 100000 | 85000 | 1537611.9359 | 384402.984 | 1922014.9199 | PLACER | 0 | 0 | 1922014.9199 | 2012349.6212
CA1500575 | SAN JOAQUIN ESTATES MUTUAL WATER COMPANY | 165 | 61 | 1 | 1 | 24750 | 38.6719 | 1200000 | 38.6719 | 37875.8086 | 121735.6055 | 100000 | 85000 | 1544611.4141 | 386152.8535 | 1930764.2676 | KERN | 0 | 0 | 1930764.2676 | 2021510.1882
CA3900755 | SHADY REST TRAILER COURT | 120 | 49 | 1 | 1 | 18000 | 28.125 | 1200000 | 28.125 | 36346.4062 | 120293.5312 | 100000 | 85000 | 1541639.9375 | 385409.9844 | 1927049.9219 | SAN JOAQUIN | 0 | 0 | 1927049.9219 | 2017621.2682
CA3900719 | MOKELUMNE MOBILE SENIOR PARK | 55 | 25 | 1 | 1 | 8250 | 12.8906 | 1200000 | 12.8906 | 34137.2695 | 118210.5352 | 100000 | 85000 | 1537347.8047 | 384336.9512 | 1921684.7559 | SAN JOAQUIN | 0 | 0 | 1921684.7559 | 2012003.9394
CA1500507 | ST. CLAIR RANCHOS MUTUAL WATER CO. | 105 | 32 | 1 | 1 | 15750 | 24.6094 | 1200000 | 24.6094 | 35836.6055 | 119812.8398 | 100000 | 85000 | 1540649.4453 | 385162.3613 | 1925811.8066 | KERN | 0 | 0 | 1925811.8066 | 2016324.9616
CA5700554 | CAMPERS INN - RV & GOLF COURSE | 120 | 68 | 1 | 1 | 18000 | 28.125 | 1200000 | 28.125 | 36346.4062 | 120293.5312 | 100000 | 85000 | 1541639.9375 | 385409.9844 | 1927049.9219 | YOLO | 0 | 0 | 1927049.9219 | 2017621.2682
CA0300019 | FIDDLETOWN COMMUNITY SERVICE | 100 | 66 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | AMADOR | 0 | 0 | 1925399.1016 | 2015892.8593
CA4900605 | MARK WEST ACRES MWC | 61 | 22 | 1 | 1 | 9150 | 14.2969 | 1200000 | 14.2969 | 34341.1898 | 118402.8117 | 100000 | 85000 | 1537744.0016 | 384436.0004 | 1922180.002 | SONOMA | 0.3 | 461323.2005 | 2383503.2024 | 2495527.8529
CA2701897 | BERRY DR WS #02 | 50 | 19 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | MONTEREY | 0.3 | 461105.2922 | 2382377.343 | 2494349.0781
CA4900533 | MORTON'S WARM SPRINGS / SONOMA SPRINGS | 59 | 21 | 1 | 1 | 8850 | 13.8281 | 1200000 | 13.8281 | 34273.2164 | 118338.7195 | 100000 | 85000 | 1537611.9359 | 384402.984 | 1922014.9199 | SONOMA | 0.3 | 461283.5808 | 2383298.5007 | 2495313.5302
CA1500327 | RANCHO SECO INC. WATER SYSTEM | 55 | 23 | 1 | 1 | 8250 | 12.8906 | 1200000 | 12.8906 | 34137.2695 | 118210.5352 | 100000 | 85000 | 1537347.8047 | 384336.9512 | 1921684.7559 | KERN | 0 | 0 | 1921684.7559 | 2012003.9394
CA1502564 | SIERRA MEADOWS | 68 | 51 | 1 | 1 | 10200 | 15.9375 | 1200000 | 15.9375 | 34579.0969 | 118627.1344 | 100000 | 85000 | 1538206.2312 | 384551.5578 | 1922757.7891 | KERN | 0 | 0 | 1922757.7891 | 2013127.4051
CA0400027 | FOOTHILL SOLAR COMPANY | 180 | 127 | 1 | 1 | 27000 | 42.1875 | 1200000 | 42.1875 | 38385.6094 | 122216.2969 | 100000 | 85000 | 1545601.9062 | 386400.4766 | 1932002.3828 | BUTTE | 0 | 0 | 1932002.3828 | 2022806.4948
CA3900813 | HAVEN ACRES RIVER CLUB INC | 100 | 51 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SAN JOAQUIN | 0 | 0 | 1925399.1016 | 2015892.8593
CA2700541 | DEL MONTE FARMS RD WS #03 | 55 | 16 | 1 | 1 | 8250 | 12.8906 | 1200000 | 12.8906 | 34137.2695 | 118210.5352 | 100000 | 85000 | 1537347.8047 | 384336.9512 | 1921684.7559 | MONTEREY | 0.3 | 461204.3414 | 2382889.0973 | 2494884.8848
CA2700638 | MAHER RD WS #05 | 65 | 17 | 1 | 1 | 9750 | 15.2344 | 1200000 | 15.2344 | 34477.1367 | 118530.9961 | 100000 | 85000 | 1538008.1328 | 384502.0332 | 1922510.166 | MONTEREY | 0.3 | 461402.4398 | 2383912.6059 | 2495956.4983
CA2400201 | VOLTA COMMUNITY SD | 156 | 44 | 1 | 1 | 23400 | 36.5625 | 1200000 | 36.5625 | 37569.9281 | 121447.1906 | 100000 | 85000 | 1544017.1187 | 386004.2797 | 1930021.3984 | MERCED | 0 | 0 | 1930021.3984 | 2020732.4042
CA2700522 | CABANA HOLIDAY WS | 400 | 146 | 1 | 1 | 60000 | 93.75 | 1200000 | 93.75 | 45862.6875 | 129266.4375 | 100000 | 85000 | 1560129.125 | 390032.2812 | 1950161.4062 | MONTEREY | 0.3 | 468038.7375 | 2418200.1437 | 2531855.5505
CA3900733 | COUNTRY CLUB VISTA MUTUAL WATER CO | 75 | 31 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | SAN JOAQUIN | 0 | 0 | 1923335.5762 | 2013732.3483
CA4900736 | CLEAR CREEK WATER COMPANY | 40 | 19 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | SONOMA | 0.3 | 460907.1937 | 2381353.8344 | 2493277.4646
CA5301103 | COVINGTON MILL - A | 60 | 42 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | TRINITY | 0 | 0 | 1922097.4609 | 2012436.0416
CA4500303 | TUCKER OAKS EAST WATER DISTRICT | 95 | 34 | 1 | 1 | 14250 | 22.2656 | 1200000 | 22.2656 | 35496.7383 | 119492.3789 | 100000 | 85000 | 1539989.1172 | 384997.2793 | 1924986.3965 | SHASTA | 0 | 0 | 1924986.3965 | 2015460.7571
CA2300731 | CITY OF 10,000 BUDDHAS | 200 | 50 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | MENDOCINO | 0 | 0 | 1933653.2031 | 2024534.9037
CA1502659 | OWENS PEAK SOUTH | 40 | 17 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | KERN | 0 | 0 | 1920446.6406 | 2010707.6327
CA0400019 | OROVILLE MOBILE HOME PARK | 74 | 35 | 1 | 1 | 11100 | 17.3438 | 1200000 | 17.3438 | 34783.0172 | 118819.4109 | 100000 | 85000 | 1538602.4281 | 384650.607 | 1923253.0352 | BUTTE | 0 | 0 | 1923253.0352 | 2013645.9278
CA4500018 | SALT CREEK SUMMER HOMES | 151 | 47 | 1 | 1 | 22650 | 35.3906 | 1200000 | 35.3906 | 37399.9945 | 121286.9602 | 100000 | 85000 | 1543686.9547 | 385921.7387 | 1929608.6934 | SHASTA | 0 | 0 | 1929608.6934 | 2020300.3019
CA3400149 | RANCHO MARINA | 250 | 77 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | SACRAMENTO | 0.32 | 496071.745 | 2433851.9989 | 2548243.0429
CA1700579 | VILLA BLUE ESTATES WATER DISTRICT | 60 | 21 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | LAKE | 0 | 0 | 1922097.4609 | 2012436.0416
CA3301682 | TRAILS END MUTUAL WATER COMPANY | 52 | 34 | 1 | 1 | 7800 | 12.1875 | 1200000 | 12.1875 | 34035.3094 | 118114.3969 | 100000 | 85000 | 1537149.7063 | 384287.4266 | 1921437.1328 | RIVERSIDE | 0.32 | 491887.906 | 2413325.0388 | 2526751.3156
CA2701570 | LOS CARNEROS MWA | 105 | 24 | 1 | 1 | 15750 | 24.6094 | 1200000 | 24.6094 | 35836.6055 | 119812.8398 | 100000 | 85000 | 1540649.4453 | 385162.3613 | 1925811.8066 | MONTEREY | 0.3 | 462194.8336 | 2388006.6402 | 2500242.9523
CA0400041 | FOREST RANCH MOBILE PARK | 25 | 16 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | BUTTE | 0 | 0 | 1919208.5254 | 2009411.3261
CA2700772 | STRUVE RD WS #02 | 166 | 105 | 1 | 1 | 24900 | 38.9062 | 1200000 | 38.9062 | 37909.7953 | 121767.6516 | 100000 | 85000 | 1544677.4469 | 386169.3617 | 1930846.8086 | MONTEREY | 0.3 | 463403.2341 | 2394250.0427 | 2506779.7947
CA0400026 | MEADOWBROOK OAKS | 50 | 26 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | BUTTE | 0 | 0 | 1921272.0508 | 2011571.8372
CA4500247 | WEST COTTONWOOD APARTMENTS | 35 | 17 | 1 | 1 | 5250 | 8.2031 | 1200000 | 8.2031 | 33457.5352 | 117569.6133 | 100000 | 85000 | 1536027.1484 | 384006.7871 | 1920033.9355 | SHASTA | 0 | 0 | 1920033.9355 | 2010275.5305
CA0400004 | FOREST RANCH MUTUAL WATER SYSTEM | 92 | 42 | 1 | 1 | 13800 | 21.5625 | 1200000 | 21.5625 | 35394.7781 | 119396.2406 | 100000 | 85000 | 1539791.0188 | 384947.7547 | 1924738.7734 | BUTTE | 0 | 0 | 1924738.7734 | 2015201.4958
CA5200531 | RIVER POINTE LANDING MHP | 104 | 40 | 1 | 1 | 15600 | 24.375 | 1200000 | 24.375 | 35802.6188 | 119780.7937 | 100000 | 85000 | 1540583.4125 | 385145.8531 | 1925729.2656 | TEHAMA | 0 | 0 | 1925729.2656 | 2016238.5411
CA0300011 | SUTTER PINES MHP | 40 | 19 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | AMADOR | 0 | 0 | 1920446.6406 | 2010707.6327
CA3310080 | LAKE HEMET MWD-CAMP GROUND | 600 | 287 | 1 | 1 | 90000 | 140.625 | 1200000 | 140.625 | 52660.0312 | 135675.6562 | 100000 | 85000 | 1573335.6875 | 393333.9219 | 1966669.6094 | RIVERSIDE | 0.32 | 503467.42 | 2470137.0294 | 2586233.4698
CA1400078 | SCE BISHOP CREEK PLANT 4 | 38 | 15 | 1 | 1 | 5700 | 8.9062 | 1200000 | 8.9062 | 33559.4953 | 117665.7516 | 100000 | 85000 | 1536225.2469 | 384056.3117 | 1920281.5586 | INYO | 0 | 0 | 1920281.5586 | 2010534.7918
CA3900831 | ARBOR MOBILE HOME PARK WS | 340 | 173 | 1 | 1 | 51000 | 79.6875 | 1200000 | 79.6875 | 43823.4844 | 127343.6719 | 100000 | 85000 | 1556167.1562 | 389041.7891 | 1945208.9453 | SAN JOAQUIN | 0 | 0 | 1945208.9453 | 2036633.7657
CA1100445 | ORLAND MOBILE H.P. | 178 | 54 | 1 | 1 | 26700 | 41.7188 | 1200000 | 41.7188 | 38317.6359 | 122152.2047 | 100000 | 85000 | 1545469.8406 | 386367.4602 | 1931837.3008 | GLENN | 0 | 0 | 1931837.3008 | 2022633.6539
CA1500458 | R.S. MUTUAL WATER COMPANY | 67 | 24 | 1 | 1 | 10050 | 15.7031 | 1200000 | 15.7031 | 34545.1102 | 118595.0883 | 100000 | 85000 | 1538140.1984 | 384535.0496 | 1922675.248 | KERN | 0 | 0 | 1922675.248 | 2013040.9847
CA1502750 | RIVERVIEW HOMEOWNERS ASSOCIATION | 40 | 20 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | KERN | 0 | 0 | 1920446.6406 | 2010707.6327
CA2702004 | CAL AM WATER COMPANY - RALPH LANE | 96 | 27 | 1 | 1 | 14400 | 22.5 | 1200000 | 22.5 | 35530.725 | 119524.425 | 100000 | 85000 | 1540055.15 | 385013.7875 | 1925068.9375 | MONTEREY | 0.3 | 462016.545 | 2387085.4825 | 2499278.5002
CA0400091 | DEL ORO WATER COMPANY - BUZZTAIL DIST. | 99 | 30 | 1 | 1 | 14850 | 23.2031 | 1200000 | 23.2031 | 35632.6852 | 119620.5633 | 100000 | 85000 | 1540253.2484 | 385063.3121 | 1925316.5605 | BUTTE | 0 | 0 | 1925316.5605 | 2015806.4389
CA1500540 | PINON VALLEY WATER COMPANY | 109 | 39 | 1 | 1 | 16350 | 25.5469 | 1200000 | 25.5469 | 35972.5523 | 119941.0242 | 100000 | 85000 | 1540913.5766 | 385228.3941 | 1926141.9707 | KERN | 0 | 0 | 1926141.9707 | 2016670.6433
CA0400012 | FARM LABOR HOUSING | 460 | 135 | 1 | 1 | 69000 | 107.8125 | 1200000 | 107.8125 | 47901.8906 | 131189.2031 | 100000 | 85000 | 1564091.0938 | 391022.7734 | 1955113.8672 | BUTTE | 0 | 0 | 1955113.8672 | 2047004.2189
CA5400505 | HARTLAND CHRISTIAN CAMP | 250 | 54 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | TULARE | 0 | 0 | 1937780.2539 | 2028855.9258
CA4500203 | RAPID RIVER MOBILEHOME PARK | 92 | 44 | 1 | 1 | 13800 | 21.5625 | 1200000 | 21.5625 | 35394.7781 | 119396.2406 | 100000 | 85000 | 1539791.0188 | 384947.7547 | 1924738.7734 | SHASTA | 0 | 0 | 1924738.7734 | 2015201.4958
CA2900541 | CHRISTIAN ENCOUNTER MINISTRIES | 35 | 16 | 1 | 1 | 5250 | 8.2031 | 1200000 | 8.2031 | 33457.5352 | 117569.6133 | 100000 | 85000 | 1536027.1484 | 384006.7871 | 1920033.9355 | NEVADA | 0 | 0 | 1920033.9355 | 2010275.5305
CA3301676 | THOMAS MOUNTAIN WATER COMPANY | 162 | 57 | 1 | 1 | 24300 | 37.9688 | 1200000 | 37.9688 | 37773.8484 | 121639.4672 | 100000 | 85000 | 1544413.3156 | 386103.3289 | 1930516.6445 | RIVERSIDE | 0.32 | 494212.261 | 2424728.9055 | 2538691.1641
CA1100452 | SHADY OAKS TRAILER PARK | 57 | 43 | 1 | 1 | 8550 | 13.3594 | 1200000 | 13.3594 | 34205.243 | 118274.6273 | 100000 | 85000 | 1537479.8703 | 384369.9676 | 1921849.8379 | GLENN | 0 | 0 | 1921849.8379 | 2012176.7803
CA5400537 | LINDYS LANDING | 49 | 177 | 1 | 1 | 7350 | 11.4844 | 1200000 | 11.4844 | 33933.3492 | 118018.2586 | 100000 | 85000 | 1536951.6078 | 384237.902 | 1921189.5098 | TULARE | 0 | 0 | 1921189.5098 | 2011485.4167
CA1500459 | LAKE OF THE WOODS MOBILE VILLAGE | 82 | 86 | 1 | 1 | 12300 | 19.2188 | 1200000 | 19.2188 | 35054.9109 | 119075.7797 | 100000 | 85000 | 1539130.6906 | 384782.6727 | 1923913.3633 | KERN | 0 | 0 | 1923913.3633 | 2014337.2914
CA2701046 | CAMPHORA APARTMENTS | 126 | 42 | 1 | 1 | 18900 | 29.5312 | 1200000 | 29.5312 | 36550.3266 | 120485.8078 | 100000 | 85000 | 1542036.1344 | 385509.0336 | 1927545.168 | MONTEREY | 0.3 | 462610.8403 | 2390156.0083 | 2502493.3407
CA3500509 | TRES PINOS CWD | 350 | 121 | 1 | 1 | 52500 | 82.0312 | 1200000 | 82.0312 | 44163.3516 | 127664.1328 | 100000 | 85000 | 1556827.4844 | 389206.8711 | 1946034.3555 | SAN BENITO | 0.3 | 467048.2453 | 2413082.6008 | 2526497.483
CA1000445 | LINDA VISTA FARMS | 63 | 17 | 1 | 1 | 9450 | 14.7656 | 1200000 | 14.7656 | 34409.1633 | 118466.9039 | 100000 | 85000 | 1537876.0672 | 384469.0168 | 1922345.084 | FRESNO | 0 | 0 | 1922345.084 | 2012695.3029
CA5200508 | RIO VISTA MOBILE HOME PARK | 543 | 195 | 1 | 1 | 81450 | 127.2656 | 1200000 | 127.2656 | 50722.7883 | 133849.0289 | 100000 | 85000 | 1569571.8172 | 392392.9543 | 1961964.7715 | TEHAMA | 0 | 0 | 1961964.7715 | 2054177.1157
CA5400666 | DEL ORO GRANDVIEW GARDENS DISTRICT | 327 | 98 | 1 | 1 | 49050 | 76.6406 | 1200000 | 76.6406 | 43381.657 | 126927.0727 | 100000 | 85000 | 1555308.7297 | 388827.1824 | 1944135.9121 | TULARE | 0 | 0 | 1944135.9121 | 2035510.3
CA4000563 | HIGUERA APARTMENTS | 30 | 24 | 1 | 1 | 4500 | 7.0312 | 1200000 | 7.0312 | 33287.6016 | 117409.3828 | 100000 | 85000 | 1535696.9844 | 383924.2461 | 1919621.2305 | SAN LUIS OBISPO | 0.3 | 460709.0953 | 2380330.3258 | 2492205.8511
CA1500591 | SWEET WATER CO-OP | 47 | 15 | 1 | 1 | 7050 | 11.0156 | 1200000 | 11.0156 | 33865.3758 | 117954.1664 | 100000 | 85000 | 1536819.5422 | 384204.8855 | 1921024.4277 | KERN | 0 | 0 | 1921024.4277 | 2011312.5758
CA2000865 | MD 58 SIERRA HIGHLANDS | 75 | 25 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | MADERA | 0 | 0 | 1923335.5762 | 2013732.3483
CA1000057 | DEL ORO WATER CO - METROPOLITAN DISTRICT | 96 | 29 | 1 | 1 | 14400 | 22.5 | 1200000 | 22.5 | 35530.725 | 119524.425 | 100000 | 85000 | 1540055.15 | 385013.7875 | 1925068.9375 | FRESNO | 0 | 0 | 1925068.9375 | 2015547.1776
CA3205001 | WALKER RANCH CSD | 50 | 1107 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | PLUMAS | 0 | 0 | 1921272.0508 | 2011571.8372
CA4200851 | ROLLING HILLS MUTUAL WATER COMPANY | 66 | 21 | 1 | 1 | 9900 | 15.4688 | 1200000 | 15.4688 | 34511.1234 | 118563.0422 | 100000 | 85000 | 1538074.1656 | 384518.5414 | 1922592.707 | SANTA BARBARA | 0.3 | 461422.2497 | 2384014.9567 | 2496063.6597
CA2300596 | BIG RIVER VISTA MUTUAL WATER COMPANY | 36 | 19 | 1 | 1 | 5400 | 8.4375 | 1200000 | 8.4375 | 33491.5219 | 117601.6594 | 100000 | 85000 | 1536093.1812 | 384023.2953 | 1920116.4766 | MENDOCINO | 0 | 0 | 1920116.4766 | 2010361.951
CA0900404 | OAKLANE MOBILE VILLAGE, LLC. | 75 | 35 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | EL DORADO | 0.3 | 461600.5383 | 2384936.1145 | 2497028.1118
CA3600399 | PARADISE MOBILE ESTATES | 190 | 38 | 1 | 1 | 28500 | 44.5312 | 1200000 | 44.5312 | 38725.4766 | 122536.7578 | 100000 | 85000 | 1546262.2344 | 386565.5586 | 1932827.793 | SAN BERNARDINO | 0.3 | 463878.6703 | 2396706.4633 | 2509351.6671
CA3901217 | HAYNES BOARD & CARE HOME | 41 | 15 | 1 | 1 | 6150 | 9.6094 | 1200000 | 9.6094 | 33661.4555 | 117761.8898 | 100000 | 85000 | 1536423.3453 | 384105.8363 | 1920529.1816 | SAN JOAQUIN | 0 | 0 | 1920529.1816 | 2010794.0532
CA1100413 | COUNTRY LEISURE MOBILE ESTATES | 40 | 33 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | GLENN | 0 | 0 | 1920446.6406 | 2010707.6327
CA4900653 | LONE PINE MUTUAL WATER COMPANY | 65 | 28 | 1 | 1 | 9750 | 15.2344 | 1200000 | 15.2344 | 34477.1367 | 118530.9961 | 100000 | 85000 | 1538008.1328 | 384502.0332 | 1922510.166 | SONOMA | 0.3 | 461402.4398 | 2383912.6059 | 2495956.4983
CA0400023 | GOLDEN OAKS MOBILE ESTATES | 34 | 52 | 1 | 1 | 5100 | 7.9688 | 1200000 | 7.9688 | 33423.5484 | 117537.5672 | 100000 | 85000 | 1535961.1156 | 383990.2789 | 1919951.3945 | BUTTE | 0 | 0 | 1919951.3945 | 2010189.1101
CA5400616 | LEMON COVE WATER CO | 109 | 60 | 1 | 1 | 16350 | 25.5469 | 1200000 | 25.5469 | 35972.5523 | 119941.0242 | 100000 | 85000 | 1540913.5766 | 385228.3941 | 1926141.9707 | TULARE | 0 | 0 | 1926141.9707 | 2016670.6433
CA5200539 | FRIENDLY ACRES MHP | 75 | 51 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | TEHAMA | 0 | 0 | 1923335.5762 | 2013732.3483
CA5305103 | MAD RIVER COMPOUND - USFS | 57 | 16 | 1 | 1 | 8550 | 13.3594 | 1200000 | 13.3594 | 34205.243 | 118274.6273 | 100000 | 85000 | 1537479.8703 | 384369.9676 | 1921849.8379 | TRINITY | 0 | 0 | 1921849.8379 | 2012176.7803
CA5800824 | COUNTRY VILLAGE MOBILE HOME PARK | 50 | 45 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | YUBA | 0 | 0 | 1921272.0508 | 2011571.8372
CA1100436 | ORLAND OAKS MHP | 186 | 83 | 1 | 1 | 27900 | 43.5938 | 1200000 | 43.5938 | 38589.5297 | 122408.5734 | 100000 | 85000 | 1545998.1031 | 386499.5258 | 1932497.6289 | GLENN | 0 | 0 | 1932497.6289 | 2023325.0175
CA3400169 | SPINDRIFT MARINA | 100 | 50 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SACRAMENTO | 0.32 | 492902.17 | 2418301.2716 | 2531961.4313
CA0400149 | HUMBOLDT WOODLANDS MUTUAL | 75 | 31 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | BUTTE | 0 | 0 | 1923335.5762 | 2013732.3483
CA1400099 | MOUNTAIN VIEW TRAILER COURT | 53 | 24 | 1 | 1 | 7950 | 12.4219 | 1200000 | 12.4219 | 34069.2961 | 118146.443 | 100000 | 85000 | 1537215.7391 | 384303.9348 | 1921519.6738 | INYO | 0 | 0 | 1921519.6738 | 2011831.0985
CA2700792 | SUMMERHILL MHP WS | 95 | 34 | 1 | 1 | 14250 | 22.2656 | 1200000 | 22.2656 | 35496.7383 | 119492.3789 | 100000 | 85000 | 1539989.1172 | 384997.2793 | 1924986.3965 | MONTEREY | 0.3 | 461996.7352 | 2386983.1316 | 2499171.3388
CA0400155 | BIGGERS GLEN MUTUAL WATER CO | 25 | 29 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | BUTTE | 0 | 0 | 1919208.5254 | 2009411.3261
CA1500426 | ROSE VILLA APARTMENTS | 65 | 32 | 1 | 1 | 9750 | 15.2344 | 1200000 | 15.2344 | 34477.1367 | 118530.9961 | 100000 | 85000 | 1538008.1328 | 384502.0332 | 1922510.166 | KERN | 0 | 0 | 1922510.166 | 2012868.1438
CA1500571 | KERN MOBILE ESTATES LLC | 73 | 60 | 1 | 1 | 10950 | 17.1094 | 1200000 | 17.1094 | 34749.0305 | 118787.3648 | 100000 | 85000 | 1538536.3953 | 384634.0988 | 1923170.4941 | KERN | 0 | 0 | 1923170.4941 | 2013559.5074
CA1502232 | ROSAMOND MOBILEHOME PARK | 175 | 79 | 1 | 1 | 26250 | 41.0156 | 1200000 | 41.0156 | 38215.6758 | 122056.0664 | 100000 | 85000 | 1545271.7422 | 386317.9355 | 1931589.6777 | KERN | 0 | 0 | 1931589.6777 | 2022374.3926
CA2701740 | BLUFFS WS | 120 | 44 | 1 | 1 | 18000 | 28.125 | 1200000 | 28.125 | 36346.4062 | 120293.5312 | 100000 | 85000 | 1541639.9375 | 385409.9844 | 1927049.9219 | MONTEREY | 0.3 | 462491.9813 | 2389541.9031 | 2501850.3726
CA3500527 | VALENZUELA WATER SYSTEM | 55 | 17 | 1 | 1 | 8250 | 12.8906 | 1200000 | 12.8906 | 34137.2695 | 118210.5352 | 100000 | 85000 | 1537347.8047 | 384336.9512 | 1921684.7559 | SAN BENITO | 0.3 | 461204.3414 | 2382889.0973 | 2494884.8848
CA5000058 | FISHERMAN'S BEND MHP | 120 | 66 | 1 | 1 | 18000 | 28.125 | 1200000 | 28.125 | 36346.4062 | 120293.5312 | 100000 | 85000 | 1541639.9375 | 385409.9844 | 1927049.9219 | STANISLAUS | 0 | 0 | 1927049.9219 | 2017621.2682
CA1502247 | DESERT BREEZE MOBILE HOME ESTATES | 82 | 63 | 1 | 1 | 12300 | 19.2188 | 1200000 | 19.2188 | 35054.9109 | 119075.7797 | 100000 | 85000 | 1539130.6906 | 384782.6727 | 1923913.3633 | KERN | 0 | 0 | 1923913.3633 | 2014337.2914
CA4500008 | LAKESHORE VILLA MUTUAL WATER CO | 81 | 40 | 1 | 1 | 12150 | 18.9844 | 1200000 | 18.9844 | 35020.9242 | 119043.7336 | 100000 | 85000 | 1539064.6578 | 384766.1645 | 1923830.8223 | SHASTA | 0 | 0 | 1923830.8223 | 2014250.8709
CA4500098 | ANDERSON MOBILE HOME PARK | 70 | 21 | 1 | 1 | 10500 | 16.4062 | 1200000 | 16.4062 | 34647.0703 | 118691.2266 | 100000 | 85000 | 1538338.2969 | 384584.5742 | 1922922.8711 | SHASTA | 0 | 0 | 1922922.8711 | 2013300.246
CA0400090 | MOUNTAIN VILLAGE HOMEOWNER'S ASSOC | 40 | 17 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | BUTTE | 0 | 0 | 1920446.6406 | 2010707.6327
CA5200559 | ABBEY OF NEW CLAIRVAUX | 25 | 22 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | TEHAMA | 0 | 0 | 1919208.5254 | 2009411.3261
CA2700992 | MILLER'S LODGE WS | 25 | 51 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | MONTEREY | 0.3 | 460610.0461 | 2379818.5715 | 2491670.0443
CA1502465 | PANAMA ROAD PROPERTY OWNERS ASSOC | 45 | 16 | 1 | 1 | 6750 | 10.5469 | 1200000 | 10.5469 | 33797.4023 | 117890.0742 | 100000 | 85000 | 1536687.4766 | 384171.8691 | 1920859.3457 | KERN | 0 | 0 | 1920859.3457 | 2011139.735
CA2000512 | EAST ACRES MUTUAL WATER COMPANY | 250 | 85 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | MADERA | 0 | 0 | 1937780.2539 | 2028855.9258
CA2000724 | SA 14 CHUK CHANSE SUBDIVISION | 100 | 31 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | MADERA | 0 | 0 | 1925399.1016 | 2015892.8593
CA2700682 | PARADISE RD WS #09 | 206 | 17 | 1 | 1 | 30900 | 48.2812 | 1200000 | 48.2812 | 39269.2641 | 123049.4953 | 100000 | 85000 | 1547318.7594 | 386829.6898 | 1934148.4492 | MONTEREY | 0.3 | 464195.6278 | 2398344.077 | 2511066.2487
CA2300743 | DOLPHIN ISLE MARINA | 560 | 86 | 1 | 1 | 84000 | 131.25 | 1200000 | 131.25 | 51300.5625 | 134393.8125 | 100000 | 85000 | 1570694.375 | 392673.5938 | 1963367.9688 | MENDOCINO | 0 | 0 | 1963367.9688 | 2055646.2633
CA2300705 | LITTLE LAKE MOBILE HOME PARK | 38 | 19 | 1 | 1 | 5700 | 8.9062 | 1200000 | 8.9062 | 33559.4953 | 117665.7516 | 100000 | 85000 | 1536225.2469 | 384056.3117 | 1920281.5586 | MENDOCINO | 0 | 0 | 1920281.5586 | 2010534.7918
CA0202522 | SIERRA PINES MOBILE HOME PARK | 70 | 32 | 1 | 1 | 10500 | 16.4062 | 1200000 | 16.4062 | 34647.0703 | 118691.2266 | 100000 | 85000 | 1538338.2969 | 384584.5742 | 1922922.8711 | ALPINE | 0 | 0 | 1922922.8711 | 2013300.246
CA3400135 | KORTHS PIRATES LAIR | 150 | 64 | 1 | 1 | 22500 | 35.1562 | 1200000 | 35.1562 | 37366.0078 | 121254.9141 | 100000 | 85000 | 1543620.9219 | 385905.2305 | 1929526.1523 | SACRAMENTO | 0.32 | 493958.695 | 2423484.8473 | 2537388.6352
CA1000551 | FCSA #43/RAISIN CITY | 190 | 68 | 1 | 1 | 28500 | 44.5312 | 1200000 | 44.5312 | 38725.4766 | 122536.7578 | 100000 | 85000 | 1546262.2344 | 386565.5586 | 1932827.793 | FRESNO | 0 | 0 | 1932827.793 | 2023670.6992
CA0800557 | HUNTER VALLEY CSD | 96 | 62 | 1 | 1 | 14400 | 22.5 | 1200000 | 22.5 | 35530.725 | 119524.425 | 100000 | 85000 | 1540055.15 | 385013.7875 | 1925068.9375 | DEL NORTE | 0 | 0 | 1925068.9375 | 2015547.1776
CA3701934 | PINE VALLEY BIBLE CONFERENCE CENTER | 350 | 57 | 1 | 1 | 52500 | 82.0312 | 1200000 | 82.0312 | 44163.3516 | 127664.1328 | 100000 | 85000 | 1556827.4844 | 389206.8711 | 1946034.3555 | SAN DIEGO | 0.32 | 498184.795 | 2444219.1505 | 2559097.4505
CA4900789 | BLUE SPRUCE MOBILE HOME PARK | 90 | 56 | 1 | 1 | 13500 | 21.0938 | 1200000 | 21.0938 | 35326.8047 | 119332.1484 | 100000 | 85000 | 1539658.9531 | 384914.7383 | 1924573.6914 | SONOMA | 0.3 | 461897.6859 | 2386471.3773 | 2498635.5321
CA5401026 | DEER MEADOW MUTUAL WATER COMPANY | 67 | 25 | 1 | 1 | 10050 | 15.7031 | 1200000 | 15.7031 | 34545.1102 | 118595.0883 | 100000 | 85000 | 1538140.1984 | 384535.0496 | 1922675.248 | TULARE | 0 | 0 | 1922675.248 | 2013040.9847
CA1900541 | WESTERN SKIES MOBILE HOME PARK | 198 | 61 | 1 | 1 | 29700 | 46.4062 | 1200000 | 46.4062 | 38997.3703 | 122793.1266 | 100000 | 85000 | 1546790.4969 | 386697.6242 | 1933488.1211 | LOS ANGELES | 0.32 | 494972.959 | 2428461.0801 | 2542598.7509
CA5610702 | U.S.N., SAN NICOLAS ISLAND | 187 | 106 | 1 | 1 | 28050 | 43.8281 | 1200000 | 43.8281 | 38623.5164 | 122440.6195 | 100000 | 85000 | 1546064.1359 | 386516.034 | 1932580.1699 | VENTURA | 0.32 | 494740.5235 | 2427320.6934 | 2541404.766
CA3500836 | BETABEL RV RESORT | 49 | 176 | 1 | 1 | 7350 | 11.4844 | 1200000 | 11.4844 | 33933.3492 | 118018.2586 | 100000 | 85000 | 1536951.6078 | 384237.902 | 1921189.5098 | SAN BENITO | 0.3 | 461085.4823 | 2382274.9921 | 2494241.9167
CA1700527 | MOUNTAIN OF ATTENTION WATER | 40 | 26 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | LAKE | 0 | 0 | 1920446.6406 | 2010707.6327
CA5800803 | LOMA RICA WATER COMPANY | 200 | 70 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | YUBA | 0 | 0 | 1933653.2031 | 2024534.9037
CA3900559 | WINE COUNTRY APARTMENTS | 40 | 16 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | SAN JOAQUIN | 0 | 0 | 1920446.6406 | 2010707.6327
CA5000263 | OASIS INVESTMENTS | 75 | 31 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | STANISLAUS | 0 | 0 | 1923335.5762 | 2013732.3483
CA3900983 | CHERRY LANE TRAILER PARK | 100 | 43 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SAN JOAQUIN | 0 | 0 | 1925399.1016 | 2015892.8593
CA3901114 | KING ISLAND TRAILER PARK WATER SYSTEM | 200 | 76 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | SAN JOAQUIN | 0 | 0 | 1933653.2031 | 2024534.9037
CA5200008 | BREESE SUBDIVISION 2 | 75 | 30 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | TEHAMA | 0 | 0 | 1923335.5762 | 2013732.3483
CA3900701 | CURRIER ESTATES WATER CORP | 148 | 37 | 1 | 1 | 22200 | 34.6875 | 1200000 | 34.6875 | 37298.0344 | 121190.8219 | 100000 | 85000 | 1543488.8562 | 385872.2141 | 1929361.0703 | SAN JOAQUIN | 0 | 0 | 1929361.0703 | 2020041.0406
CA5200558 | RIVER VIEW MHC LLC | 100 | 55 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | TEHAMA | 0 | 0 | 1925399.1016 | 2015892.8593
CA2700709 | RANCHO BORROMEO MWS | 100 | 36 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | MONTEREY | 0.3 | 462095.7844 | 2387494.8859 | 2499707.1456
CA2700669 | ORCHARD LN WS #02 | 32 | 16 | 1 | 1 | 4800 | 7.5 | 1200000 | 7.5 | 33355.575 | 117473.475 | 100000 | 85000 | 1535829.05 | 383957.2625 | 1919786.3125 | MONTEREY | 0.3 | 460748.715 | 2380535.0275 | 2492420.1738
CA2702110 | DELANY WC | 60 | 17 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | MONTEREY | 0.3 | 461303.3906 | 2383400.8516 | 2495420.6916
CA1700606 | BAYCLIFF WATER | 70 | 56 | 1 | 1 | 10500 | 16.4062 | 1200000 | 16.4062 | 34647.0703 | 118691.2266 | 100000 | 85000 | 1538338.2969 | 384584.5742 | 1922922.8711 | LAKE | 0 | 0 | 1922922.8711 | 2013300.246
CA2210924 | YOSEMITE WEST WATER SYSTEM | 420 | 186 | 1 | 1 | 63000 | 98.4375 | 1200000 | 98.4375 | 46542.4219 | 129907.3594 | 100000 | 85000 | 1561449.7812 | 390362.4453 | 1951812.2266 | MARIPOSA | 0 | 0 | 1951812.2266 | 2043547.4012
CA1210023 | LOLETA C.S.D. | 750 | 281 | 1 | 1 | 112500 | 175.7812 | 1200000 | 175.7812 | 57758.0391 | 140482.5703 | 100000 | 85000 | 1583240.6094 | 395810.1523 | 1979050.7617 | HUMBOLDT | 0 | 0 | 1979050.7617 | 2072066.1475
CA1100254 | VOYLES TRAILER PARK | 27 | 15 | 1 | 1 | 4050 | 6.3281 | 1200000 | 6.3281 | 33185.6414 | 117313.2445 | 100000 | 85000 | 1535498.8859 | 383874.7215 | 1919373.6074 | GLENN | 0 | 0 | 1919373.6074 | 2009584.167
CA3710009 | DESCANSO COMMUNITY SERVICES DISTRICT | 870 | 317 | 1 | 1 | 130500 | 203.9062 | 1200000 | 203.9062 | 61836.4453 | 144328.1016 | 100000 | 85000 | 1591164.5469 | 397791.1367 | 1988955.6836 | SAN DIEGO | 0.32 | 509172.655 | 2498128.3386 | 2615540.3705
CA2700548 | DOLAN RD MWC | 120 | 40 | 1 | 1 | 18000 | 28.125 | 1200000 | 28.125 | 36346.4062 | 120293.5312 | 100000 | 85000 | 1541639.9375 | 385409.9844 | 1927049.9219 | MONTEREY | 0.3 | 462491.9813 | 2389541.9031 | 2501850.3726
CA4900536 | OCCIDENTAL COMMUNITY SERVICES DISTRICT | 383 | 109 | 1 | 1 | 57450 | 89.7656 | 1200000 | 89.7656 | 45284.9133 | 128721.6539 | 100000 | 85000 | 1559006.5672 | 389751.6418 | 1948758.209 | SONOMA | 0.3 | 467701.9702 | 2416460.1791 | 2530033.8076
CA5200255 | CORNING RV PARK | 112 | 40 | 1 | 1 | 16800 | 26.25 | 1200000 | 26.25 | 36074.5125 | 120037.1625 | 100000 | 85000 | 1541111.675 | 385277.9188 | 1926389.5938 | TEHAMA | 0 | 0 | 1926389.5938 | 2016929.9047
CA5602109 | GLENVIEW MOBILE PARK | 160 | 26 | 1 | 1 | 24000 | 37.5 | 1200000 | 37.5 | 37705.875 | 121575.375 | 100000 | 85000 | 1544281.25 | 386070.3125 | 1930351.5625 | VENTURA | 0.32 | 494170 | 2424521.5625 | 2538474.0759
CA5510021 | TUD-PEACEFUL PINES WATER SYSTEM | 56 | 33 | 1 | 1 | 8400 | 13.125 | 1200000 | 13.125 | 34171.2562 | 118242.5813 | 100000 | 85000 | 1537413.8375 | 384353.4594 | 1921767.2969 | TUOLUMNE | 0 | 0 | 1921767.2969 | 2012090.3598
CA2702026 | APRICOT LN WS | 53 | 16 | 1 | 1 | 7950 | 12.4219 | 1200000 | 12.4219 | 34069.2961 | 118146.443 | 100000 | 85000 | 1537215.7391 | 384303.9348 | 1921519.6738 | MONTEREY | 0.3 | 461164.7217 | 2382684.3955 | 2494670.5621
CA1900785 | MITCHELL'S AVENUE E MOBILE HOME PARK | 24 | 24 | 1 | 1 | 3600 | 5.625 | 1200000 | 5.625 | 33083.6813 | 117217.1062 | 100000 | 85000 | 1535300.7875 | 383825.1969 | 1919125.9844 | LOS ANGELES | 0.32 | 491296.252 | 2410422.2364 | 2523712.0815
CA2600621 | WHITE MOUNTAIN MUTUAL WATER COMPANY | 142 | 43 | 1 | 1 | 21300 | 33.2812 | 1200000 | 33.2812 | 37094.1141 | 120998.5453 | 100000 | 85000 | 1543092.6594 | 385773.1648 | 1928865.8242 | MONO | 0 | 0 | 1928865.8242 | 2019522.518
CA1500289 | ATHAL MUTUAL WATER SYSTEM | 150 | 55 | 1 | 1 | 22500 | 35.1562 | 1200000 | 35.1562 | 37366.0078 | 121254.9141 | 100000 | 85000 | 1543620.9219 | 385905.2305 | 1929526.1523 | KERN | 0 | 0 | 1929526.1523 | 2020213.8815
CA3500524 | RIVER OAKS R.V.P. | 52 | 15 | 1 | 1 | 7800 | 12.1875 | 1200000 | 12.1875 | 34035.3094 | 118114.3969 | 100000 | 85000 | 1537149.7063 | 384287.4266 | 1921437.1328 | SAN BENITO | 0.3 | 461144.9119 | 2382582.0447 | 2494563.4008
CA0900102 | GOLD BEACH PARK | 100 | 40 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | EL DORADO | 0.3 | 462095.7844 | 2387494.8859 | 2499707.1456
CA3400128 | HAPPY HARBOR (SWS) | 60 | 45 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | SACRAMENTO | 0.32 | 492056.95 | 2414154.4109 | 2527619.6683
CA4900637 | MAGIC MOUNTAIN MUTUAL WATER COMPANY | 100 | 67 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SONOMA | 0.3 | 462095.7844 | 2387494.8859 | 2499707.1456
CA4700627 | JUNIPER CREEK ESTATES | 130 | 51 | 1 | 1 | 19500 | 30.4688 | 1200000 | 30.4688 | 36686.2734 | 120613.9922 | 100000 | 85000 | 1542300.2656 | 385575.0664 | 1927875.332 | SISKIYOU | 0 | 0 | 1927875.332 | 2018485.4726
CA4300603 | OAK DELL PARK | 100 | 53 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SANTA CLARA | 0.32 | 492902.17 | 2418301.2716 | 2531961.4313
CA1400070 | SIERRA GRANDE ESTATES MUTUAL WATER CO. | 200 | 49 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | INYO | 0 | 0 | 1933653.2031 | 2024534.9037
CA3900579 | CENTURY MOBILE HOME PARK | 50 | 19 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | SAN JOAQUIN | 0 | 0 | 1921272.0508 | 2011571.8372
CA4900640 | SONOMA COUNTY MUTUAL WATER COMPANY | 40 | 18 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | SONOMA | 0.3 | 460907.1937 | 2381353.8344 | 2493277.4646
CA4500009 | CORTLAND PINES MUTUAL WATER CO | 92 | 33 | 1 | 1 | 13800 | 21.5625 | 1200000 | 21.5625 | 35394.7781 | 119396.2406 | 100000 | 85000 | 1539791.0188 | 384947.7547 | 1924738.7734 | SHASTA | 0 | 0 | 1924738.7734 | 2015201.4958
CA5400556 | RIVER RETREAT MUTUAL | 53 | 25 | 1 | 1 | 7950 | 12.4219 | 1200000 | 12.4219 | 34069.2961 | 118146.443 | 100000 | 85000 | 1537215.7391 | 384303.9348 | 1921519.6738 | TULARE | 0 | 0 | 1921519.6738 | 2011831.0985
CA3900649 | GLENWOOD MOBILE HOME PARK | 100 | 50 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SAN JOAQUIN | 0 | 0 | 1925399.1016 | 2015892.8593
CA1700657 | WINDFLOWER POINT MUTUAL WATER COMPANY | 25 | 25 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | LAKE | 0 | 0 | 1919208.5254 | 2009411.3261
CA2300667 | WOODS, THE (MENDOCINO) | 153 | 115 | 1 | 1 | 22950 | 35.8594 | 1200000 | 35.8594 | 37467.968 | 121351.0523 | 100000 | 85000 | 1543819.0203 | 385954.7551 | 1929773.7754 | MENDOCINO | 0 | 0 | 1929773.7754 | 2020473.1428
CA4900892 | SUMMIT VIEW RANCH MUTUAL WATER CO. | 45 | 24 | 1 | 1 | 6750 | 10.5469 | 1200000 | 10.5469 | 33797.4023 | 117890.0742 | 100000 | 85000 | 1536687.4766 | 384171.8691 | 1920859.3457 | SONOMA | 0.3 | 461006.243 | 2381865.5887 | 2493813.2713
CA2701498 | HARBOR VIEW WA | 75 | 29 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | MONTEREY | 0.3 | 461600.5383 | 2384936.1145 | 2497028.1118
CA3200078 | FRCCSD OLD MILL RANCH | 32 | 23 | 1 | 1 | 4800 | 7.5 | 1200000 | 7.5 | 33355.575 | 117473.475 | 100000 | 85000 | 1535829.05 | 383957.2625 | 1919786.3125 | PLUMAS | 0 | 0 | 1919786.3125 | 2010016.2692
CA1500461 | FOUNTAIN TRAILER PARK WATER | 68 | 33 | 1 | 1 | 10200 | 15.9375 | 1200000 | 15.9375 | 34579.0969 | 118627.1344 | 100000 | 85000 | 1538206.2312 | 384551.5578 | 1922757.7891 | KERN | 0 | 0 | 1922757.7891 | 2013127.4051
CA1700610 | BELLA LAGO MOBILE HOME PARK | 152 | 46 | 1 | 1 | 22800 | 35.625 | 1200000 | 35.625 | 37433.9812 | 121319.0063 | 100000 | 85000 | 1543752.9875 | 385938.2469 | 1929691.2344 | LAKE | 0 | 0 | 1929691.2344 | 2020386.7224
CA3200195 | GREENHAVEN HOA | 38 | 18 | 1 | 1 | 5700 | 8.9062 | 1200000 | 8.9062 | 33559.4953 | 117665.7516 | 100000 | 85000 | 1536225.2469 | 384056.3117 | 1920281.5586 | PLUMAS | 0 | 0 | 1920281.5586 | 2010534.7918
CA1000259 | NEW HORIZONS MOBILE/RV PARK | 82 | 77 | 1 | 1 | 12300 | 19.2188 | 1200000 | 19.2188 | 35054.9109 | 119075.7797 | 100000 | 85000 | 1539130.6906 | 384782.6727 | 1923913.3633 | FRESNO | 0 | 0 | 1923913.3633 | 2014337.2914
CA0800605 | WEST PARK PROPERTIES | 112 | 42 | 1 | 1 | 16800 | 26.25 | 1200000 | 26.25 | 36074.5125 | 120037.1625 | 100000 | 85000 | 1541111.675 | 385277.9188 | 1926389.5938 | DEL NORTE | 0 | 0 | 1926389.5938 | 2016929.9047
CA2400167 | BALLICO CSD | 238 | 73 | 1 | 1 | 35700 | 55.7812 | 1200000 | 55.7812 | 40356.8391 | 124074.9703 | 100000 | 85000 | 1549431.8094 | 387357.9523 | 1936789.7617 | MERCED | 0 | 0 | 1936789.7617 | 2027818.8805
CA1502620 | POND MUTUAL WATER COMPANY | 48 | 18 | 1 | 1 | 7200 | 11.25 | 1200000 | 11.25 | 33899.3625 | 117986.2125 | 100000 | 85000 | 1536885.575 | 384221.3937 | 1921106.9688 | KERN | 0 | 0 | 1921106.9688 | 2011398.9963
CA5200014 | WILSON ACRES MUTUAL WATER | 75 | 28 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | TEHAMA | 0 | 0 | 1923335.5762 | 2013732.3483
CA3900705 | FINNLEES TRAILER PARK | 55 | 26 | 1 | 1 | 8250 | 12.8906 | 1200000 | 12.8906 | 34137.2695 | 118210.5352 | 100000 | 85000 | 1537347.8047 | 384336.9512 | 1921684.7559 | SAN JOAQUIN | 0 | 0 | 1921684.7559 | 2012003.9394
CA1900038 | LANCASTER PARK MOBILE HOME PARK | 61 | 21 | 1 | 1 | 9150 | 14.2969 | 1200000 | 14.2969 | 34341.1898 | 118402.8117 | 100000 | 85000 | 1537744.0016 | 384436.0004 | 1922180.002 | LOS ANGELES | 0.32 | 492078.0805 | 2414258.0825 | 2527728.2123
CA1700596 | BLUE LAKES VILLAGE | 65 | 44 | 1 | 1 | 9750 | 15.2344 | 1200000 | 15.2344 | 34477.1367 | 118530.9961 | 100000 | 85000 | 1538008.1328 | 384502.0332 | 1922510.166 | LAKE | 0 | 0 | 1922510.166 | 2012868.1438
CA3700073 | H & J WATER COMPANY | 50 | 39 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | SAN DIEGO | 0.32 | 491845.645 | 2413117.6958 | 2526534.2275
CA5800850 | REBEL RIDGE VILLAGE | 60 | 41 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | YUBA | 0 | 0 | 1922097.4609 | 2012436.0416
CA2702374 | COUNTRYSIDE ESTATES MWC | 223 | 23 | 1 | 1 | 33450 | 52.2656 | 1200000 | 52.2656 | 39847.0383 | 123594.2789 | 100000 | 85000 | 1548441.3172 | 387110.3293 | 1935551.6465 | MONTEREY | 0.3 | 464532.3952 | 2400084.0416 | 2512887.9916
CA4300999 | UVAS PINES RV PARK | 86 | 43 | 1 | 1 | 12900 | 20.1562 | 1200000 | 20.1562 | 35190.8578 | 119203.9641 | 100000 | 85000 | 1539394.8219 | 384848.7055 | 1924243.5273 | SANTA CLARA | 0.32 | 492606.343 | 2416849.8703 | 2530441.8142
CA2700547 | DESMOND RD WS #03 | 56 | 19 | 1 | 1 | 8400 | 13.125 | 1200000 | 13.125 | 34171.2562 | 118242.5813 | 100000 | 85000 | 1537413.8375 | 384353.4594 | 1921767.2969 | MONTEREY | 0.3 | 461224.1512 | 2382991.4481 | 2494992.0462
CA4210009 | CUYAMA COMMUNITY SERVICES DISTRICT | 763 | 254 | 1 | 1 | 114450 | 178.8281 | 1200000 | 178.8281 | 58199.8664 | 140899.1695 | 100000 | 85000 | 1584099.0359 | 396024.759 | 1980123.7949 | SANTA BARBARA | 0.3 | 475229.7108 | 2455353.5057 | 2570755.1205
CA0409181 | BLUE OAK TERRACE MUTUAL | 50 | 23 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | BUTTE | 0 | 0 | 1921272.0508 | 2011571.8372
CA3900517 | ALMOND PARK WATER SYSTEM | 60 | 20 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | SAN JOAQUIN | 0 | 0 | 1922097.4609 | 2012436.0416
CA3200127 | ARLINGTON HEIGHTS MHP | 33 | 39 | 1 | 1 | 4950 | 7.7344 | 1200000 | 7.7344 | 33389.5617 | 117505.5211 | 100000 | 85000 | 1535895.0828 | 383973.7707 | 1919868.8535 | PLUMAS | 0 | 0 | 1919868.8535 | 2010102.6896
CA5800827 | WHISPERING PINES MOBILE HOME PARK | 25 | 19 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | YUBA | 0 | 0 | 1919208.5254 | 2009411.3261
CA3301028 | BALDY MOUNTAIN RANCH | 144 | 80 | 1 | 1 | 21600 | 33.75 | 1200000 | 33.75 | 37162.0875 | 121062.6375 | 100000 | 85000 | 1543224.725 | 385806.1813 | 1929030.9062 | RIVERSIDE | 0.32 | 493831.912 | 2422862.8183 | 2536737.3707
CA2000553 | MD 28 RIPPERDAN SELF HELP | 48 | 17 | 1 | 1 | 7200 | 11.25 | 1200000 | 11.25 | 33899.3625 | 117986.2125 | 100000 | 85000 | 1536885.575 | 384221.3937 | 1921106.9688 | MADERA | 0 | 0 | 1921106.9688 | 2011398.9963
CA4500194 | VILLAGE GREEN | 90 | 32 | 1 | 1 | 13500 | 21.0938 | 1200000 | 21.0938 | 35326.8047 | 119332.1484 | 100000 | 85000 | 1539658.9531 | 384914.7383 | 1924573.6914 | SHASTA | 0 | 0 | 1924573.6914 | 2015028.6549
CA2701355 | PRINCES CAMP RESORT WS | 126 | 55 | 1 | 1 | 18900 | 29.5312 | 1200000 | 29.5312 | 36550.3266 | 120485.8078 | 100000 | 85000 | 1542036.1344 | 385509.0336 | 1927545.168 | MONTEREY | 0.3 | 462610.8403 | 2390156.0083 | 2502493.3407
CA1503536 | GLENNVILLE MUTUAL WATER COMPANY | 100 | 25 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | KERN | 0 | 0 | 1925399.1016 | 2015892.8593
CA1300555 | MITCHELLS CAMP FAMILY ASSOC. | 175 | 70 | 1 | 1 | 26250 | 41.0156 | 1200000 | 41.0156 | 38215.6758 | 122056.0664 | 100000 | 85000 | 1545271.7422 | 386317.9355 | 1931589.6777 | IMPERIAL | 0 | 0 | 1931589.6777 | 2022374.3926
CA0800800 | PINE GROVE TRAILER PARK | 100 | 51 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | DEL NORTE | 0 | 0 | 1925399.1016 | 2015892.8593
CA2701904 | SAN JERARDO COOP WS | 249 | 67 | 1 | 1 | 37350 | 58.3594 | 1200000 | 58.3594 | 40730.693 | 124427.4773 | 100000 | 85000 | 1550158.1703 | 387539.5426 | 1937697.7129 | MONTEREY | 0.3 | 465047.4511 | 2402745.164 | 2515674.1867
CA2900531 | CREEKSIDE VILLAGE | 300 | 131 | 1 | 1 | 45000 | 70.3125 | 1200000 | 70.3125 | 42464.0156 | 126061.8281 | 100000 | 85000 | 1553525.8438 | 388381.4609 | 1941907.3047 | NEVADA | 0 | 0 | 1941907.3047 | 2033176.948
CA1900717 | CASA DULCE ESTATES | 28 | 17 | 1 | 1 | 4200 | 6.5625 | 1200000 | 6.5625 | 33219.6281 | 117345.2906 | 100000 | 85000 | 1535564.9187 | 383891.2297 | 1919456.1484 | LOS ANGELES | 0.32 | 491380.774 | 2410836.9224 | 2524146.2578
CA4500062 | LONE TREE MOBILE HOME PARK | 85 | 26 | 1 | 1 | 12750 | 19.9219 | 1200000 | 19.9219 | 35156.8711 | 119171.918 | 100000 | 85000 | 1539328.7891 | 384832.1973 | 1924160.9863 | SHASTA | 0 | 0 | 1924160.9863 | 2014596.5527
CA3110043 | TAHOE CITY PUD - MADDEN CREEK | 300 | 183 | 1 | 1 | 45000 | 70.3125 | 1200000 | 70.3125 | 42464.0156 | 126061.8281 | 100000 | 85000 | 1553525.8438 | 388381.4609 | 1941907.3047 | PLACER | 0 | 0 | 1941907.3047 | 2033176.948
CA0707501 | ANGLER S RANCH #3 | 60 | 32 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | CONTRA COSTA | 0.3 | 461303.3906 | 2383400.8516 | 2495420.6916
CA4300578 | ANGELO LANE WATER COMPANY | 52 | 15 | 1 | 1 | 7800 | 12.1875 | 1200000 | 12.1875 | 34035.3094 | 118114.3969 | 100000 | 85000 | 1537149.7063 | 384287.4266 | 1921437.1328 | SANTA CLARA | 0.32 | 491887.906 | 2413325.0388 | 2526751.3156
CA0400003 | HARTLEY MUTUAL WATER SYSTEM | 31 | 15 | 1 | 1 | 4650 | 7.2656 | 1200000 | 7.2656 | 33321.5883 | 117441.4289 | 100000 | 85000 | 1535763.0172 | 383940.7543 | 1919703.7715 | BUTTE | 0 | 0 | 1919703.7715 | 2009929.8487
CA4300615 | THOUSAND TRAILS - MORGAN HILL | 508 | 320 | 1 | 1 | 76200 | 119.0625 | 1200000 | 119.0625 | 49533.2531 | 132727.4156 | 100000 | 85000 | 1567260.6687 | 391815.1672 | 1959075.8359 | SANTA CLARA | 0.32 | 501523.414 | 2460599.2499 | 2576247.4147
CA2900511 | SHADY LAKE WATER ASSOCIATION | 90 | 28 | 1 | 1 | 13500 | 21.0938 | 1200000 | 21.0938 | 35326.8047 | 119332.1484 | 100000 | 85000 | 1539658.9531 | 384914.7383 | 1924573.6914 | NEVADA | 0 | 0 | 1924573.6914 | 2015028.6549
CA3900596 | VILLA CEREZOS | 200 | 82 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | SAN JOAQUIN | 0 | 0 | 1933653.2031 | 2024534.9037
CA4200505 | CACHUMA VILLAGE | 60 | 24 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | SANTA BARBARA | 0.3 | 461303.3906 | 2383400.8516 | 2495420.6916
CA3500579 | VINEYARD ESTATES MWC | 90 | 26 | 1 | 1 | 13500 | 21.0938 | 1200000 | 21.0938 | 35326.8047 | 119332.1484 | 100000 | 85000 | 1539658.9531 | 384914.7383 | 1924573.6914 | SAN BENITO | 0.3 | 461897.6859 | 2386471.3773 | 2498635.5321
CA4900665 | RUSSIAN RIVER MUTUAL WATER CO. | 84 | 30 | 1 | 1 | 12600 | 19.6875 | 1200000 | 19.6875 | 35122.8844 | 119139.8719 | 100000 | 85000 | 1539262.7563 | 384815.6891 | 1924078.4453 | SONOMA | 0.3 | 461778.8269 | 2385857.2722 | 2497992.564
CA2300668 | POINT CABRILLO HIGHLANDS | 42 | 21 | 1 | 1 | 6300 | 9.8438 | 1200000 | 9.8438 | 33695.4422 | 117793.9359 | 100000 | 85000 | 1536489.3781 | 384122.3445 | 1920611.7227 | MENDOCINO | 0 | 0 | 1920611.7227 | 2010880.4736
CA1900537 | OAK GROVE FAMILY PARK | 109 | 40 | 1 | 1 | 16350 | 25.5469 | 1200000 | 25.5469 | 35972.5523 | 119941.0242 | 100000 | 85000 | 1540913.5766 | 385228.3941 | 1926141.9707 | LOS ANGELES | 0.32 | 493092.3445 | 2419234.3152 | 2532938.328
CA1900961 | WINTERHAVEN MOBILE ESTATES | 56 | 20 | 1 | 1 | 8400 | 13.125 | 1200000 | 13.125 | 34171.2562 | 118242.5813 | 100000 | 85000 | 1537413.8375 | 384353.4594 | 1921767.2969 | LOS ANGELES | 0.32 | 491972.428 | 2413739.7249 | 2527185.4919
CA4400684 | APTOS RIDGE MUTUAL WATER CO | 52 | 16 | 1 | 1 | 7800 | 12.1875 | 1200000 | 12.1875 | 34035.3094 | 118114.3969 | 100000 | 85000 | 1537149.7063 | 384287.4266 | 1921437.1328 | SANTA CRUZ | 0.3 | 461144.9119 | 2382582.0447 | 2494563.4008
CA2700771 | SPRINGFIELD WATER COMPANY | 200 | 34 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | MONTEREY | 0.3 | 464076.7687 | 2397729.9719 | 2510423.2806
CA2702409 | EL CAMINO WC INC | 133 | 21 | 1 | 1 | 19950 | 31.1719 | 1200000 | 31.1719 | 36788.2336 | 120710.1305 | 100000 | 85000 | 1542498.3641 | 385624.591 | 1928122.9551 | MONTEREY | 0.3 | 462749.5092 | 2390872.4643 | 2503243.4701
CA3400150 | DELTA CROSSING MHP | 30 | 22 | 1 | 1 | 4500 | 7.0312 | 1200000 | 7.0312 | 33287.6016 | 117409.3828 | 100000 | 85000 | 1535696.9844 | 383924.2461 | 1919621.2305 | SACRAMENTO | 0.32 | 491423.035 | 2411044.2655 | 2524363.3459
CA3500550 | SAN JUSTO MUTUAL WATER COMPANY | 160 | 60 | 1 | 1 | 24000 | 37.5 | 1200000 | 37.5 | 37705.875 | 121575.375 | 100000 | 85000 | 1544281.25 | 386070.3125 | 1930351.5625 | SAN BENITO | 0.3 | 463284.375 | 2393635.9375 | 2506136.8266
CA4900570 | PALOMINO LAKES MUTUAL WATER CO. | 250 | 113 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | SONOMA | 0.3 | 465067.2609 | 2402847.5148 | 2515781.348
CA3301267 | FISHERMAN'S RETREAT | 402 | 172 | 1 | 1 | 60300 | 94.2188 | 1200000 | 94.2188 | 45930.6609 | 129330.5297 | 100000 | 85000 | 1560261.1906 | 390065.2977 | 1950326.4883 | RIVERSIDE | 0.32 | 499283.581 | 2449610.0693 | 2564741.7425
CA0800556 | HRC C.S.D. | 150 | 54 | 1 | 1 | 22500 | 35.1562 | 1200000 | 35.1562 | 37366.0078 | 121254.9141 | 100000 | 85000 | 1543620.9219 | 385905.2305 | 1929526.1523 | DEL NORTE | 0 | 0 | 1929526.1523 | 2020213.8815
CA2701364 | PEDRAZZI MWC | 273 | 96 | 1 | 1 | 40950 | 63.9844 | 1200000 | 63.9844 | 41546.3742 | 125196.5836 | 100000 | 85000 | 1551742.9578 | 387935.7395 | 1939678.6973 | MONTEREY | 0.3 | 465522.8873 | 2405201.5846 | 2518246.0591
CA5000061 | MARTIN'S MOBILE HOME COURT | 60 | 20 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | STANISLAUS | 0 | 0 | 1922097.4609 | 2012436.0416
CA4500003 | MEL MAR MUTUAL WATER CO | 300 | 91 | 1 | 1 | 45000 | 70.3125 | 1200000 | 70.3125 | 42464.0156 | 126061.8281 | 100000 | 85000 | 1553525.8438 | 388381.4609 | 1941907.3047 | SHASTA | 0 | 0 | 1941907.3047 | 2033176.948
CA0707598 | CAMINO MOBILEHOME | 210 | 75 | 1 | 1 | 31500 | 49.2188 | 1200000 | 49.2188 | 39405.2109 | 123177.6797 | 100000 | 85000 | 1547582.8906 | 386895.7227 | 1934478.6133 | CONTRA COSTA | 0.3 | 464274.8672 | 2398753.4805 | 2511494.8941
CA5000060 | CASA DE AMIGOS MOBILE HOME PARK | 220 | 73 | 1 | 1 | 33000 | 51.5625 | 1200000 | 51.5625 | 39745.0781 | 123498.1406 | 100000 | 85000 | 1548243.2188 | 387060.8047 | 1935304.0234 | STANISLAUS | 0 | 0 | 1935304.0234 | 2026263.3125
CA1500314 | DEL ORO WC - COUNTRY ESTATES DIST | 297 | 90 | 1 | 1 | 44550 | 69.6094 | 1200000 | 69.6094 | 42362.0555 | 125965.6898 | 100000 | 85000 | 1553327.7453 | 388331.9363 | 1941659.6816 | KERN | 0 | 0 | 1941659.6816 | 2032917.6867
CA3301045 | BLYTHE MOBILE HOME ESTATES | 35 | 25 | 1 | 1 | 5250 | 8.2031 | 1200000 | 8.2031 | 33457.5352 | 117569.6133 | 100000 | 85000 | 1536027.1484 | 384006.7871 | 1920033.9355 | RIVERSIDE | 0.32 | 491528.6875 | 2411562.623 | 2524906.0663
CA3301330 | INDIAN OAKS TRAILER PARK | 90 | 63 | 1 | 1 | 13500 | 21.0938 | 1200000 | 21.0938 | 35326.8047 | 119332.1484 | 100000 | 85000 | 1539658.9531 | 384914.7383 | 1924573.6914 | RIVERSIDE | 0.32 | 492690.865 | 2417264.5564 | 2530875.9906
CA1600507 | HARDWICK WATER COMPANY | 69 | 20 | 1 | 1 | 10350 | 16.1719 | 1200000 | 16.1719 | 34613.0836 | 118659.1805 | 100000 | 85000 | 1538272.2641 | 384568.066 | 1922840.3301 | KINGS | 0 | 0 | 1922840.3301 | 2013213.8256
CA3600071 | CHAMISAL MWC | 63 | 29 | 1 | 1 | 9450 | 14.7656 | 1200000 | 14.7656 | 34409.1633 | 118466.9039 | 100000 | 85000 | 1537876.0672 | 384469.0168 | 1922345.084 | SAN BERNARDINO | 0.3 | 461362.8202 | 2383707.9041 | 2495742.1756
CA4500104 | SUNRISE MOBILEHOME PARK | 35 | 16 | 1 | 1 | 5250 | 8.2031 | 1200000 | 8.2031 | 33457.5352 | 117569.6133 | 100000 | 85000 | 1536027.1484 | 384006.7871 | 1920033.9355 | SHASTA | 0 | 0 | 1920033.9355 | 2010275.5305
CA0900422 | CRYSTAL CAVES MHP | 112 | 40 | 1 | 1 | 16800 | 26.25 | 1200000 | 26.25 | 36074.5125 | 120037.1625 | 100000 | 85000 | 1541111.675 | 385277.9188 | 1926389.5938 | EL DORADO | 0.3 | 462333.5025 | 2388723.0962 | 2500993.0818
CA1200718 | WADDINGTON W.W. | 75 | 25 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | HUMBOLDT | 0 | 0 | 1923335.5762 | 2013732.3483
CA4900608 | SIX ACRES WATER COMPANY | 66 | 22 | 1 | 1 | 9900 | 15.4688 | 1200000 | 15.4688 | 34511.1234 | 118563.0422 | 100000 | 85000 | 1538074.1656 | 384518.5414 | 1922592.707 | SONOMA | 0.3 | 461422.2497 | 2384014.9567 | 2496063.6597
CA2600546 | CROWLEY LAKE MUTUAL WATER COMPANY | 175 | 57 | 1 | 1 | 26250 | 41.0156 | 1200000 | 41.0156 | 38215.6758 | 122056.0664 | 100000 | 85000 | 1545271.7422 | 386317.9355 | 1931589.6777 | MONO | 0 | 0 | 1931589.6777 | 2022374.3926
CA0800532 | BIG ROCK C.S.D. | 400 | 107 | 1 | 1 | 60000 | 93.75 | 1200000 | 93.75 | 45862.6875 | 129266.4375 | 100000 | 85000 | 1560129.125 | 390032.2812 | 1950161.4062 | DEL NORTE | 0 | 0 | 1950161.4062 | 2041818.9923
CA3100538 | ROSECREST MUTUAL | 31 | 15 | 1 | 1 | 4650 | 7.2656 | 1200000 | 7.2656 | 33321.5883 | 117441.4289 | 100000 | 85000 | 1535763.0172 | 383940.7543 | 1919703.7715 | PLACER | 0 | 0 | 1919703.7715 | 2009929.8487
CA3900664 | NEW HOPE LANDING GENERAL STORE | 125 | 44 | 1 | 1 | 18750 | 29.2969 | 1200000 | 29.2969 | 36516.3398 | 120453.7617 | 100000 | 85000 | 1541970.1016 | 385492.5254 | 1927462.627 | SAN JOAQUIN | 0 | 0 | 1927462.627 | 2018053.3704
CA4901309 | HILTON MUTUAL WATER COMPANY | 100 | 16 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SONOMA | 0.3 | 462095.7844 | 2387494.8859 | 2499707.1456
CA2000849 | MD 60 DILLON ESTATES | 150 | 38 | 1 | 1 | 22500 | 35.1562 | 1200000 | 35.1562 | 37366.0078 | 121254.9141 | 100000 | 85000 | 1543620.9219 | 385905.2305 | 1929526.1523 | MADERA | 0 | 0 | 1929526.1523 | 2020213.8815
CA1100237 | WILLOWS MOBILE HOME COMMUNITY & RV PARK | 190 | 87 | 1 | 1 | 28500 | 44.5312 | 1200000 | 44.5312 | 38725.4766 | 122536.7578 | 100000 | 85000 | 1546262.2344 | 386565.5586 | 1932827.793 | GLENN | 0 | 0 | 1932827.793 | 2023670.6992
CA2702325 | FERNWOOD WS | 133 | 17 | 1 | 1 | 19950 | 31.1719 | 1200000 | 31.1719 | 36788.2336 | 120710.1305 | 100000 | 85000 | 1542498.3641 | 385624.591 | 1928122.9551 | MONTEREY | 0.3 | 462749.5092 | 2390872.4643 | 2503243.4701
CA0500075 | LAKESIDE MOBILE ESTATES | 54 | 24 | 1 | 1 | 8100 | 12.6562 | 1200000 | 12.6562 | 34103.2828 | 118178.4891 | 100000 | 85000 | 1537281.7719 | 384320.443 | 1921602.2148 | CALAVERAS | 0 | 0 | 1921602.2148 | 2011917.5189
CA4300560 | GREEN MOUNTAIN WATER COMPANY | 80 | 38 | 1 | 1 | 12000 | 18.75 | 1200000 | 18.75 | 34986.9375 | 119011.6875 | 100000 | 85000 | 1538998.625 | 384749.6562 | 1923748.2812 | SANTA CLARA | 0.32 | 492479.56 | 2416227.8413 | 2529790.5498
CA1000472 | PG&E HELMS SUPPORT FACILITY | 40 | 22 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | FRESNO | 0 | 0 | 1920446.6406 | 2010707.6327
CA2900548 | SIERRA ESTATES MUTUAL WATER COMPANY | 100 | 32 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | NEVADA | 0 | 0 | 1925399.1016 | 2015892.8593
CA3400107 | RIVER'S EDGE MARINA & RESORT | 150 | 83 | 1 | 1 | 22500 | 35.1562 | 1200000 | 35.1562 | 37366.0078 | 121254.9141 | 100000 | 85000 | 1543620.9219 | 385905.2305 | 1929526.1523 | SACRAMENTO | 0.32 | 493958.695 | 2423484.8473 | 2537388.6352
CA5800572 | FAIRWAY DOWNS MUTUAL WATER CO | 100 | 27 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | YUBA | 0 | 0 | 1925399.1016 | 2015892.8593
CA4900639 | REDWOOD HEIGHTS MUTUAL WATER COMPANY | 30 | 18 | 1 | 1 | 4500 | 7.0312 | 1200000 | 7.0312 | 33287.6016 | 117409.3828 | 100000 | 85000 | 1535696.9844 | 383924.2461 | 1919621.2305 | SONOMA | 0.3 | 460709.0953 | 2380330.3258 | 2492205.8511
CA1000369 | ZONNEVELD DAIRY - CEDAR | 70 | 15 | 1 | 1 | 10500 | 16.4062 | 1200000 | 16.4062 | 34647.0703 | 118691.2266 | 100000 | 85000 | 1538338.2969 | 384584.5742 | 1922922.8711 | FRESNO | 0 | 0 | 1922922.8711 | 2013300.246
CA5500353 | SIERRA VILLAGE MOBILE HOME PARK | 30 | 30 | 1 | 1 | 4500 | 7.0312 | 1200000 | 7.0312 | 33287.6016 | 117409.3828 | 100000 | 85000 | 1535696.9844 | 383924.2461 | 1919621.2305 | TUOLUMNE | 0 | 0 | 1919621.2305 | 2009843.4283
CA2700579 | ELKHORN RD WS #04 | 60 | 20 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | MONTEREY | 0.3 | 461303.3906 | 2383400.8516 | 2495420.6916
CA4500092 | RIVER BREEZE MOBILE HOME PARK | 87 | 32 | 1 | 1 | 13050 | 20.3906 | 1200000 | 20.3906 | 35224.8445 | 119236.0102 | 100000 | 85000 | 1539460.8547 | 384865.2137 | 1924326.0684 | SHASTA | 0 | 0 | 1924326.0684 | 2014769.3936
CA1000244 | SHADY LAKES MOBILE HOME PARK | 160 | 65 | 1 | 1 | 24000 | 37.5 | 1200000 | 37.5 | 37705.875 | 121575.375 | 100000 | 85000 | 1544281.25 | 386070.3125 | 1930351.5625 | FRESNO | 0 | 0 | 1930351.5625 | 2021078.0859
CA3900721 | WOODBRIDGE MOBILE ESTATES | 110 | 37 | 1 | 1 | 16500 | 25.7812 | 1200000 | 25.7812 | 36006.5391 | 119973.0703 | 100000 | 85000 | 1540979.6094 | 385244.9023 | 1926224.5117 | SAN JOAQUIN | 0 | 0 | 1926224.5117 | 2016757.0638
CA2210901 | MPWD-COULTERVILLE CSA 1 | 193 | 98 | 1 | 1 | 28950 | 45.2344 | 1200000 | 45.2344 | 38827.4367 | 122632.8961 | 100000 | 85000 | 1546460.3328 | 386615.0832 | 1933075.416 | MARIPOSA | 0 | 0 | 1933075.416 | 2023929.9606
CA1400144 | SUNLAND VILLAGE MOBILE HOME PARK | 42 | 26 | 1 | 1 | 6300 | 9.8438 | 1200000 | 9.8438 | 33695.4422 | 117793.9359 | 100000 | 85000 | 1536489.3781 | 384122.3445 | 1920611.7227 | INYO | 0 | 0 | 1920611.7227 | 2010880.4736
CA3100043 | GOLD HILL MOBILEHOME PARK | 75 | 32 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | PLACER | 0 | 0 | 1923335.5762 | 2013732.3483
CA5000082 | 4N MOBILEHOME PARK | 65 | 31 | 1 | 1 | 9750 | 15.2344 | 1200000 | 15.2344 | 34477.1367 | 118530.9961 | 100000 | 85000 | 1538008.1328 | 384502.0332 | 1922510.166 | STANISLAUS | 0 | 0 | 1922510.166 | 2012868.1438
CA2701906 | LAKE SAN ANTONIO PARK WS | 54 | 30 | 1 | 1 | 8100 | 12.6562 | 1200000 | 12.6562 | 34103.2828 | 118178.4891 | 100000 | 85000 | 1537281.7719 | 384320.443 | 1921602.2148 | MONTEREY | 0.3 | 461184.5316 | 2382786.7464 | 2494777.7235
CA4500255 | SACRAMENTO RIVER RV PARK | 382 | 156 | 1 | 1 | 57300 | 89.5312 | 1200000 | 89.5312 | 45250.9266 | 128689.6078 | 100000 | 85000 | 1558940.5344 | 389735.1336 | 1948675.668 | SHASTA | 0 | 0 | 1948675.668 | 2040263.4244
CA5000067 | TULLY MOBILE ESTATES | 40 | 15 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | STANISLAUS | 0 | 0 | 1920446.6406 | 2010707.6327
CA3900563 | GAYLA MANOR PWS | 146 | 54 | 1 | 1 | 21900 | 34.2188 | 1200000 | 34.2188 | 37230.0609 | 121126.7297 | 100000 | 85000 | 1543356.7906 | 385839.1977 | 1929195.9883 | SAN JOAQUIN | 0 | 0 | 1929195.9883 | 2019868.1997
CA5200510 | RIVER RANCH MOBILE HOME PARK | 305 | 109 | 1 | 1 | 45750 | 71.4844 | 1200000 | 71.4844 | 42633.9492 | 126222.0586 | 100000 | 85000 | 1553856.0078 | 388464.002 | 1942320.0098 | TEHAMA | 0 | 0 | 1942320.0098 | 2033609.0502
CA4200827 | SANTA YNEZ ROBLAR MOBILE HOME PARK | 25 | 19 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | SANTA BARBARA | 0.3 | 460610.0461 | 2379818.5715 | 2491670.0443
CA5500149 | COLUMBIA MOBILE HOME PARK | 88 | 63 | 1 | 1 | 13200 | 20.625 | 1200000 | 20.625 | 35258.8313 | 119268.0562 | 100000 | 85000 | 1539526.8875 | 384881.7219 | 1924408.6094 | TUOLUMNE | 0 | 0 | 1924408.6094 | 2014855.814
CA4300994 | COYOTE VALLEY RV RESORT | 500 | 129 | 1 | 1 | 75000 | 117.1875 | 1200000 | 117.1875 | 49261.3594 | 132471.0469 | 100000 | 85000 | 1566732.4062 | 391683.1016 | 1958415.5078 | SANTA CLARA | 0.32 | 501354.37 | 2459769.8778 | 2575379.0621
CA1100404 | DEL ORO WC - BLACK BUTTE DISTRICT | 284 | 85 | 1 | 1 | 42600 | 66.5625 | 1200000 | 66.5625 | 41920.2281 | 125549.0906 | 100000 | 85000 | 1552469.3188 | 388117.3297 | 1940586.6484 | GLENN | 0 | 0 | 1940586.6484 | 2031794.2209
CA5100112 | TIERRA BUENA MHP #1 | 50 | 17 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | SUTTER | 0 | 0 | 1921272.0508 | 2011571.8372
CA2700842 | BAUMANN RD WS #01 | 40 | 17 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | MONTEREY | 0.3 | 460907.1937 | 2381353.8344 | 2493277.4646
CA5201147 | GOLDEN MEADOWS CSD | 102 | 49 | 1 | 1 | 15300 | 23.9062 | 1200000 | 23.9062 | 35734.6453 | 119716.7016 | 100000 | 85000 | 1540451.3469 | 385112.8367 | 1925564.1836 | TEHAMA | 0 | 0 | 1925564.1836 | 2016065.7002
CA3900682 | LOCKEFORD MOBILE HOME PARK WTR SYS | 100 | 43 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SAN JOAQUIN | 0 | 0 | 1925399.1016 | 2015892.8593
CA1100405 | BLACK BUTTE MOBILE H.P. | 148 | 49 | 1 | 1 | 22200 | 34.6875 | 1200000 | 34.6875 | 37298.0344 | 121190.8219 | 100000 | 85000 | 1543488.8562 | 385872.2141 | 1929361.0703 | GLENN | 0 | 0 | 1929361.0703 | 2020041.0406
CA1500494 | WILSON ROAD WATER COMMUNITY | 66 | 20 | 1 | 1 | 9900 | 15.4688 | 1200000 | 15.4688 | 34511.1234 | 118563.0422 | 100000 | 85000 | 1538074.1656 | 384518.5414 | 1922592.707 | KERN | 0 | 0 | 1922592.707 | 2012954.5643
CA5800828 | COUNTRYSIDE MOBILE HOME PARK | 185 | 86 | 1 | 1 | 27750 | 43.3594 | 1200000 | 43.3594 | 38555.543 | 122376.5273 | 100000 | 85000 | 1545932.0703 | 386483.0176 | 1932415.0879 | YUBA | 0 | 0 | 1932415.0879 | 2023238.597
CA5601106 | FILLMORE WEST MOBILE HOME PARK | 99 | 33 | 1 | 1 | 14850 | 23.2031 | 1200000 | 23.2031 | 35632.6852 | 119620.5633 | 100000 | 85000 | 1540253.2484 | 385063.3121 | 1925316.5605 | VENTURA | 0.32 | 492881.0395 | 2418197.6 | 2531852.8872
CA3900606 | A1 WINSTONS MOBILE HOME PARK | 75 | 30 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | SAN JOAQUIN | 0 | 0 | 1923335.5762 | 2013732.3483
CA4901221 | GRATON MUTUAL (GREEN VALLEY HOA) | 50 | 16 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | SONOMA | 0.3 | 461105.2922 | 2382377.343 | 2494349.0781
CA3400397 | LAGUNA VILLAGE RV PARK | 32 | 28 | 1 | 1 | 4800 | 7.5 | 1200000 | 7.5 | 33355.575 | 117473.475 | 100000 | 85000 | 1535829.05 | 383957.2625 | 1919786.3125 | SACRAMENTO | 0.32 | 491465.296 | 2411251.6085 | 2524580.4341
CA4900634 | HUCKLEBERRY MUTUAL WATER COMPANY | 45 | 29 | 1 | 1 | 6750 | 10.5469 | 1200000 | 10.5469 | 33797.4023 | 117890.0742 | 100000 | 85000 | 1536687.4766 | 384171.8691 | 1920859.3457 | SONOMA | 0.3 | 461006.243 | 2381865.5887 | 2493813.2713
CA5400523 | EL MONTE VILLAGE MHP | 100 | 47 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | TULARE | 0 | 0 | 1925399.1016 | 2015892.8593
CA2701898 | CLEAR RIDGE WA | 123 | 41 | 1 | 1 | 18450 | 28.8281 | 1200000 | 28.8281 | 36448.3664 | 120389.6695 | 100000 | 85000 | 1541838.0359 | 385459.509 | 1927297.5449 | MONTEREY | 0.3 | 462551.4108 | 2389848.9557 | 2502171.8566
CA3701341 | QUIET OAKS MOBILE HOME PARK | 120 | 45 | 1 | 1 | 18000 | 28.125 | 1200000 | 28.125 | 36346.4062 | 120293.5312 | 100000 | 85000 | 1541639.9375 | 385409.9844 | 1927049.9219 | SAN DIEGO | 0.32 | 493324.78 | 2420374.7019 | 2534132.3129
CA5200555 | RIO RANCH COMMUNITY SVCS DIST | 44 | 30 | 1 | 1 | 6600 | 10.3125 | 1200000 | 10.3125 | 33763.4156 | 117858.0281 | 100000 | 85000 | 1536621.4438 | 384155.3609 | 1920776.8047 | TEHAMA | 0 | 0 | 1920776.8047 | 2011053.3145
CA3901276 | HANOT FOUNDATION INC | 38 | 15 | 1 | 1 | 5700 | 8.9062 | 1200000 | 8.9062 | 33559.4953 | 117665.7516 | 100000 | 85000 | 1536225.2469 | 384056.3117 | 1920281.5586 | SAN JOAQUIN | 0 | 0 | 1920281.5586 | 2010534.7918
CA2700634 | CHETMOORE ACRES WA | 70 | 25 | 1 | 1 | 10500 | 16.4062 | 1200000 | 16.4062 | 34647.0703 | 118691.2266 | 100000 | 85000 | 1538338.2969 | 384584.5742 | 1922922.8711 | MONTEREY | 0.3 | 461501.4891 | 2384424.3602 | 2496492.3051
CA3900835 | WAYSIDE MOTEL APARTMENTS WTR SYS | 70 | 25 | 1 | 1 | 10500 | 16.4062 | 1200000 | 16.4062 | 34647.0703 | 118691.2266 | 100000 | 85000 | 1538338.2969 | 384584.5742 | 1922922.8711 | SAN JOAQUIN | 0 | 0 | 1922922.8711 | 2013300.246
CA1503226 | QVWD-WEST & EAST COMBINED WATER SYSTEM | 207 | 75 | 1 | 1 | 31050 | 48.5156 | 1200000 | 48.5156 | 39303.2508 | 123081.5414 | 100000 | 85000 | 1547384.7922 | 386846.198 | 1934230.9902 | KERN | 0 | 0 | 1934230.9902 | 2025139.8468
CA5510025 | TUD - PHOENIX LAKE PARK | 119 | 57 | 1 | 1 | 17850 | 27.8906 | 1200000 | 27.8906 | 36312.4195 | 120261.4852 | 100000 | 85000 | 1541573.9047 | 385393.4762 | 1926967.3809 | TUOLUMNE | 0 | 0 | 1926967.3809 | 2017534.8478
CA3901304 | ENCLAVE AT THE DELTA | 39 | 15 | 1 | 1 | 5850 | 9.1406 | 1200000 | 9.1406 | 33593.482 | 117697.7977 | 100000 | 85000 | 1536291.2797 | 384072.8199 | 1920364.0996 | SAN JOAQUIN | 0 | 0 | 1920364.0996 | 2010621.2123
CA2000608 | WILDWOOD MOBILE HOME PK INC | 100 | 68 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | MADERA | 0 | 0 | 1925399.1016 | 2015892.8593
CA0300053 | RANCHO DEL ORO | 44 | 24 | 1 | 1 | 6600 | 10.3125 | 1200000 | 10.3125 | 33763.4156 | 117858.0281 | 100000 | 85000 | 1536621.4438 | 384155.3609 | 1920776.8047 | AMADOR | 0 | 0 | 1920776.8047 | 2011053.3145
CA4500314 | SHASTA CO CSA # 13 ALPINE MEADOWS | 31 | 31 | 1 | 1 | 4650 | 7.2656 | 1200000 | 7.2656 | 33321.5883 | 117441.4289 | 100000 | 85000 | 1535763.0172 | 383940.7543 | 1919703.7715 | SHASTA | 0 | 0 | 1919703.7715 | 2009929.8487
CA1900913 | LILY OF THE VALLEY MOBILE VILLAGE | 495 | 182 | 1 | 1 | 74250 | 116.0156 | 1200000 | 116.0156 | 49091.4258 | 132310.8164 | 100000 | 85000 | 1566402.2422 | 391600.5605 | 1958002.8027 | LOS ANGELES | 0.32 | 501248.7175 | 2459251.5202 | 2574836.3417
CA4900669 | WENDELL LANE MUTUAL WATER COMPANY | 82 | 25 | 1 | 1 | 12300 | 19.2188 | 1200000 | 19.2188 | 35054.9109 | 119075.7797 | 100000 | 85000 | 1539130.6906 | 384782.6727 | 1923913.3633 | SONOMA | 0.3 | 461739.2072 | 2385652.5705 | 2497778.2413
CA0400123 | HUMBOLDT HIGHLANDS MUTUAL | 50 | 28 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | BUTTE | 0 | 0 | 1921272.0508 | 2011571.8372
CA2000526 | PIKE RANCH MUTUAL WATER CO | 74 | 20 | 1 | 1 | 11100 | 17.3438 | 1200000 | 17.3438 | 34783.0172 | 118819.4109 | 100000 | 85000 | 1538602.4281 | 384650.607 | 1923253.0352 | MADERA | 0 | 0 | 1923253.0352 | 2013645.9278
CA5602108 | GARDEN ACRES MUTUAL WATER CO | 840 | 140 | 1 | 1 | 126000 | 196.875 | 1200000 | 196.875 | 60816.8438 | 143366.7188 | 100000 | 85000 | 1589183.5625 | 397295.8906 | 1986479.4531 | VENTURA | 0.32 | 508538.74 | 2495018.1931 | 2612284.0482
CA5800821 | HERITAGE PARK | 26 | 20 | 1 | 1 | 3900 | 6.0938 | 1200000 | 6.0938 | 33151.6547 | 117281.1984 | 100000 | 85000 | 1535432.8531 | 383858.2133 | 1919291.0664 | YUBA | 0 | 0 | 1919291.0664 | 2009497.7465
CA2000530 | CRASS MUTUAL WATER COMPANY | 80 | 26 | 1 | 1 | 12000 | 18.75 | 1200000 | 18.75 | 34986.9375 | 119011.6875 | 100000 | 85000 | 1538998.625 | 384749.6562 | 1923748.2812 | MADERA | 0 | 0 | 1923748.2812 | 2014164.4505
CA4500082 | MIDWAY MOBILEHOME PARK | 50 | 29 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | SHASTA | 0 | 0 | 1921272.0508 | 2011571.8372
CA4400850 | THE WILLOWS RESORT | 54 | 69 | 1 | 1 | 8100 | 12.6562 | 1200000 | 12.6562 | 34103.2828 | 118178.4891 | 100000 | 85000 | 1537281.7719 | 384320.443 | 1921602.2148 | SANTA CRUZ | 0.3 | 461184.5316 | 2382786.7464 | 2494777.7235
CA5200013 | WOMACK SUBDIVISION M.W.C. | 40 | 16 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | TEHAMA | 0 | 0 | 1920446.6406 | 2010707.6327
CA3900586 | B&G MOBILE HOME PARK LLC WS | 50 | 22 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | SAN JOAQUIN | 0 | 0 | 1921272.0508 | 2011571.8372
CA2700766 | STRAWBERRY RD WS #06 | 78 | 27 | 1 | 1 | 11700 | 18.2812 | 1200000 | 18.2812 | 34918.9641 | 118947.5953 | 100000 | 85000 | 1538866.5594 | 384716.6398 | 1923583.1992 | MONTEREY | 0.3 | 461659.9678 | 2385243.167 | 2497349.5959
CA2700589 | GLENN AVE WS #01 | 73 | 26 | 1 | 1 | 10950 | 17.1094 | 1200000 | 17.1094 | 34749.0305 | 118787.3648 | 100000 | 85000 | 1538536.3953 | 384634.0988 | 1923170.4941 | MONTEREY | 0.3 | 461560.9186 | 2384731.4127 | 2496813.7891
CA3200189 | VALIVU ESTATES MHP | 54 | 19 | 1 | 1 | 8100 | 12.6562 | 1200000 | 12.6562 | 34103.2828 | 118178.4891 | 100000 | 85000 | 1537281.7719 | 384320.443 | 1921602.2148 | PLUMAS | 0 | 0 | 1921602.2148 | 2011917.5189
CA0300062 | HOPE FOUNDATION/MORIAH HEIGHTS | 299 | 21 | 1 | 1 | 44850 | 70.0781 | 1200000 | 70.0781 | 42430.0289 | 126029.782 | 100000 | 85000 | 1553459.8109 | 388364.9527 | 1941824.7637 | AMADOR | 0 | 0 | 1941824.7637 | 2033090.5276
CA2000529 | BONADELLE RANCHOS MUTUAL WATER | 50 | 23 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | MADERA | 0 | 0 | 1921272.0508 | 2011571.8372
CA5400641 | TEVISTON CSD | 343 | 140 | 1 | 1 | 51450 | 80.3906 | 1200000 | 80.3906 | 43925.4445 | 127439.8102 | 100000 | 85000 | 1556365.2547 | 389091.3137 | 1945456.5684 | TULARE | 0 | 0 | 1945456.5684 | 2036893.0271
CA4500027 | BIG SPRINGS MUTUAL WATER SYSTEM | 97 | 42 | 1 | 1 | 14550 | 22.7344 | 1200000 | 22.7344 | 35564.7117 | 119556.4711 | 100000 | 85000 | 1540121.1828 | 385030.2957 | 1925151.4785 | SHASTA | 0 | 0 | 1925151.4785 | 2015633.598
CA0300024 | TABEAU MOBILE HOME PARK | 25 | 22 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | AMADOR | 0 | 0 | 1919208.5254 | 2009411.3261
CA1100711 | BUTTE CITY COMMUNITY S.D. | 75 | 48 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | GLENN | 0 | 0 | 1923335.5762 | 2013732.3483
CA3700922 | LIVE OAK SPRINGS WATER SYSTEM | 300 | 94 | 1 | 1 | 45000 | 70.3125 | 1200000 | 70.3125 | 42464.0156 | 126061.8281 | 100000 | 85000 | 1553525.8438 | 388381.4609 | 1941907.3047 | SAN DIEGO | 0.32 | 497128.27 | 2439035.5747 | 2553670.2467
CA3301171 | BRADFORD RUN RV | 100 | 59 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | RIVERSIDE | 0.32 | 492902.17 | 2418301.2716 | 2531961.4313
CA1700630 | PIER 1900 HOMEOWNER S ASSOCIATION | 152 | 54 | 1 | 1 | 22800 | 35.625 | 1200000 | 35.625 | 37433.9812 | 121319.0063 | 100000 | 85000 | 1543752.9875 | 385938.2469 | 1929691.2344 | LAKE | 0 | 0 | 1929691.2344 | 2020386.7224
CA5500119 | YOSEMITE VISTA ESTATES | 59 | 59 | 1 | 1 | 8850 | 13.8281 | 1200000 | 13.8281 | 34273.2164 | 118338.7195 | 100000 | 85000 | 1537611.9359 | 384402.984 | 1922014.9199 | TUOLUMNE | 0 | 0 | 1922014.9199 | 2012349.6212
CA5601144 | RANCHO SESPE WORKERS IMP ASSOC | 600 | 109 | 1 | 1 | 90000 | 140.625 | 1200000 | 140.625 | 52660.0312 | 135675.6562 | 100000 | 85000 | 1573335.6875 | 393333.9219 | 1966669.6094 | VENTURA | 0.32 | 503467.42 | 2470137.0294 | 2586233.4698
CA1900975 | CALI LAKE RV RESORT | 99 | 47 | 1 | 1 | 14850 | 23.2031 | 1200000 | 23.2031 | 35632.6852 | 119620.5633 | 100000 | 85000 | 1540253.2484 | 385063.3121 | 1925316.5605 | LOS ANGELES | 0.32 | 492881.0395 | 2418197.6 | 2531852.8872
CA2800527 | LINDA FALLS TERRACE MUTUAL | 35 | 17 | 1 | 1 | 5250 | 8.2031 | 1200000 | 8.2031 | 33457.5352 | 117569.6133 | 100000 | 85000 | 1536027.1484 | 384006.7871 | 1920033.9355 | NAPA | 0.3 | 460808.1445 | 2380842.0801 | 2492741.6578
CA5000218 | COUNTRY VILLA APTS | 60 | 23 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | STANISLAUS | 0 | 0 | 1922097.4609 | 2012436.0416
CA2701278 | RANCHO CHAPARRAL MWC | 58 | 20 | 1 | 1 | 8700 | 13.5938 | 1200000 | 13.5938 | 34239.2297 | 118306.6734 | 100000 | 85000 | 1537545.9031 | 384386.4758 | 1921932.3789 | MONTEREY | 0.3 | 461263.7709 | 2383196.1498 | 2495206.3689
CA4300551 | HAPPY ACRES MWC | 220 | 79 | 1 | 1 | 33000 | 51.5625 | 1200000 | 51.5625 | 39745.0781 | 123498.1406 | 100000 | 85000 | 1548243.2188 | 387060.8047 | 1935304.0234 | SANTA CLARA | 0.32 | 495437.83 | 2430741.8534 | 2544986.7205
CA5200526 | HIDDEN HARBOR MARINA & RVP | 70 | 70 | 1 | 1 | 10500 | 16.4062 | 1200000 | 16.4062 | 34647.0703 | 118691.2266 | 100000 | 85000 | 1538338.2969 | 384584.5742 | 1922922.8711 | TEHAMA | 0 | 0 | 1922922.8711 | 2013300.246
CA3500912 | COMSTOCK MUTUAL WATER COMPANY | 100 | 33 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SAN BENITO | 0.3 | 462095.7844 | 2387494.8859 | 2499707.1456
CA2700535 | JOST POST WA | 60 | 20 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | MONTEREY | 0.3 | 461303.3906 | 2383400.8516 | 2495420.6916
CA1500542 | WILLOW SPRINGS MOBILE HOME PARK | 275 | 104 | 1 | 1 | 41250 | 64.4531 | 1200000 | 64.4531 | 41614.3477 | 125260.6758 | 100000 | 85000 | 1551875.0234 | 387968.7559 | 1939843.7793 | KERN | 0 | 0 | 1939843.7793 | 2031016.4369
CA1700589 | BLUE LAKES MOBILE HOME PARK | 32 | 24 | 1 | 1 | 4800 | 7.5 | 1200000 | 7.5 | 33355.575 | 117473.475 | 100000 | 85000 | 1535829.05 | 383957.2625 | 1919786.3125 | LAKE | 0 | 0 | 1919786.3125 | 2010016.2692
CA2700503 | ASSISI MWC | 126 | 42 | 1 | 1 | 18900 | 29.5312 | 1200000 | 29.5312 | 36550.3266 | 120485.8078 | 100000 | 85000 | 1542036.1344 | 385509.0336 | 1927545.168 | MONTEREY | 0.3 | 462610.8403 | 2390156.0083 | 2502493.3407
CA2000561 | MD 08 NORTH FORK WATER SYSTEM | 264 | 75 | 1 | 1 | 39600 | 61.875 | 1200000 | 61.875 | 41240.4938 | 124908.1687 | 100000 | 85000 | 1551148.6625 | 387787.1656 | 1938935.8281 | MADERA | 0 | 0 | 1938935.8281 | 2030065.812
CA1800516 | LITTLE VALLEY CSD | 70 | 44 | 1 | 1 | 10500 | 16.4062 | 1200000 | 16.4062 | 34647.0703 | 118691.2266 | 100000 | 85000 | 1538338.2969 | 384584.5742 | 1922922.8711 | LASSEN | 0 | 0 | 1922922.8711 | 2013300.246
CA1700674 | WALNUT COVE MOBILE ESTATES | 200 | 60 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | LAKE | 0 | 0 | 1933653.2031 | 2024534.9037
CA4700626 | COVE MOBILE VILLA | 105 | 47 | 1 | 1 | 15750 | 24.6094 | 1200000 | 24.6094 | 35836.6055 | 119812.8398 | 100000 | 85000 | 1540649.4453 | 385162.3613 | 1925811.8066 | SISKIYOU | 0 | 0 | 1925811.8066 | 2016324.9616
CA1502056 | CLARK STREET COMMUNITY WELL | 90 | 20 | 1 | 1 | 13500 | 21.0938 | 1200000 | 21.0938 | 35326.8047 | 119332.1484 | 100000 | 85000 | 1539658.9531 | 384914.7383 | 1924573.6914 | KERN | 0 | 0 | 1924573.6914 | 2015028.6549
CA3500911 | CREEKBRIDGE MUTUAL WATER COMPANY | 69 | 22 | 1 | 1 | 10350 | 16.1719 | 1200000 | 16.1719 | 34613.0836 | 118659.1805 | 100000 | 85000 | 1538272.2641 | 384568.066 | 1922840.3301 | SAN BENITO | 0.3 | 461481.6792 | 2384322.0093 | 2496385.1437
CA5200521 | ANTELOPE CREEK MHP | 175 | 60 | 1 | 1 | 26250 | 41.0156 | 1200000 | 41.0156 | 38215.6758 | 122056.0664 | 100000 | 85000 | 1545271.7422 | 386317.9355 | 1931589.6777 | TEHAMA | 0 | 0 | 1931589.6777 | 2022374.3926
CA2300646 | BELLA SHORES MOBILE HOME PARK | 80 | 60 | 1 | 1 | 12000 | 18.75 | 1200000 | 18.75 | 34986.9375 | 119011.6875 | 100000 | 85000 | 1538998.625 | 384749.6562 | 1923748.2812 | MENDOCINO | 0 | 0 | 1923748.2812 | 2014164.4505
CA5403217 | OKIEVILLE HIGHLAND ACRES MWC | 300 | 72 | 1 | 1 | 45000 | 70.3125 | 1200000 | 70.3125 | 42464.0156 | 126061.8281 | 100000 | 85000 | 1553525.8438 | 388381.4609 | 1941907.3047 | TULARE | 0 | 0 | 1941907.3047 | 2033176.948
CA4900795 | STONEGATE MOBILE HOME PARK | 100 | 75 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SONOMA | 0.3 | 462095.7844 | 2387494.8859 | 2499707.1456
CA3900661 | MAPACHE TRAILER PARK | 275 | 99 | 1 | 1 | 41250 | 64.4531 | 1200000 | 64.4531 | 41614.3477 | 125260.6758 | 100000 | 85000 | 1551875.0234 | 387968.7559 | 1939843.7793 | SAN JOAQUIN | 0 | 0 | 1939843.7793 | 2031016.4369
CA2600532 | LUNDY MUTUAL WATER COMPANY | 70 | 32 | 1 | 1 | 10500 | 16.4062 | 1200000 | 16.4062 | 34647.0703 | 118691.2266 | 100000 | 85000 | 1538338.2969 | 384584.5742 | 1922922.8711 | MONO | 0 | 0 | 1922922.8711 | 2013300.246
CA0707519 | DUTCH SLOUGH WATER WORKS | 49 | 58 | 1 | 1 | 7350 | 11.4844 | 1200000 | 11.4844 | 33933.3492 | 118018.2586 | 100000 | 85000 | 1536951.6078 | 384237.902 | 1921189.5098 | CONTRA COSTA | 0.3 | 461085.4823 | 2382274.9921 | 2494241.9167
CA5200562 | SKY VIEW COUNTY WATER | 412 | 85 | 1 | 1 | 61800 | 96.5625 | 1200000 | 96.5625 | 46270.5281 | 129650.9906 | 100000 | 85000 | 1560921.5188 | 390230.3797 | 1951151.8984 | TEHAMA | 0 | 0 | 1951151.8984 | 2042856.0377
CA2702055 | VIERRA KNOLLS MWC | 66 | 22 | 1 | 1 | 9900 | 15.4688 | 1200000 | 15.4688 | 34511.1234 | 118563.0422 | 100000 | 85000 | 1538074.1656 | 384518.5414 | 1922592.707 | MONTEREY | 0.3 | 461422.2497 | 2384014.9567 | 2496063.6597
CA1500599 | CHOCTAW VALLEY MUTUAL WATER CO. | 44 | 18 | 1 | 1 | 6600 | 10.3125 | 1200000 | 10.3125 | 33763.4156 | 117858.0281 | 100000 | 85000 | 1536621.4438 | 384155.3609 | 1920776.8047 | KERN | 0 | 0 | 1920776.8047 | 2011053.3145
CA1700580 | TWIN CREEKS MOBILE AND RV VILLAGE | 50 | 17 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | LAKE | 0 | 0 | 1921272.0508 | 2011571.8372
CA1700536 | SUNRISE SHORE MUTUAL WATER COMPANY | 83 | 42 | 1 | 1 | 12450 | 19.4531 | 1200000 | 19.4531 | 35088.8977 | 119107.8258 | 100000 | 85000 | 1539196.7234 | 384799.1809 | 1923995.9043 | LAKE | 0 | 0 | 1923995.9043 | 2014423.7118
CA0800861 | RESERVATION RANCH | 50 | 20 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | DEL NORTE | 0 | 0 | 1921272.0508 | 2011571.8372
CA1900767 | GOLDEN VALLEY MUNICIPAL WATER DISTRICT | 70 | 18 | 1 | 1 | 10500 | 16.4062 | 1200000 | 16.4062 | 34647.0703 | 118691.2266 | 100000 | 85000 | 1538338.2969 | 384584.5742 | 1922922.8711 | LOS ANGELES | 0.32 | 492268.255 | 2415191.1261 | 2528705.109
CA1000405 | PIEDRA PARK ASSOCIATION | 25 | 15 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | FRESNO | 0 | 0 | 1919208.5254 | 2009411.3261
CA3900720 | SHADED TERRACE PWS | 161 | 72 | 1 | 1 | 24150 | 37.7344 | 1200000 | 37.7344 | 37739.8617 | 121607.4211 | 100000 | 85000 | 1544347.2828 | 386086.8207 | 1930434.1035 | SAN JOAQUIN | 0 | 0 | 1930434.1035 | 2021164.5064
CA5400682 | PLAINVIEW MWC - CENTRAL WATER | 138 | 42 | 1 | 1 | 20700 | 32.3438 | 1200000 | 32.3438 | 36958.1672 | 120870.3609 | 100000 | 85000 | 1542828.5281 | 385707.132 | 1928535.6602 | TULARE | 0 | 0 | 1928535.6602 | 2019176.8362
CA4900573 | WILSHIRE HEIGHTS MUTUAL WATER COMPANY | 100 | 41 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SONOMA | 0.3 | 462095.7844 | 2387494.8859 | 2499707.1456
CA3400192 | TUNNEL TRAILER PARK | 44 | 21 | 1 | 1 | 6600 | 10.3125 | 1200000 | 10.3125 | 33763.4156 | 117858.0281 | 100000 | 85000 | 1536621.4438 | 384155.3609 | 1920776.8047 | SACRAMENTO | 0.32 | 491718.862 | 2412495.6667 | 2525882.963
CA4900785 | NOEL HEIGHTS-CAL WATER SERVICE (PUC) | 137 | 50 | 1 | 1 | 20550 | 32.1094 | 1200000 | 32.1094 | 36924.1805 | 120838.3148 | 100000 | 85000 | 1542762.4953 | 385690.6238 | 1928453.1191 | SONOMA | 0.3 | 462828.7486 | 2391281.8677 | 2503672.1155
CA2300514 | ELK COUNTY WATER DISTRICT | 380 | 99 | 1 | 1 | 57000 | 89.0625 | 1200000 | 89.0625 | 45182.9531 | 128625.5156 | 100000 | 85000 | 1558808.4688 | 389702.1172 | 1948510.5859 | MENDOCINO | 0 | 0 | 1948510.5859 | 2040090.5835
CA4910029 | CAMP MEEKER WATER SYSTEM | 1171 | 356 | 1 | 1 | 175650 | 274.4531 | 1200000 | 274.4531 | 72066.4477 | 153973.9758 | 100000 | 85000 | 1611040.4234 | 402760.1059 | 2013800.5293 | SONOMA | 0.3 | 483312.127 | 2497112.6563 | 2614476.9512
CA4900611 | RAINS CREEK WATER DISTRICT | 208 | 63 | 1 | 1 | 31200 | 48.75 | 1200000 | 48.75 | 39337.2375 | 123113.5875 | 100000 | 85000 | 1547450.825 | 386862.7062 | 1934313.5312 | SONOMA | 0.3 | 464235.2475 | 2398548.7788 | 2511280.5714
CA3901031 | 132 INVESTMENTS WATER SYSTEM | 100 | 93 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SAN JOAQUIN | 0 | 0 | 1925399.1016 | 2015892.8593
CA4300924 | PARKWAY LAKES RV PARK | 250 | 121 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | SANTA CLARA | 0.32 | 496071.745 | 2433851.9989 | 2548243.0429
CA5400819 | MOUNTAIN VIEW MHP | 44 | 24 | 1 | 1 | 6600 | 10.3125 | 1200000 | 10.3125 | 33763.4156 | 117858.0281 | 100000 | 85000 | 1536621.4438 | 384155.3609 | 1920776.8047 | TULARE | 0 | 0 | 1920776.8047 | 2011053.3145
CA4500089 | PINE RIDGE PARK ESTATES | 44 | 27 | 1 | 1 | 6600 | 10.3125 | 1200000 | 10.3125 | 33763.4156 | 117858.0281 | 100000 | 85000 | 1536621.4438 | 384155.3609 | 1920776.8047 | SHASTA | 0 | 0 | 1920776.8047 | 2011053.3145
CA5000071 | TWIN CYPRESS MOBILE HOME PARK | 112 | 45 | 1 | 1 | 16800 | 26.25 | 1200000 | 26.25 | 36074.5125 | 120037.1625 | 100000 | 85000 | 1541111.675 | 385277.9188 | 1926389.5938 | STANISLAUS | 0 | 0 | 1926389.5938 | 2016929.9047
CA2702094 | BLACKIE RD WS #18 | 60 | 21 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | MONTEREY | 0.3 | 461303.3906 | 2383400.8516 | 2495420.6916
CA5200556 | MAYWOOD MOBILE HOME PARK | 140 | 50 | 1 | 1 | 21000 | 32.8125 | 1200000 | 32.8125 | 37026.1406 | 120934.4531 | 100000 | 85000 | 1542960.5938 | 385740.1484 | 1928700.7422 | TEHAMA | 0 | 0 | 1928700.7422 | 2019349.6771
CA1206004 | PALMER CREEK CSD | 320 | 132 | 1 | 1 | 48000 | 75 | 1200000 | 75 | 43143.75 | 126702.75 | 100000 | 85000 | 1554846.5 | 388711.625 | 1943558.125 | HUMBOLDT | 0 | 0 | 1943558.125 | 2034905.3569
CA3700422 | LAGUNA MOUNTIAN MUTUAL WATER CO. | 100 | 28 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SAN DIEGO | 0.32 | 492902.17 | 2418301.2716 | 2531961.4313
CA3200155 | FRCCSD HOT SPRINGS | 25 | 17 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | PLUMAS | 0 | 0 | 1919208.5254 | 2009411.3261
CA2700691 | PESANTE RD WS #06 | 48 | 16 | 1 | 1 | 7200 | 11.25 | 1200000 | 11.25 | 33899.3625 | 117986.2125 | 100000 | 85000 | 1536885.575 | 384221.3937 | 1921106.9688 | MONTEREY | 0.3 | 461065.6725 | 2382172.6412 | 2494134.7554
CA0707613 | WILLOW MOBILE HOME PARK | 350 | 172 | 1 | 1 | 52500 | 82.0312 | 1200000 | 82.0312 | 44163.3516 | 127664.1328 | 100000 | 85000 | 1556827.4844 | 389206.8711 | 1946034.3555 | CONTRA COSTA | 0.3 | 467048.2453 | 2413082.6008 | 2526497.483
CA3110018 | TAHOE PARK WATER COMPANY | 750 | 445 | 1 | 1 | 112500 | 175.7812 | 1200000 | 175.7812 | 57758.0391 | 140482.5703 | 100000 | 85000 | 1583240.6094 | 395810.1523 | 1979050.7617 | PLACER | 0 | 0 | 1979050.7617 | 2072066.1475
CA3301800 | STONEWOOD CANYON ESTATES | 40 | 26 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | RIVERSIDE | 0.32 | 491634.34 | 2412080.9806 | 2525448.7867
CA2701670 | LANGLEY/VALLE PACIFICO WS | 81 | 31 | 1 | 1 | 12150 | 18.9844 | 1200000 | 18.9844 | 35020.9242 | 119043.7336 | 100000 | 85000 | 1539064.6578 | 384766.1645 | 1923830.8223 | MONTEREY | 0.3 | 461719.3973 | 2385550.2196 | 2497671.0799
CA5200551 | WOODSON BRIDGE MHP | 158 | 104 | 1 | 1 | 23700 | 37.0312 | 1200000 | 37.0312 | 37637.9016 | 121511.2828 | 100000 | 85000 | 1544149.1844 | 386037.2961 | 1930186.4805 | TEHAMA | 0 | 0 | 1930186.4805 | 2020905.2451
CA2000589 | MAMMOTH POOL MOBILE HOME PARK | 60 | 32 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | MADERA | 0 | 0 | 1922097.4609 | 2012436.0416
CA2000511 | MD 85 VALETA | 45 | 20 | 1 | 1 | 6750 | 10.5469 | 1200000 | 10.5469 | 33797.4023 | 117890.0742 | 100000 | 85000 | 1536687.4766 | 384171.8691 | 1920859.3457 | MADERA | 0 | 0 | 1920859.3457 | 2011139.735
CA1700561 | BLUE LAKES IMPROVEMENT CLUB | 80 | 41 | 1 | 1 | 12000 | 18.75 | 1200000 | 18.75 | 34986.9375 | 119011.6875 | 100000 | 85000 | 1538998.625 | 384749.6562 | 1923748.2812 | LAKE | 0 | 0 | 1923748.2812 | 2014164.4505
CA3900607 | COUNTRY SQUIRE MOBILE ESTATES & WATER SY | 64 | 49 | 1 | 1 | 9600 | 15 | 1200000 | 15 | 34443.15 | 118498.95 | 100000 | 85000 | 1537942.1 | 384485.525 | 1922427.625 | SAN JOAQUIN | 0 | 0 | 1922427.625 | 2012781.7234
CA5400744 | EAST THREE RIVERS MUTUAL WATER CORP | 40 | 15 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | TULARE | 0 | 0 | 1920446.6406 | 2010707.6327
CA2700687 | PESANTE RD WS #02 | 120 | 40 | 1 | 1 | 18000 | 28.125 | 1200000 | 28.125 | 36346.4062 | 120293.5312 | 100000 | 85000 | 1541639.9375 | 385409.9844 | 1927049.9219 | MONTEREY | 0.3 | 462491.9813 | 2389541.9031 | 2501850.3726
CA2300717 | CREEKSIDE CABINS & RV RESORT | 124 | 55 | 1 | 1 | 18600 | 29.0625 | 1200000 | 29.0625 | 36482.3531 | 120421.7156 | 100000 | 85000 | 1541904.0688 | 385476.0172 | 1927380.0859 | MENDOCINO | 0 | 0 | 1927380.0859 | 2017966.95
CA3400155 | SEQUOIA WATER ASSOC | 54 | 18 | 1 | 1 | 8100 | 12.6562 | 1200000 | 12.6562 | 34103.2828 | 118178.4891 | 100000 | 85000 | 1537281.7719 | 384320.443 | 1921602.2148 | SACRAMENTO | 0.32 | 491930.167 | 2413532.3818 | 2526968.4038
CA3400138 | LOCKE WATER WORKS CO [SWS] | 80 | 44 | 1 | 1 | 12000 | 18.75 | 1200000 | 18.75 | 34986.9375 | 119011.6875 | 100000 | 85000 | 1538998.625 | 384749.6562 | 1923748.2812 | SACRAMENTO | 0.32 | 492479.56 | 2416227.8413 | 2529790.5498
CA3303087 | SAN JOSE COMMUNITY WATER SYSTEM | 71 | 15 | 1 | 1 | 10650 | 16.6406 | 1200000 | 16.6406 | 34681.057 | 118723.2727 | 100000 | 85000 | 1538404.3297 | 384601.0824 | 1923005.4121 | RIVERSIDE | 0.32 | 492289.3855 | 2415294.7976 | 2528813.6531
CA2701633 | PARADISE RD WS #21 | 48 | 16 | 1 | 1 | 7200 | 11.25 | 1200000 | 11.25 | 33899.3625 | 117986.2125 | 100000 | 85000 | 1536885.575 | 384221.3937 | 1921106.9688 | MONTEREY | 0.3 | 461065.6725 | 2382172.6412 | 2494134.7554
CA5200560 | MIRA MONTE WATER CO. | 142 | 41 | 1 | 1 | 21300 | 33.2812 | 1200000 | 33.2812 | 37094.1141 | 120998.5453 | 100000 | 85000 | 1543092.6594 | 385773.1648 | 1928865.8242 | TEHAMA | 0 | 0 | 1928865.8242 | 2019522.518
CA3600386 | FOOTHILL ESTATES MHP | 135 | 33 | 1 | 1 | 20250 | 31.6406 | 1200000 | 31.6406 | 36856.207 | 120774.2227 | 100000 | 85000 | 1542630.4297 | 385657.6074 | 1928288.0371 | SAN BERNARDINO | 0.3 | 462789.1289 | 2391077.166 | 2503457.7928
CA3500510 | MCMAHON ROAD MUTUAL WATER COMPANY | 102 | 32 | 1 | 1 | 15300 | 23.9062 | 1200000 | 23.9062 | 35734.6453 | 119716.7016 | 100000 | 85000 | 1540451.3469 | 385112.8367 | 1925564.1836 | SAN BENITO | 0.3 | 462135.4041 | 2387699.5877 | 2499921.4683
CA4900512 | HAPPY ACRES MUTUAL BENEFIT WATER SYSTEM | 260 | 79 | 1 | 1 | 39000 | 60.9375 | 1200000 | 60.9375 | 41104.5469 | 124779.9844 | 100000 | 85000 | 1550884.5312 | 387721.1328 | 1938605.6641 | SONOMA | 0.3 | 465265.3594 | 2403871.0234 | 2516852.9615
CA0707585 | MORAGA HEIGHTS MUTUAL WATER | 60 | 20 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | CONTRA COSTA | 0.3 | 461303.3906 | 2383400.8516 | 2495420.6916
CA5403212 | MONSON WATER SYSTEM | 140 | 32 | 1 | 1 | 21000 | 32.8125 | 1200000 | 32.8125 | 37026.1406 | 120934.4531 | 100000 | 85000 | 1542960.5938 | 385740.1484 | 1928700.7422 | TULARE | 0 | 0 | 1928700.7422 | 2019349.6771
CA4500290 | PINE GROVE MOBILEHOME PARK | 53 | 19 | 1 | 1 | 7950 | 12.4219 | 1200000 | 12.4219 | 34069.2961 | 118146.443 | 100000 | 85000 | 1537215.7391 | 384303.9348 | 1921519.6738 | SHASTA | 0 | 0 | 1921519.6738 | 2011831.0985
CA3900512 | MORADA ACRES WATER SYSTEM | 105 | 32 | 1 | 1 | 15750 | 24.6094 | 1200000 | 24.6094 | 35836.6055 | 119812.8398 | 100000 | 85000 | 1540649.4453 | 385162.3613 | 1925811.8066 | SAN JOAQUIN | 0 | 0 | 1925811.8066 | 2016324.9616
CA2700733 | SAN JUAN RD WS #01 | 49 | 15 | 1 | 1 | 7350 | 11.4844 | 1200000 | 11.4844 | 33933.3492 | 118018.2586 | 100000 | 85000 | 1536951.6078 | 384237.902 | 1921189.5098 | MONTEREY | 0.3 | 461085.4823 | 2382274.9921 | 2494241.9167
CA1000295 | KINGS PARK APARTMENTS | 120 | 41 | 1 | 1 | 18000 | 28.125 | 1200000 | 28.125 | 36346.4062 | 120293.5312 | 100000 | 85000 | 1541639.9375 | 385409.9844 | 1927049.9219 | FRESNO | 0 | 0 | 1927049.9219 | 2017621.2682
CA5400735 | RODRIGUEZ LABOR CAMP | 110 | 35 | 1 | 1 | 16500 | 25.7812 | 1200000 | 25.7812 | 36006.5391 | 119973.0703 | 100000 | 85000 | 1540979.6094 | 385244.9023 | 1926224.5117 | TULARE | 0 | 0 | 1926224.5117 | 2016757.0638
CA1700702 | INNISFREE WATER COMPANY | 56 | 17 | 1 | 1 | 8400 | 13.125 | 1200000 | 13.125 | 34171.2562 | 118242.5813 | 100000 | 85000 | 1537413.8375 | 384353.4594 | 1921767.2969 | LAKE | 0 | 0 | 1921767.2969 | 2012090.3598
CA5410039 | PLAINVIEW MUTUAL WATER COMPANY | 617 | 187 | 1 | 1 | 92550 | 144.6094 | 1200000 | 144.6094 | 53237.8055 | 136220.4398 | 100000 | 85000 | 1574458.2453 | 393614.5613 | 1968072.8066 | TULARE | 0 | 0 | 1968072.8066 | 2060572.2286
CA2701063 | RIVER RD WS #25 | 65 | 19 | 1 | 1 | 9750 | 15.2344 | 1200000 | 15.2344 | 34477.1367 | 118530.9961 | 100000 | 85000 | 1538008.1328 | 384502.0332 | 1922510.166 | MONTEREY | 0.3 | 461402.4398 | 2383912.6059 | 2495956.4983
CA1400109 | SIERRA NORTH COMMUNITY SERVICE DISTRICT | 45 | 16 | 1 | 1 | 6750 | 10.5469 | 1200000 | 10.5469 | 33797.4023 | 117890.0742 | 100000 | 85000 | 1536687.4766 | 384171.8691 | 1920859.3457 | INYO | 0 | 0 | 1920859.3457 | 2011139.735
CA1000627 | ZONNEVELD DAIRY - CERINI | 48 | 17 | 1 | 1 | 7200 | 11.25 | 1200000 | 11.25 | 33899.3625 | 117986.2125 | 100000 | 85000 | 1536885.575 | 384221.3937 | 1921106.9688 | FRESNO | 0 | 0 | 1921106.9688 | 2011398.9963
CA5400660 | LAKE SUCCESS MOBILE LODGE | 80 | 19 | 1 | 1 | 12000 | 18.75 | 1200000 | 18.75 | 34986.9375 | 119011.6875 | 100000 | 85000 | 1538998.625 | 384749.6562 | 1923748.2812 | TULARE | 0 | 0 | 1923748.2812 | 2014164.4505
CA2210925 | YOSEMITE TERRACE ESTATES | 130 | 53 | 1 | 1 | 19500 | 30.4688 | 1200000 | 30.4688 | 36686.2734 | 120613.9922 | 100000 | 85000 | 1542300.2656 | 385575.0664 | 1927875.332 | MARIPOSA | 0 | 0 | 1927875.332 | 2018485.4726
CA1900154 | TIERRA BONITA MUTUAL WATER | 75 | 32 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | LOS ANGELES | 0.32 | 492373.9075 | 2415709.4837 | 2529247.8294
CA2700837 | BLACKIE RD WS #05 | 62 | 16 | 1 | 1 | 9300 | 14.5312 | 1200000 | 14.5312 | 34375.1766 | 118434.8578 | 100000 | 85000 | 1537810.0344 | 384452.5086 | 1922262.543 | MONTEREY | 0.3 | 461343.0103 | 2383605.5533 | 2495635.0143
CA1400025 | VALLEY VISTA MUTUAL WATER COMPANY | 70 | 25 | 1 | 1 | 10500 | 16.4062 | 1200000 | 16.4062 | 34647.0703 | 118691.2266 | 100000 | 85000 | 1538338.2969 | 384584.5742 | 1922922.8711 | INYO | 0 | 0 | 1922922.8711 | 2013300.246
CA1009120 | RAU DAIRY | 105 | 43 | 1 | 1 | 15750 | 24.6094 | 1200000 | 24.6094 | 35836.6055 | 119812.8398 | 100000 | 85000 | 1540649.4453 | 385162.3613 | 1925811.8066 | FRESNO | 0 | 0 | 1925811.8066 | 2016324.9616
CA0707601 | RUSSOS MOBILE PARK | 110 | 20 | 1 | 1 | 16500 | 25.7812 | 1200000 | 25.7812 | 36006.5391 | 119973.0703 | 100000 | 85000 | 1540979.6094 | 385244.9023 | 1926224.5117 | CONTRA COSTA | 0.3 | 462293.8828 | 2388518.3945 | 2500778.7591
CA1400511 | MEADOW LAKE APARTMENTS | 22 | 16 | 1 | 1 | 3300 | 5.1562 | 1200000 | 5.1562 | 33015.7078 | 117153.0141 | 100000 | 85000 | 1535168.7219 | 383792.1805 | 1918960.9023 | INYO | 0 | 0 | 1918960.9023 | 2009152.0648
CA5200502 | LAS FLORES WATER WORKS | 191 | 63 | 1 | 1 | 28650 | 44.7656 | 1200000 | 44.7656 | 38759.4633 | 122568.8039 | 100000 | 85000 | 1546328.2672 | 386582.0668 | 1932910.334 | TEHAMA | 0 | 0 | 1932910.334 | 2023757.1197
CA1400036 | KEELER COMMUNITY SERVICE DISTRICT | 66 | 83 | 1 | 1 | 9900 | 15.4688 | 1200000 | 15.4688 | 34511.1234 | 118563.0422 | 100000 | 85000 | 1538074.1656 | 384518.5414 | 1922592.707 | INYO | 0 | 0 | 1922592.707 | 2012954.5643
CA3600397 | MOSS MOBILE MANOR | 290 | 43 | 1 | 1 | 43500 | 67.9688 | 1200000 | 67.9688 | 42124.1484 | 125741.3672 | 100000 | 85000 | 1552865.5156 | 388216.3789 | 1941081.8945 | SAN BERNARDINO | 0.3 | 465859.6547 | 2406941.5492 | 2520067.802
CA0400042 | FOREST VILLAGE LLC | 34 | 21 | 1 | 1 | 5100 | 7.9688 | 1200000 | 7.9688 | 33423.5484 | 117537.5672 | 100000 | 85000 | 1535961.1156 | 383990.2789 | 1919951.3945 | BUTTE | 0 | 0 | 1919951.3945 | 2010189.1101
CA4900674 | PINE HILL TERRACE MOBILE HOME PARK | 27 | 23 | 1 | 1 | 4050 | 6.3281 | 1200000 | 6.3281 | 33185.6414 | 117313.2445 | 100000 | 85000 | 1535498.8859 | 383874.7215 | 1919373.6074 | SONOMA | 0.3 | 460649.6658 | 2380023.2732 | 2491884.367
CA3500581 | RANCHO SAN JOAQUIN MWC | 96 | 30 | 1 | 1 | 14400 | 22.5 | 1200000 | 22.5 | 35530.725 | 119524.425 | 100000 | 85000 | 1540055.15 | 385013.7875 | 1925068.9375 | SAN BENITO | 0.3 | 462016.545 | 2387085.4825 | 2499278.5002
CA5000080 | COUNTRY WESTERN MOBILE HOME PARK | 90 | 55 | 1 | 1 | 13500 | 21.0938 | 1200000 | 21.0938 | 35326.8047 | 119332.1484 | 100000 | 85000 | 1539658.9531 | 384914.7383 | 1924573.6914 | STANISLAUS | 0 | 0 | 1924573.6914 | 2015028.6549
CA4500054 | BALLS FERRY FISHING RESORT | 204 | 75 | 1 | 1 | 30600 | 47.8125 | 1200000 | 47.8125 | 39201.2906 | 122985.4031 | 100000 | 85000 | 1547186.6938 | 386796.6734 | 1933983.3672 | SHASTA | 0 | 0 | 1933983.3672 | 2024880.5854
CA1900868 | RIVERS END TRAILER PARK | 35 | 45 | 1 | 1 | 5250 | 8.2031 | 1200000 | 8.2031 | 33457.5352 | 117569.6133 | 100000 | 85000 | 1536027.1484 | 384006.7871 | 1920033.9355 | LOS ANGELES | 0.32 | 491528.6875 | 2411562.623 | 2524906.0663
CA2700686 | GARLEN COURT WS | 65 | 17 | 1 | 1 | 9750 | 15.2344 | 1200000 | 15.2344 | 34477.1367 | 118530.9961 | 100000 | 85000 | 1538008.1328 | 384502.0332 | 1922510.166 | MONTEREY | 0.3 | 461402.4398 | 2383912.6059 | 2495956.4983
CA2701589 | SUNNY ACRES MWS | 45 | 15 | 1 | 1 | 6750 | 10.5469 | 1200000 | 10.5469 | 33797.4023 | 117890.0742 | 100000 | 85000 | 1536687.4766 | 384171.8691 | 1920859.3457 | MONTEREY | 0.3 | 461006.243 | 2381865.5887 | 2493813.2713
CA2000800 | MARQUEZ RENTAL | 50 | 20 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | MADERA | 0 | 0 | 1921272.0508 | 2011571.8372
CA4300542 | SAN MARTIN COUNTY WATER DISTRICT | 618 | 185 | 1 | 1 | 92700 | 144.8438 | 1200000 | 144.8438 | 53271.7922 | 136252.4859 | 100000 | 85000 | 1574524.2781 | 393631.0695 | 1968155.3477 | SANTA CLARA | 0.32 | 503847.769 | 2472003.1167 | 2588187.2631
CA4200579 | ROSARIO PARK | 38 | 19 | 1 | 1 | 5700 | 8.9062 | 1200000 | 8.9062 | 33559.4953 | 117665.7516 | 100000 | 85000 | 1536225.2469 | 384056.3117 | 1920281.5586 | SANTA BARBARA | 0.3 | 460867.5741 | 2381149.1327 | 2493063.1419
CA1502670 | FAIRVIEW WATER COMPANY, LLC | 240 | 72 | 1 | 1 | 36000 | 56.25 | 1200000 | 56.25 | 40424.8125 | 124139.0625 | 100000 | 85000 | 1549563.875 | 387390.9688 | 1936954.8438 | KERN | 0 | 0 | 1936954.8438 | 2027991.7214
CA2701040 | MCCOY RD WS #05 | 72 | 24 | 1 | 1 | 10800 | 16.875 | 1200000 | 16.875 | 34715.0437 | 118755.3188 | 100000 | 85000 | 1538470.3625 | 384617.5906 | 1923087.9531 | MONTEREY | 0.3 | 461541.1088 | 2384629.0619 | 2496706.6278
CA1500442 | SUNSET APARTMENTS WS | 37 | 20 | 1 | 1 | 5550 | 8.6719 | 1200000 | 8.6719 | 33525.5086 | 117633.7055 | 100000 | 85000 | 1536159.2141 | 384039.8035 | 1920199.0176 | KERN | 0 | 0 | 1920199.0176 | 2010448.3714
CA3900523 | MORADA MANOR WATER SYSTEM | 109 | 34 | 1 | 1 | 16350 | 25.5469 | 1200000 | 25.5469 | 35972.5523 | 119941.0242 | 100000 | 85000 | 1540913.5766 | 385228.3941 | 1926141.9707 | SAN JOAQUIN | 0 | 0 | 1926141.9707 | 2016670.6433
CA4400557 | ST FRANCIS TRACT WATER SYSTEM | 118 | 29 | 1 | 1 | 17700 | 27.6562 | 1200000 | 27.6562 | 36278.4328 | 120229.4391 | 100000 | 85000 | 1541507.8719 | 385376.968 | 1926884.8398 | SANTA CRUZ | 0.3 | 462452.3616 | 2389337.2014 | 2501636.0499
CA1200687 | RIVERBEND MOBILE HOME PARK | 60 | 28 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | HUMBOLDT | 0 | 0 | 1922097.4609 | 2012436.0416
CA1500413 | TEJON RANCH MAIN HEADQUARTERS | 132 | 33 | 1 | 1 | 19800 | 30.9375 | 1200000 | 30.9375 | 36754.2469 | 120678.0844 | 100000 | 85000 | 1542432.3313 | 385608.0828 | 1928040.4141 | KERN | 0 | 0 | 1928040.4141 | 2018658.3135
CA0707575 | FRANKS MARINA | 185 | 66 | 1 | 1 | 27750 | 43.3594 | 1200000 | 43.3594 | 38555.543 | 122376.5273 | 100000 | 85000 | 1545932.0703 | 386483.0176 | 1932415.0879 | CONTRA COSTA | 0.3 | 463779.6211 | 2396194.709 | 2508815.8603
CA0800603 | BUTTE COURT MOBILE HOME PARK | 67 | 23 | 1 | 1 | 10050 | 15.7031 | 1200000 | 15.7031 | 34545.1102 | 118595.0883 | 100000 | 85000 | 1538140.1984 | 384535.0496 | 1922675.248 | DEL NORTE | 0 | 0 | 1922675.248 | 2013040.9847
CA2300837 | YOKAYO TRIBE OF INDIANS | 75 | 23 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | MENDOCINO | 0 | 0 | 1923335.5762 | 2013732.3483
CA5400504 | PORTERVILLE MOBILE VILLAGE | 154 | 62 | 1 | 1 | 23100 | 36.0938 | 1200000 | 36.0938 | 37501.9547 | 121383.0984 | 100000 | 85000 | 1543885.0531 | 385971.2633 | 1929856.3164 | TULARE | 0 | 0 | 1929856.3164 | 2020559.5633
CA5200546 | ANTELOPE-HOMEWOOD MHP | 140 | 24 | 1 | 1 | 21000 | 32.8125 | 1200000 | 32.8125 | 37026.1406 | 120934.4531 | 100000 | 85000 | 1542960.5938 | 385740.1484 | 1928700.7422 | TEHAMA | 0 | 0 | 1928700.7422 | 2019349.6771
CA1000247 | SHERWOOD FOREST MHP | 75 | 48 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | FRESNO | 0 | 0 | 1923335.5762 | 2013732.3483
CA1000238 | CAMDEN TRAILER PARK | 75 | 26 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | FRESNO | 0 | 0 | 1923335.5762 | 2013732.3483
CA4400763 | BUENA VISTA MIGRANT CENTER | 455 | 140 | 1 | 1 | 68250 | 106.6406 | 1200000 | 106.6406 | 47731.957 | 131028.9727 | 100000 | 85000 | 1563760.9297 | 390940.2324 | 1954701.1621 | SANTA CRUZ | 0.3 | 469128.2789 | 2423829.441 | 2537749.4247
CA5602111 | NYELAND ACRES MUTUAL WATER CO | 915 | 183 | 1 | 1 | 137250 | 214.4531 | 1200000 | 214.4531 | 63365.8477 | 145770.1758 | 100000 | 85000 | 1594136.0234 | 398534.0059 | 1992670.0293 | VENTURA | 0.32 | 510123.5275 | 2502793.5568 | 2620424.854
CA2701553 | POND-DEROSA OAKS WC | 216 | 75 | 1 | 1 | 32400 | 50.625 | 1200000 | 50.625 | 39609.1312 | 123369.9563 | 100000 | 85000 | 1547979.0875 | 386994.7719 | 1934973.8594 | MONTEREY | 0.3 | 464393.7263 | 2399367.5856 | 2512137.8621
CA0707597 | SANDY POINT MOBILE HOME PARK | 67 | 24 | 1 | 1 | 10050 | 15.7031 | 1200000 | 15.7031 | 34545.1102 | 118595.0883 | 100000 | 85000 | 1538140.1984 | 384535.0496 | 1922675.248 | CONTRA COSTA | 0.3 | 461442.0595 | 2384117.3076 | 2496170.821
CA1800524 | LASSEN MOBILE HOME PARK | 62 | 30 | 1 | 1 | 9300 | 14.5312 | 1200000 | 14.5312 | 34375.1766 | 118434.8578 | 100000 | 85000 | 1537810.0344 | 384452.5086 | 1922262.543 | LASSEN | 0 | 0 | 1922262.543 | 2012608.8825
CA1500455 | WILLIAM FISHER MEMORIAL WATER COMPANY | 56 | 16 | 1 | 1 | 8400 | 13.125 | 1200000 | 13.125 | 34171.2562 | 118242.5813 | 100000 | 85000 | 1537413.8375 | 384353.4594 | 1921767.2969 | KERN | 0 | 0 | 1921767.2969 | 2012090.3598
CA3400172 | TOKAY PARK WATER CO | 525 | 198 | 1 | 1 | 78750 | 123.0469 | 1200000 | 123.0469 | 50111.0273 | 133272.1992 | 100000 | 85000 | 1568383.2266 | 392095.8066 | 1960479.0332 | SACRAMENTO | 0.32 | 501882.6325 | 2462361.6657 | 2578092.664
CA5200657 | NORCAL WATER WORKS | 45 | 17 | 1 | 1 | 6750 | 10.5469 | 1200000 | 10.5469 | 33797.4023 | 117890.0742 | 100000 | 85000 | 1536687.4766 | 384171.8691 | 1920859.3457 | TEHAMA | 0 | 0 | 1920859.3457 | 2011139.735
CA4900620 | AUSTIN ACRES MUTUAL WATER COMPANY | 67 | 24 | 1 | 1 | 10050 | 15.7031 | 1200000 | 15.7031 | 34545.1102 | 118595.0883 | 100000 | 85000 | 1538140.1984 | 384535.0496 | 1922675.248 | SONOMA | 0.3 | 461442.0595 | 2384117.3076 | 2496170.821
CA3701184 | BUTTERFIELD RANCH | 350 | 75 | 1 | 1 | 52500 | 82.0312 | 1200000 | 82.0312 | 44163.3516 | 127664.1328 | 100000 | 85000 | 1556827.4844 | 389206.8711 | 1946034.3555 | SAN DIEGO | 0.32 | 498184.795 | 2444219.1505 | 2559097.4505
CA5200600 | GURNSEY AVENUE MUTUAL WATER SYSTEM | 25 | 15 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | TEHAMA | 0 | 0 | 1919208.5254 | 2009411.3261
CA0400078 | FOREST KNOLLS MUTUAL WATER CO | 46 | 21 | 1 | 1 | 6900 | 10.7812 | 1200000 | 10.7812 | 33831.3891 | 117922.1203 | 100000 | 85000 | 1536753.5094 | 384188.3773 | 1920941.8867 | BUTTE | 0 | 0 | 1920941.8867 | 2011226.1554
CA2700624 | LEAFWOOD COMMUNITY WA | 66 | 23 | 1 | 1 | 9900 | 15.4688 | 1200000 | 15.4688 | 34511.1234 | 118563.0422 | 100000 | 85000 | 1538074.1656 | 384518.5414 | 1922592.707 | MONTEREY | 0.3 | 461422.2497 | 2384014.9567 | 2496063.6597
CA1502608 | OWENS PEAK WEST | 79 | 24 | 1 | 1 | 11850 | 18.5156 | 1200000 | 18.5156 | 34952.9508 | 118979.6414 | 100000 | 85000 | 1538932.5922 | 384733.148 | 1923665.7402 | KERN | 0 | 0 | 1923665.7402 | 2014078.03
CA3500575 | SPRINGWOOD ESTATES MWC | 50 | 15 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | SAN BENITO | 0.3 | 461105.2922 | 2382377.343 | 2494349.0781
CA4300996 | VALLEY VIEW RANCHES | 45 | 16 | 1 | 1 | 6750 | 10.5469 | 1200000 | 10.5469 | 33797.4023 | 117890.0742 | 100000 | 85000 | 1536687.4766 | 384171.8691 | 1920859.3457 | SANTA CLARA | 0.32 | 491739.9925 | 2412599.3382 | 2525991.5071
CA0707608 | MARINA MOBILE MANOR | 75 | 24 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | CONTRA COSTA | 0.3 | 461600.5383 | 2384936.1145 | 2497028.1118
CA5400718 | WILLIAMS MUTUAL WATER CO | 180 | 50 | 1 | 1 | 27000 | 42.1875 | 1200000 | 42.1875 | 38385.6094 | 122216.2969 | 100000 | 85000 | 1545601.9062 | 386400.4766 | 1932002.3828 | TULARE | 0 | 0 | 1932002.3828 | 2022806.4948
CA0707523 | FLAMINGO MOBILE MANOR | 200 | 62 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | CONTRA COSTA | 0.3 | 464076.7687 | 2397729.9719 | 2510423.2806
CA2701820 | CORDA RD WS | 60 | 19 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | MONTEREY | 0.3 | 461303.3906 | 2383400.8516 | 2495420.6916
CA5400602 | EAGLE'S NEST RESORT | 279 | 78 | 1 | 1 | 41850 | 65.3906 | 1200000 | 65.3906 | 41750.2945 | 125388.8602 | 100000 | 85000 | 1552139.1547 | 388034.7887 | 1940173.9434 | TULARE | 0 | 0 | 1940173.9434 | 2031362.1187
CA4200814 | JONATA HOMEOWNERS ASSOCIATION | 45 | 16 | 1 | 1 | 6750 | 10.5469 | 1200000 | 10.5469 | 33797.4023 | 117890.0742 | 100000 | 85000 | 1536687.4766 | 384171.8691 | 1920859.3457 | SANTA BARBARA | 0.3 | 461006.243 | 2381865.5887 | 2493813.2713
CA2701687 | VALLEY OAKS MHP WS | 120 | 46 | 1 | 1 | 18000 | 28.125 | 1200000 | 28.125 | 36346.4062 | 120293.5312 | 100000 | 85000 | 1541639.9375 | 385409.9844 | 1927049.9219 | MONTEREY | 0.3 | 462491.9813 | 2389541.9031 | 2501850.3726
CA1000186 | HELM SCHOOL | 146 | 11 | 1 | 1 | 21900 | 34.2188 | 1200000 | 34.2188 | 37230.0609 | 121126.7297 | 100000 | 85000 | 1543356.7906 | 385839.1977 | 1929195.9883 | FRESNO | 0 | 0 | 1929195.9883 | 2019868.1997
CA0202501 | DIAMOND VALLEY SCHOOL | 100 | 5 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | ALPINE | 0 | 0 | 1925399.1016 | 2015892.8593
CA0400062 | RICHVALE ELEMENTARY SCHOOL | 63 | 4 | 1 | 1 | 9450 | 14.7656 | 1200000 | 14.7656 | 34409.1633 | 118466.9039 | 100000 | 85000 | 1537876.0672 | 384469.0168 | 1922345.084 | BUTTE | 0 | 0 | 1922345.084 | 2012695.3029
CA0400063 | MANZANITA ELEMENTARY SCHOOL | 295 | 3 | 1 | 1 | 44250 | 69.1406 | 1200000 | 69.1406 | 42294.082 | 125901.5977 | 100000 | 85000 | 1553195.6797 | 388298.9199 | 1941494.5996 | BUTTE | 0 | 0 | 1941494.5996 | 2032744.8458
CA0400064 | CONCOW ELEMENTARY SCHOOL | 115 | 11 | 1 | 1 | 17250 | 26.9531 | 1200000 | 26.9531 | 36176.4727 | 120133.3008 | 100000 | 85000 | 1541309.7734 | 385327.4434 | 1926637.2168 | BUTTE | 0 | 0 | 1926637.2168 | 2017189.166
CA0400065 | SPRING VALLEY SCHOOL | 70 | 1 | 1 | 1 | 10500 | 16.4062 | 1200000 | 16.4062 | 34647.0703 | 118691.2266 | 100000 | 85000 | 1538338.2969 | 384584.5742 | 1922922.8711 | BUTTE | 0 | 0 | 1922922.8711 | 2013300.246
CA0400067 | FEATHER RIVER SCHOOL | 25 | 2 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | BUTTE | 0 | 0 | 1919208.5254 | 2009411.3261
CA0400068 | BERRY CREEK SCHOOL | 95 | 6 | 1 | 1 | 14250 | 22.2656 | 1200000 | 22.2656 | 35496.7383 | 119492.3789 | 100000 | 85000 | 1539989.1172 | 384997.2793 | 1924986.3965 | BUTTE | 0 | 0 | 1924986.3965 | 2015460.7571
CA0400073 | NORD COUNTRY SCHOOL | 66 | 5 | 1 | 1 | 9900 | 15.4688 | 1200000 | 15.4688 | 34511.1234 | 118563.0422 | 100000 | 85000 | 1538074.1656 | 384518.5414 | 1922592.707 | BUTTE | 0 | 0 | 1922592.707 | 2012954.5643
CA0400079 | FOREST RANCH CHARTER SCHOOL | 146 | 4 | 1 | 1 | 21900 | 34.2188 | 1200000 | 34.2188 | 37230.0609 | 121126.7297 | 100000 | 85000 | 1543356.7906 | 385839.1977 | 1929195.9883 | BUTTE | 0 | 0 | 1929195.9883 | 2019868.1997
CA0706028 | KNIGHTSEN ELEMENTARY SCHOOL | 350 | 4 | 1 | 1 | 52500 | 82.0312 | 1200000 | 82.0312 | 44163.3516 | 127664.1328 | 100000 | 85000 | 1556827.4844 | 389206.8711 | 1946034.3555 | CONTRA COSTA | 0.3 | 467048.2453 | 2413082.6008 | 2526497.483
CA0706029 | EXCELSIOR MIDDLE SCHOOL | 600 | 2 | 1 | 1 | 90000 | 140.625 | 1200000 | 140.625 | 52660.0312 | 135675.6562 | 100000 | 85000 | 1573335.6875 | 393333.9219 | 1966669.6094 | CONTRA COSTA | 0.3 | 472000.7062 | 2438670.3156 | 2553287.8205
CA0707620 | CANYON SCHOOL | 200 | 1 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | CONTRA COSTA | 0.3 | 464076.7687 | 2397729.9719 | 2510423.2806
CA0800647 | REDWOOD MAINT. & OPER. | 421 | 1 | 1 | 1 | 63150 | 98.6719 | 1200000 | 98.6719 | 46576.4086 | 129939.4055 | 100000 | 85000 | 1561515.8141 | 390378.9535 | 1951894.7676 | DEL NORTE | 0 | 0 | 1951894.7676 | 2043633.8217
CA0800649 | MARGARET KEATING MAIN. & OPER. | 135 | 1 | 1 | 1 | 20250 | 31.6406 | 1200000 | 31.6406 | 36856.207 | 120774.2227 | 100000 | 85000 | 1542630.4297 | 385657.6074 | 1928288.0371 | DEL NORTE | 0 | 0 | 1928288.0371 | 2018917.5749
CA0900304 | SILVERFORK SCHOOL | 25 | 2 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | EL DORADO | 0.3 | 460610.0461 | 2379818.5715 | 2491670.0443
CA0900410 | LATROBE ELEMENTARY SCHOOL | 65 | 5 | 1 | 1 | 9750 | 15.2344 | 1200000 | 15.2344 | 34477.1367 | 118530.9961 | 100000 | 85000 | 1538008.1328 | 384502.0332 | 1922510.166 | EL DORADO | 0.3 | 461402.4398 | 2383912.6059 | 2495956.4983
CA1000104 | CENTERVILLE SCHOOL | 375 | 11 | 1 | 1 | 56250 | 87.8906 | 1200000 | 87.8906 | 45013.0195 | 128465.2852 | 100000 | 85000 | 1558478.3047 | 389619.5762 | 1948097.8809 | FRESNO | 0 | 0 | 1948097.8809 | 2039658.4813
CA1000111 | PINE RIDGE SCHOOL | 100 | 13 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | FRESNO | 0 | 0 | 1925399.1016 | 2015892.8593
CA1000180 | ALTA ELEMENTARY SCHOOL | 384 | 1 | 1 | 1 | 57600 | 90 | 1200000 | 90 | 45318.9 | 128753.7 | 100000 | 85000 | 1559072.6 | 389768.15 | 1948840.75 | FRESNO | 0 | 0 | 1948840.75 | 2040436.2652
CA1000181 | ALVINA SCHOOL | 240 | 8 | 1 | 1 | 36000 | 56.25 | 1200000 | 56.25 | 40424.8125 | 124139.0625 | 100000 | 85000 | 1549563.875 | 387390.9688 | 1936954.8438 | FRESNO | 0 | 0 | 1936954.8438 | 2027991.7214
CA1000182 | BURREL UNION ELEMENTARY SCHOOL | 178 | 2 | 1 | 1 | 26700 | 41.7188 | 1200000 | 41.7188 | 38317.6359 | 122152.2047 | 100000 | 85000 | 1545469.8406 | 386367.4602 | 1931837.3008 | FRESNO | 0 | 0 | 1931837.3008 | 2022633.6539
CA1000184 | DUNLAP K-8 SCHOOL | 408 | 1 | 1 | 1 | 61200 | 95.625 | 1200000 | 95.625 | 46134.5813 | 129522.8062 | 100000 | 85000 | 1560657.3875 | 390164.3469 | 1950821.7344 | FRESNO | 0 | 0 | 1950821.7344 | 2042510.3559
CA1000185 | GREAT WESTERN ELEMENTARY SCHOOL | 411 | 1 | 1 | 1 | 61650 | 96.3281 | 1200000 | 96.3281 | 46236.5414 | 129618.9445 | 100000 | 85000 | 1560855.4859 | 390213.8715 | 1951069.3574 | FRESNO | 0 | 0 | 1951069.3574 | 2042769.6172
CA1000187 | INDIANOLA SCHOOL | 511 | 10 | 1 | 1 | 76650 | 119.7656 | 1200000 | 119.7656 | 49635.2133 | 132823.5539 | 100000 | 85000 | 1567458.7672 | 391864.6918 | 1959323.459 | FRESNO | 0 | 0 | 1959323.459 | 2051411.6616
CA1000190 | LONE STAR SCHOOL | 436 | 6 | 1 | 1 | 65400 | 102.1875 | 1200000 | 102.1875 | 47086.2094 | 130420.0969 | 100000 | 85000 | 1562506.3062 | 390626.5766 | 1953132.8828 | FRESNO | 0 | 0 | 1953132.8828 | 2044930.1283
CA1000192 | MONROE SCHOOL | 200 | 3 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | FRESNO | 0 | 0 | 1933653.2031 | 2024534.9037
CA1000193 | NAVELENCIA SCHOOL | 330 | 1 | 1 | 1 | 49500 | 77.3438 | 1200000 | 77.3438 | 43483.6172 | 127023.2109 | 100000 | 85000 | 1555506.8281 | 388876.707 | 1944383.5352 | FRESNO | 0 | 0 | 1944383.5352 | 2035769.5613
CA1000194 | PACIFIC UNION ELEMENTARY SCHOOL | 490 | 1 | 1 | 1 | 73500 | 114.8438 | 1200000 | 114.8438 | 48921.4922 | 132150.5859 | 100000 | 85000 | 1566072.0781 | 391518.0195 | 1957590.0977 | FRESNO | 0 | 0 | 1957590.0977 | 2049596.8322
CA1000196 | RIVERVIEW SCHOOL | 469 | 1 | 1 | 1 | 70350 | 109.9219 | 1200000 | 109.9219 | 48207.7711 | 131477.618 | 100000 | 85000 | 1564685.3891 | 391171.3473 | 1955856.7363 | FRESNO | 0 | 0 | 1955856.7363 | 2047782.0029
CA1000198 | TERRY SCHOOL | 236 | 25 | 1 | 1 | 35400 | 55.3125 | 1200000 | 55.3125 | 40288.8656 | 124010.8781 | 100000 | 85000 | 1549299.7437 | 387324.9359 | 1936624.6797 | FRESNO | 0 | 0 | 1936624.6797 | 2027646.0396
CA1000201 | SUN EMPIRE SCHOOL | 780 | 10 | 1 | 1 | 117000 | 182.8125 | 1200000 | 182.8125 | 58777.6406 | 141443.9531 | 100000 | 85000 | 1585221.5938 | 396305.3984 | 1981526.9922 | FRESNO | 0 | 0 | 1981526.9922 | 2074658.7608
CA1000204 | AMERICAN UNION SCHOOL | 250 | 33 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | FRESNO | 0 | 0 | 1937780.2539 | 2028855.9258
CA1000206 | HOUGHTON-KEARNEY SCHOOL | 310 | 4 | 1 | 1 | 46500 | 72.6562 | 1200000 | 72.6562 | 42803.8828 | 126382.2891 | 100000 | 85000 | 1554186.1719 | 388546.543 | 1942732.7148 | FRESNO | 0 | 0 | 1942732.7148 | 2034041.1524
CA1000208 | ROOSEVELT ELEMENTARY SCHOOL | 370 | 12 | 1 | 1 | 55500 | 86.7188 | 1200000 | 86.7188 | 44843.0859 | 128305.0547 | 100000 | 85000 | 1558148.1406 | 389537.0352 | 1947685.1758 | FRESNO | 0 | 0 | 1947685.1758 | 2039226.379
CA1000217 | CENTRAL HIGH SCHOOL WEST | 1127 | 10 | 1 | 1 | 169050 | 264.1406 | 1200000 | 264.1406 | 70571.032 | 152563.9477 | 100000 | 85000 | 1608134.9797 | 402033.7449 | 2010168.7246 | FRESNO | 0 | 0 | 2010168.7246 | 2104646.6547
CA1000315 | CLAY JOINT ELEMENTARY SCHOOL | 275 | 5 | 1 | 1 | 41250 | 64.4531 | 1200000 | 64.4531 | 41614.3477 | 125260.6758 | 100000 | 85000 | 1551875.0234 | 387968.7559 | 1939843.7793 | FRESNO | 0 | 0 | 1939843.7793 | 2031016.4369
CA1000316 | KINGS CANYON HIGH SCHOOL | 120 | 1 | 1 | 1 | 18000 | 28.125 | 1200000 | 28.125 | 36346.4062 | 120293.5312 | 100000 | 85000 | 1541639.9375 | 385409.9844 | 1927049.9219 | FRESNO | 0 | 0 | 1927049.9219 | 2017621.2682
CA1000577 | DUNLAP LEADERSHIP ACADEMY | 78 | 1 | 1 | 1 | 11700 | 18.2812 | 1200000 | 18.2812 | 34918.9641 | 118947.5953 | 100000 | 85000 | 1538866.5594 | 384716.6398 | 1923583.1992 | FRESNO | 0 | 0 | 1923583.1992 | 2013991.6096
CA1100104 | WILLOW CREEK CHRISTIAN SCHOOL | 47 | 2 | 1 | 1 | 7050 | 11.0156 | 1200000 | 11.0156 | 33865.3758 | 117954.1664 | 100000 | 85000 | 1536819.5422 | 384204.8855 | 1921024.4277 | GLENN | 0 | 0 | 1921024.4277 | 2011312.5758
CA1100440 | LAKE ELEMENTARY SCHOOL | 205 | 1 | 1 | 1 | 30750 | 48.0469 | 1200000 | 48.0469 | 39235.2773 | 123017.4492 | 100000 | 85000 | 1547252.7266 | 386813.1816 | 1934065.9082 | GLENN | 0 | 0 | 1934065.9082 | 2024967.0059
CA1100448 | PLAZA ELEMENTARY SCHOOL | 250 | 4 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | GLENN | 0 | 0 | 1937780.2539 | 2028855.9258
CA1100527 | CAPAY JOINT UNION ELEM. SCHOOL | 230 | 1 | 1 | 1 | 34500 | 53.9062 | 1200000 | 53.9062 | 40084.9453 | 123818.6016 | 100000 | 85000 | 1548903.5469 | 387225.8867 | 1936129.4336 | GLENN | 0 | 0 | 1936129.4336 | 2027127.517
CA1100749 | RIVER VALLEY CHRISTIAN SCHOOL | 80 | 2 | 1 | 1 | 12000 | 18.75 | 1200000 | 18.75 | 34986.9375 | 119011.6875 | 100000 | 85000 | 1538998.625 | 384749.6562 | 1923748.2812 | GLENN | 0 | 0 | 1923748.2812 | 2014164.4505
CA1200546 | CASTERLIN SCHOOL | 130 | 1 | 1 | 1 | 19500 | 30.4688 | 1200000 | 30.4688 | 36686.2734 | 120613.9922 | 100000 | 85000 | 1542300.2656 | 385575.0664 | 1927875.332 | HUMBOLDT | 0 | 0 | 1927875.332 | 2018485.4726
CA1200681 | CUDDEBACK GRAMMAR SCHOOL | 165 | 1 | 1 | 1 | 24750 | 38.6719 | 1200000 | 38.6719 | 37875.8086 | 121735.6055 | 100000 | 85000 | 1544611.4141 | 386152.8535 | 1930764.2676 | HUMBOLDT | 0 | 0 | 1930764.2676 | 2021510.1882
CA1200778 | BRIDGEVILLE ELEM. SCHOOL | 50 | 1 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | HUMBOLDT | 0 | 0 | 1921272.0508 | 2011571.8372
CA1200817 | KNEELAND SCHOOL | 32 | 1 | 1 | 1 | 4800 | 7.5 | 1200000 | 7.5 | 33355.575 | 117473.475 | 100000 | 85000 | 1535829.05 | 383957.2625 | 1919786.3125 | HUMBOLDT | 0 | 0 | 1919786.3125 | 2010016.2692
CA1400019 | ROUND VALLEY SCHOOL | 143 | 2 | 1 | 1 | 21450 | 33.5156 | 1200000 | 33.5156 | 37128.1008 | 121030.5914 | 100000 | 85000 | 1543158.6922 | 385789.673 | 1928948.3652 | INYO | 0 | 0 | 1928948.3652 | 2019608.9384
CA1502068 | DI GIORGIO SCHOOL WATER SYSTEM | 232 | 1 | 1 | 1 | 34800 | 54.375 | 1200000 | 54.375 | 40152.9187 | 123882.6938 | 100000 | 85000 | 1549035.6125 | 387258.9031 | 1936294.5156 | KERN | 0 | 0 | 1936294.5156 | 2027300.3579
CA1502074 | EL TEJON MIDDLE SCHOOL | 550 | 1 | 1 | 1 | 82500 | 128.9062 | 1200000 | 128.9062 | 50960.6953 | 134073.3516 | 100000 | 85000 | 1570034.0469 | 392508.5117 | 1962542.5586 | KERN | 0 | 0 | 1962542.5586 | 2054782.0588
CA1502154 | LAKESIDE SCHOOL | 800 | 1 | 1 | 1 | 120000 | 187.5 | 1200000 | 187.5 | 59457.375 | 142084.875 | 100000 | 85000 | 1586542.25 | 396635.5625 | 1983177.8125 | KERN | 0 | 0 | 1983177.8125 | 2076387.1697
CA1502221 | POND SCHOOL WATER SYSTEM | 250 | 2 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | KERN | 0 | 0 | 1937780.2539 | 2028855.9258
CA1502229 | RIO BRAVO GREELEY SCHOOL WATER SYSTEM | 887 | 16 | 1 | 1 | 133050 | 207.8906 | 1200000 | 207.8906 | 62414.2195 | 144872.8852 | 100000 | 85000 | 1592287.1047 | 398071.7762 | 1990358.8809 | KERN | 0 | 0 | 1990358.8809 | 2083905.7483
CA1502260 | SOUTH FORK ELEMENTARY SCHOOL WATER SYS | 154 | 2 | 1 | 1 | 23100 | 36.0938 | 1200000 | 36.0938 | 37501.9547 | 121383.0984 | 100000 | 85000 | 1543885.0531 | 385971.2633 | 1929856.3164 | KERN | 0 | 0 | 1929856.3164 | 2020559.5633
CA1502607 | PIUTE MOUNTAIN SCHOOL WATER | 50 | 5 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | KERN | 0 | 0 | 1921272.0508 | 2011571.8372
CA1503140 | FRAZIER MOUNTAIN HIGH SCHOOL | 500 | 1 | 1 | 1 | 75000 | 117.1875 | 1200000 | 117.1875 | 49261.3594 | 132471.0469 | 100000 | 85000 | 1566732.4062 | 391683.1016 | 1958415.5078 | KERN | 0 | 0 | 1958415.5078 | 2050461.0367
CA1503368 | SOUTH FORK MIDDLE SCHOOL | 204 | 1 | 1 | 1 | 30600 | 47.8125 | 1200000 | 47.8125 | 39201.2906 | 122985.4031 | 100000 | 85000 | 1547186.6938 | 386796.6734 | 1933983.3672 | KERN | 0 | 0 | 1933983.3672 | 2024880.5854
CA1600009 | HANFORD CHRISTIAN SCHOOL | 175 | 14 | 1 | 1 | 26250 | 41.0156 | 1200000 | 41.0156 | 38215.6758 | 122056.0664 | 100000 | 85000 | 1545271.7422 | 386317.9355 | 1931589.6777 | KINGS | 0 | 0 | 1931589.6777 | 2022374.3926
CA1600013 | LAKESIDE ELEMENTARY SCHOOL | 388 | 5 | 1 | 1 | 58200 | 90.9375 | 1200000 | 90.9375 | 45454.8469 | 128881.8844 | 100000 | 85000 | 1559336.7312 | 389834.1828 | 1949170.9141 | KINGS | 0 | 0 | 1949170.9141 | 2040781.947
CA1600015 | KINGS RIVER HARDWICK SCHOOL | 908 | 7 | 1 | 1 | 136200 | 212.8125 | 1200000 | 212.8125 | 63127.9406 | 145545.8531 | 100000 | 85000 | 1593673.7937 | 398418.4484 | 1992092.2422 | KINGS | 0 | 0 | 1992092.2422 | 2085720.5776
CA1600017 | ISLAND UNION SCHOOL | 416 | 17 | 1 | 1 | 62400 | 97.5 | 1200000 | 97.5 | 46406.475 | 129779.175 | 100000 | 85000 | 1561185.65 | 390296.4125 | 1951482.0625 | KINGS | 0 | 0 | 1951482.0625 | 2043201.7194
CA1800573 | RICHMOND ELEMENTARY SCHOOL | 247 | 1 | 1 | 1 | 37050 | 57.8906 | 1200000 | 57.8906 | 40662.7195 | 124363.3852 | 100000 | 85000 | 1550026.1047 | 387506.5262 | 1937532.6309 | LASSEN | 0 | 0 | 1937532.6309 | 2028596.6645
CA1800575 | SHAFFER ELEMENTARY SCHOOL | 320 | 1 | 1 | 1 | 48000 | 75 | 1200000 | 75 | 43143.75 | 126702.75 | 100000 | 85000 | 1554846.5 | 388711.625 | 1943558.125 | LASSEN | 0 | 0 | 1943558.125 | 2034905.3569
CA1800576 | LONG VALLEY CHARTER SCHOOL | 150 | 1 | 1 | 1 | 22500 | 35.1562 | 1200000 | 35.1562 | 37366.0078 | 121254.9141 | 100000 | 85000 | 1543620.9219 | 385905.2305 | 1929526.1523 | LASSEN | 0 | 0 | 1929526.1523 | 2020213.8815
CA1800577 | JANESVILLE ELEMENTARY SCHOOL | 425 | 1 | 1 | 1 | 63750 | 99.6094 | 1200000 | 99.6094 | 46712.3555 | 130067.5898 | 100000 | 85000 | 1561779.9453 | 390444.9863 | 1952224.9316 | LASSEN | 0 | 0 | 1952224.9316 | 2043979.5034
CA1900707 | ILEAD AGUA DULCE CHARTER SCHOOL | 450 | 6 | 1 | 1 | 67500 | 105.4688 | 1200000 | 105.4688 | 47562.0234 | 130868.7422 | 100000 | 85000 | 1563430.7656 | 390857.6914 | 1954288.457 | LOS ANGELES | 0.32 | 500297.845 | 2454586.302 | 2569951.8582
CA1900750 | DEL SUR SCHOOL/WESTSIDE UNION DISTRICT | 825 | 1 | 1 | 1 | 123750 | 193.3594 | 1200000 | 193.3594 | 60307.043 | 142886.0273 | 100000 | 85000 | 1588193.0703 | 397048.2676 | 1985241.3379 | LOS ANGELES | 0.32 | 508221.7825 | 2493463.1204 | 2610655.887
CA1900751 | EASTSIDE UNION SCHOOL DISTRICT | 650 | 18 | 1 | 1 | 97500 | 152.3438 | 1200000 | 152.3438 | 54359.3672 | 137277.9609 | 100000 | 85000 | 1576637.3281 | 394159.332 | 1970796.6602 | LOS ANGELES | 0.32 | 504523.945 | 2475320.6052 | 2591660.6736
CA2000597 | DAIRYLAND SCHOOL | 250 | 8 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | MADERA | 0 | 0 | 1937780.2539 | 2028855.9258
CA2000600 | HOWARD ELEMENTARY SCHOOL | 1081 | 7 | 1 | 1 | 162150 | 253.3594 | 1200000 | 253.3594 | 69007.643 | 151089.8273 | 100000 | 85000 | 1605097.4703 | 401274.3676 | 2006371.8379 | MADERA | 0 | 0 | 2006371.8379 | 2100671.3143
CA2000601 | LA VINA SCHOOL | 513 | 7 | 1 | 1 | 76950 | 120.2344 | 1200000 | 120.2344 | 49703.1867 | 132887.6461 | 100000 | 85000 | 1567590.8328 | 391897.7082 | 1959488.541 | MADERA | 0 | 0 | 1959488.541 | 2051584.5024
CA2000602 | RIPPERDAN COMMUNITY DAY SCHOOL | 113 | 4 | 1 | 1 | 16950 | 26.4844 | 1200000 | 26.4844 | 36108.4992 | 120069.2086 | 100000 | 85000 | 1541177.7078 | 385294.427 | 1926472.1348 | MADERA | 0 | 0 | 1926472.1348 | 2017016.3251
CA2000607 | SPRING VALLEY SCHOOL | 150 | 10 | 1 | 1 | 22500 | 35.1562 | 1200000 | 35.1562 | 37366.0078 | 121254.9141 | 100000 | 85000 | 1543620.9219 | 385905.2305 | 1929526.1523 | MADERA | 0 | 0 | 1929526.1523 | 2020213.8815
CA2000612 | NORTH FORK ELEMENTARY SCHOOL | 500 | 18 | 1 | 1 | 75000 | 117.1875 | 1200000 | 117.1875 | 49261.3594 | 132471.0469 | 100000 | 85000 | 1566732.4062 | 391683.1016 | 1958415.5078 | MADERA | 0 | 0 | 1958415.5078 | 2050461.0367
CA2000616 | WASUMA SCHOOL | 354 | 5 | 1 | 1 | 53100 | 82.9688 | 1200000 | 82.9688 | 44299.2984 | 127792.3172 | 100000 | 85000 | 1557091.6156 | 389272.9039 | 1946364.5195 | MADERA | 0 | 0 | 1946364.5195 | 2037843.6519
CA2000760 | DIXIELAND ELEMENTARY SCHOOL | 338 | 4 | 1 | 1 | 50700 | 79.2188 | 1200000 | 79.2188 | 43755.5109 | 127279.5797 | 100000 | 85000 | 1556035.0906 | 389008.7727 | 1945043.8633 | MADERA | 0 | 0 | 1945043.8633 | 2036460.9249
CA2000844 | RIVERGOLD ELEMENTARY SCHOOL | 485 | 9 | 1 | 1 | 72750 | 113.6719 | 1200000 | 113.6719 | 48751.5586 | 131990.3555 | 100000 | 85000 | 1565741.9141 | 391435.4785 | 1957177.3926 | MADERA | 0 | 0 | 1957177.3926 | 2049164.73
CA2000846 | SIERRA VIEW SCHOOL | 250 | 23 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | MADERA | 0 | 0 | 1937780.2539 | 2028855.9258
CA2100582 | NICASIO SCHOOL | 40 | 5 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | MARIN | 0.3 | 460907.1937 | 2381353.8344 | 2493277.4646
CA2210908 | MUSD -COULTERVILLE - GREELEY HILL SCHOOL | 91 | 6 | 1 | 1 | 13650 | 21.3281 | 1200000 | 21.3281 | 35360.7914 | 119364.1945 | 100000 | 85000 | 1539724.9859 | 384931.2465 | 1924656.2324 | MARIPOSA | 0 | 0 | 1924656.2324 | 2015115.0753
CA2300755 | POTTER VALLEY SCHOOL DISTRICT | 309 | 36 | 1 | 1 | 46350 | 72.4219 | 1200000 | 72.4219 | 42769.8961 | 126350.243 | 100000 | 85000 | 1554120.1391 | 388530.0348 | 1942650.1738 | MENDOCINO | 0 | 0 | 1942650.1738 | 2033954.732
CA2300770 | ANDERSON VALLEY ELEMENTARY SCHOOL | 350 | 11 | 1 | 1 | 52500 | 82.0312 | 1200000 | 82.0312 | 44163.3516 | 127664.1328 | 100000 | 85000 | 1556827.4844 | 389206.8711 | 1946034.3555 | MENDOCINO | 0 | 0 | 1946034.3555 | 2037497.9702
CA2300826 | MANCHESTER UNION ELEMENTARY SCHOOL | 75 | 1 | 1 | 1 | 11250 | 17.5781 | 1200000 | 17.5781 | 34817.0039 | 118851.457 | 100000 | 85000 | 1538668.4609 | 384667.1152 | 1923335.5762 | MENDOCINO | 0 | 0 | 1923335.5762 | 2013732.3483
CA2300829 | ROUND VALLEY HIGH SCHOOL | 162 | 1 | 1 | 1 | 24300 | 37.9688 | 1200000 | 37.9688 | 37773.8484 | 121639.4672 | 100000 | 85000 | 1544413.3156 | 386103.3289 | 1930516.6445 | MENDOCINO | 0 | 0 | 1930516.6445 | 2021250.9268
CA2300830 | ROUND VALLEY ELEMENTARY SCHOOL | 263 | 1 | 1 | 1 | 39450 | 61.6406 | 1200000 | 61.6406 | 41206.507 | 124876.1227 | 100000 | 85000 | 1551082.6297 | 387770.6574 | 1938853.2871 | MENDOCINO | 0 | 0 | 1938853.2871 | 2029979.3916
CA2300846 | MENDOCINO SCHOOL DISTRICT-ALBION SCHOOL | 25 | 2 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | MENDOCINO | 0 | 0 | 1919208.5254 | 2009411.3261
CA2300863 | EEL RIVER CHARTER SCHOOL | 73 | 1 | 1 | 1 | 10950 | 17.1094 | 1200000 | 17.1094 | 34749.0305 | 118787.3648 | 100000 | 85000 | 1538536.3953 | 384634.0988 | 1923170.4941 | MENDOCINO | 0 | 0 | 1923170.4941 | 2013559.5074
CA2300874 | MONTESSORI DEL MAR LEARNING CENTER | 50 | 3 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | MENDOCINO | 0 | 0 | 1921272.0508 | 2011571.8372
CA2400062 | SNELLING MERCED FALLS SCHOOL | 85 | 4 | 1 | 1 | 12750 | 19.9219 | 1200000 | 19.9219 | 35156.8711 | 119171.918 | 100000 | 85000 | 1539328.7891 | 384832.1973 | 1924160.9863 | MERCED | 0 | 0 | 1924160.9863 | 2014596.5527
CA2400064 | MERQUIN ELEMENTARY SCHOOL | 284 | 2 | 1 | 1 | 42600 | 66.5625 | 1200000 | 66.5625 | 41920.2281 | 125549.0906 | 100000 | 85000 | 1552469.3188 | 388117.3297 | 1940586.6484 | MERCED | 0 | 0 | 1940586.6484 | 2031794.2209
CA2400066 | PLANADA ELEMENTARYSCHOOL | 567 | 1 | 1 | 1 | 85050 | 132.8906 | 1200000 | 132.8906 | 51538.4695 | 134618.1352 | 100000 | 85000 | 1571156.6047 | 392789.1512 | 1963945.7559 | MERCED | 0 | 0 | 1963945.7559 | 2056251.2064
CA2400071 | WASHINGTON SCHOOL | 230 | 4 | 1 | 1 | 34500 | 53.9062 | 1200000 | 53.9062 | 40084.9453 | 123818.6016 | 100000 | 85000 | 1548903.5469 | 387225.8867 | 1936129.4336 | MERCED | 0 | 0 | 1936129.4336 | 2027127.517
CA2400075 | EL NIDO ELEMENTARY SCHOOL | 219 | 2 | 1 | 1 | 32850 | 51.3281 | 1200000 | 51.3281 | 39711.0914 | 123466.0945 | 100000 | 85000 | 1548177.1859 | 387044.2965 | 1935221.4824 | MERCED | 0 | 0 | 1935221.4824 | 2026176.8921
CA2400091 | CHARLESTON SCHOOL | 325 | 1 | 1 | 1 | 48750 | 76.1719 | 1200000 | 76.1719 | 43313.6836 | 126862.9805 | 100000 | 85000 | 1555176.6641 | 388794.166 | 1943970.8301 | MERCED | 0 | 0 | 1943970.8301 | 2035337.4591
CA2400097 | CRESSEY SCHOOL | 155 | 7 | 1 | 1 | 23250 | 36.3281 | 1200000 | 36.3281 | 37535.9414 | 121415.1445 | 100000 | 85000 | 1543951.0859 | 385987.7715 | 1929938.8574 | MERCED | 0 | 0 | 1929938.8574 | 2020645.9837
CA2400099 | GRACE MENNONITE SCHOOL | 100 | 1 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | MERCED | 0 | 0 | 1925399.1016 | 2015892.8593
CA2400122 | LONGVIEW MENNONITE SCHOOL | 120 | 1 | 1 | 1 | 18000 | 28.125 | 1200000 | 28.125 | 36346.4062 | 120293.5312 | 100000 | 85000 | 1541639.9375 | 385409.9844 | 1927049.9219 | MERCED | 0 | 0 | 1927049.9219 | 2017621.2682
CA2400134 | BUHACH PRESCHOOL (KINDERCARE) | 110 | 3 | 1 | 1 | 16500 | 25.7812 | 1200000 | 25.7812 | 36006.5391 | 119973.0703 | 100000 | 85000 | 1540979.6094 | 385244.9023 | 1926224.5117 | MERCED | 0 | 0 | 1926224.5117 | 2016757.0638
CA2400219 | MERCED NEW LIFE SCHOOL | 36 | 2 | 1 | 1 | 5400 | 8.4375 | 1200000 | 8.4375 | 33491.5219 | 117601.6594 | 100000 | 85000 | 1536093.1812 | 384023.2953 | 1920116.4766 | MERCED | 0 | 0 | 1920116.4766 | 2010361.951
CA2600568 | EDNA BEAMAN ELEMENTARY SCHOOL | 26 | 2 | 1 | 1 | 3900 | 6.0938 | 1200000 | 6.0938 | 33151.6547 | 117281.1984 | 100000 | 85000 | 1535432.8531 | 383858.2133 | 1919291.0664 | MONO | 0 | 0 | 1919291.0664 | 2009497.7465
CA2700552 | ECHO VALLEY SCHOOL WS | 579 | 1 | 1 | 1 | 86850 | 135.7031 | 1200000 | 135.7031 | 51946.3102 | 135002.6883 | 100000 | 85000 | 1571948.9984 | 392987.2496 | 1964936.248 | MONTEREY | 0.3 | 471584.6995 | 2436520.9476 | 2551037.4321
CA2700577 | ELKHORN SCHOOL WS | 694 | 1 | 1 | 1 | 104100 | 162.6562 | 1200000 | 162.6562 | 55854.7828 | 138687.9891 | 100000 | 85000 | 1579542.7719 | 394885.693 | 1974428.4648 | MONTEREY | 0.3 | 473862.8316 | 2448291.2964 | 2563360.9873
CA2700705 | PRUNEDALE SCHOOL WS | 655 | 1 | 1 | 1 | 98250 | 153.5156 | 1200000 | 153.5156 | 54529.3008 | 137438.1914 | 100000 | 85000 | 1576967.4922 | 394241.873 | 1971209.3652 | MONTEREY | 0.3 | 473090.2477 | 2444299.6129 | 2559181.6947
CA2700727 | SAN ANTONIO SCHOOL DISTRICT WS | 300 | 1 | 1 | 1 | 45000 | 70.3125 | 1200000 | 70.3125 | 42464.0156 | 126061.8281 | 100000 | 85000 | 1553525.8438 | 388381.4609 | 1941907.3047 | MONTEREY | 0.3 | 466057.7531 | 2407965.0578 | 2521139.4155
CA2700964 | BRADLEY UNION SCHOOL WS | 100 | 1 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | MONTEREY | 0.3 | 462095.7844 | 2387494.8859 | 2499707.1456
CA2701221 | WASHINGTON SCHOOL WS | 250 | 2 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | MONTEREY | 0.3 | 465067.2609 | 2402847.5148 | 2515781.348
CA2702180 | GRAVES SCHOOL WS | 56 | 2 | 1 | 1 | 8400 | 13.125 | 1200000 | 13.125 | 34171.2562 | 118242.5813 | 100000 | 85000 | 1537413.8375 | 384353.4594 | 1921767.2969 | MONTEREY | 0.3 | 461224.1512 | 2382991.4481 | 2494992.0462
CA2702254 | PACIFIC VALLEY SCHOOL WS | 25 | 5 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | MONTEREY | 0.3 | 460610.0461 | 2379818.5715 | 2491670.0443
CA2702317 | MISSION SCHOOL WS | 100 | 1 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | MONTEREY | 0.3 | 462095.7844 | 2387494.8859 | 2499707.1456
CA2702322 | CAPTAIN COOPER SCHOOL WS | 95 | 1 | 1 | 1 | 14250 | 22.2656 | 1200000 | 22.2656 | 35496.7383 | 119492.3789 | 100000 | 85000 | 1539989.1172 | 384997.2793 | 1924986.3965 | MONTEREY | 0.3 | 461996.7352 | 2386983.1316 | 2499171.3388
CA2702490 | CENTRAL BAY HIGH SCHOOL WS | 70 | 1 | 1 | 1 | 10500 | 16.4062 | 1200000 | 16.4062 | 34647.0703 | 118691.2266 | 100000 | 85000 | 1538338.2969 | 384584.5742 | 1922922.8711 | MONTEREY | 0.3 | 461501.4891 | 2384424.3602 | 2496492.3051
CA2800847 | NVUSD: CARNEROS SCHOOL | 100 | 1 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | NAPA | 0.3 | 462095.7844 | 2387494.8859 | 2499707.1456
CA2800848 | NVUSD: MT. GEORGE SCHOOL | 100 | 1 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | NAPA | 0.3 | 462095.7844 | 2387494.8859 | 2499707.1456
CA2900535 | PLEASANT RIDGE SCHOOL | 120 | 4 | 1 | 1 | 18000 | 28.125 | 1200000 | 28.125 | 36346.4062 | 120293.5312 | 100000 | 85000 | 1541639.9375 | 385409.9844 | 1927049.9219 | NEVADA | 0 | 0 | 1927049.9219 | 2017621.2682
CA2900536 | CLEAR CREEK SCHOOL | 160 | 8 | 1 | 1 | 24000 | 37.5 | 1200000 | 37.5 | 37705.875 | 121575.375 | 100000 | 85000 | 1544281.25 | 386070.3125 | 1930351.5625 | NEVADA | 0 | 0 | 1930351.5625 | 2021078.0859
CA2900578 | TWIN RIDGES GRIZZLY HILL SCHOOL | 125 | 11 | 1 | 1 | 18750 | 29.2969 | 1200000 | 29.2969 | 36516.3398 | 120453.7617 | 100000 | 85000 | 1541970.1016 | 385492.5254 | 1927462.627 | NEVADA | 0 | 0 | 1927462.627 | 2018053.3704
CA2900587 | MOUNTAIN VALLEY CHILD AND FAMILY SERVICE | 50 | 10 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | NEVADA | 0 | 0 | 1921272.0508 | 2011571.8372
CA2901208 | DONNER TRAIL ELEMENTARY SCHOOL | 60 | 1 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | NEVADA | 0 | 0 | 1922097.4609 | 2012436.0416
CA3100072 | LIVE OAK WALDORF SCHOOL | 200 | 1 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | PLACER | 0 | 0 | 1933653.2031 | 2024534.9037
CA3100083 | OPHIR ELEMENTARY SCHOOL WATER SYSTEM | 260 | 1 | 1 | 1 | 39000 | 60.9375 | 1200000 | 60.9375 | 41104.5469 | 124779.9844 | 100000 | 85000 | 1550884.5312 | 387721.1328 | 1938605.6641 | PLACER | 0 | 0 | 1938605.6641 | 2029720.1303
CA3107342 | LINCOLN HIGH SCHOOL FARM | 50 | 1 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | PLACER | 0 | 0 | 1921272.0508 | 2011571.8372
CA3200079 | PUSD TAYLORSVILLE ELEMENTARY SCHOOL | 94 | 1 | 1 | 1 | 14100 | 22.0312 | 1200000 | 22.0312 | 35462.7516 | 119460.3328 | 100000 | 85000 | 1539923.0844 | 384980.7711 | 1924903.8555 | PLUMAS | 0 | 0 | 1924903.8555 | 2015374.3367
CA3200215 | SCHRAMEL WATER SYSTEM | 100 | 1 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | PLUMAS | 0 | 0 | 1925399.1016 | 2015892.8593
CA3400248 | FRANKLIN ELEMENTARY SCHOOL | 650 | 13 | 1 | 1 | 97500 | 152.3438 | 1200000 | 152.3438 | 54359.3672 | 137277.9609 | 100000 | 85000 | 1576637.3281 | 394159.332 | 1970796.6602 | SACRAMENTO | 0.32 | 504523.945 | 2475320.6052 | 2591660.6736
CA3400250 | PLEASANT GROVE ELEMENTARY SCHOOL | 185 | 10 | 1 | 1 | 27750 | 43.3594 | 1200000 | 43.3594 | 38555.543 | 122376.5273 | 100000 | 85000 | 1545932.0703 | 386483.0176 | 1932415.0879 | SACRAMENTO | 0.32 | 494698.2625 | 2427113.3504 | 2541187.6779
CA3400251 | SIERRA ENTERPRISE ELEMENTARY SCHOOL | 430 | 13 | 1 | 1 | 64500 | 100.7812 | 1200000 | 100.7812 | 46882.2891 | 130227.8203 | 100000 | 85000 | 1562110.1094 | 390527.5273 | 1952637.6367 | SACRAMENTO | 0.32 | 499875.235 | 2452512.8717 | 2567780.9767
CA3400254 | DILLARD ELEMENTARY SCHOOL | 350 | 4 | 1 | 1 | 52500 | 82.0312 | 1200000 | 82.0312 | 44163.3516 | 127664.1328 | 100000 | 85000 | 1556827.4844 | 389206.8711 | 1946034.3555 | SACRAMENTO | 0.32 | 498184.795 | 2444219.1505 | 2559097.4505
CA3400259 | GRANT HIGH SCHOOL [SWS] | 1400 | 12 | 1 | 1 | 210000 | 328.125 | 1200000 | 328.125 | 79849.4062 | 161312.5312 | 100000 | 85000 | 1626161.9375 | 406540.4844 | 2032702.4219 | SACRAMENTO | 0.32 | 520371.82 | 2553074.2419 | 2673068.7312
CA3400268 | WALNUT GROVE ELEMENTARY SCHOOL | 200 | 2 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | SACRAMENTO | 0.32 | 495015.22 | 2428668.4231 | 2542815.839
CA3400273 | WILTON BIBLE CHURCH | 125 | 5 | 1 | 1 | 18750 | 29.2969 | 1200000 | 29.2969 | 36516.3398 | 120453.7617 | 100000 | 85000 | 1541970.1016 | 385492.5254 | 1927462.627 | SACRAMENTO | 0.32 | 493430.4325 | 2420893.0595 | 2534675.0332
CA3400391 | BRADSHAW CHRISTIAN SCHOOL | 935 | 8 | 1 | 1 | 140250 | 219.1406 | 1200000 | 219.1406 | 64045.582 | 146411.0977 | 100000 | 85000 | 1595456.6797 | 398864.1699 | 1994320.8496 | SACRAMENTO | 0.32 | 510546.1375 | 2504866.9871 | 2622595.7355
CA3500521 | SOUTHSIDE ELEMENTARY SCHOOL | 300 | 2 | 1 | 1 | 45000 | 70.3125 | 1200000 | 70.3125 | 42464.0156 | 126061.8281 | 100000 | 85000 | 1553525.8438 | 388381.4609 | 1941907.3047 | SAN BENITO | 0.3 | 466057.7531 | 2407965.0578 | 2521139.4155
CA3500801 | WILLOW GROVE UNION ELEMENTARY SCHOOL | 25 | 4 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | SAN BENITO | 0.3 | 460610.0461 | 2379818.5715 | 2491670.0443
CA3600432 | LUCERNE VALLEY ELEMENTARY SCHOOL | 441 | 15 | 1 | 1 | 66150 | 103.3594 | 1200000 | 103.3594 | 47256.143 | 130580.3273 | 100000 | 85000 | 1562836.4703 | 390709.1176 | 1953545.5879 | SAN BERNARDINO | 0.3 | 468850.9411 | 2422396.529 | 2536249.1658
CA3600790 | NEWBERRY ELEMENTARY SCHOOL | 255 | 2 | 1 | 1 | 38250 | 59.7656 | 1200000 | 59.7656 | 40934.6133 | 124619.7539 | 100000 | 85000 | 1550554.3672 | 387638.5918 | 1938192.959 | SAN BERNARDINO | 0.3 | 465166.3102 | 2403359.2691 | 2516317.1548
CA3601057 | MOUNTAIN VIEW CONTINUATION SCHOOL | 30 | 4 | 1 | 1 | 4500 | 7.0312 | 1200000 | 7.0312 | 33287.6016 | 117409.3828 | 100000 | 85000 | 1535696.9844 | 383924.2461 | 1919621.2305 | SAN BERNARDINO | 0.3 | 460709.0953 | 2380330.3258 | 2492205.8511
CA3601095 | LUCERNE VALLEY HIGH SCHOOL | 329 | 11 | 1 | 1 | 49350 | 77.1094 | 1200000 | 77.1094 | 43449.6305 | 126991.1648 | 100000 | 85000 | 1555440.7953 | 388860.1988 | 1944300.9941 | SAN BERNARDINO | 0.3 | 466632.2386 | 2410933.2327 | 2524247.0947
CA3700118 | CAMP LOCKETT MIDDLE SCHOOL | 150 | 4 | 1 | 1 | 22500 | 35.1562 | 1200000 | 35.1562 | 37366.0078 | 121254.9141 | 100000 | 85000 | 1543620.9219 | 385905.2305 | 1929526.1523 | SAN DIEGO | 0.32 | 493958.695 | 2423484.8473 | 2537388.6352
CA3700963 | POTRERO ELEMENTARY SCHOOL | 300 | 19 | 1 | 1 | 45000 | 70.3125 | 1200000 | 70.3125 | 42464.0156 | 126061.8281 | 100000 | 85000 | 1553525.8438 | 388381.4609 | 1941907.3047 | SAN DIEGO | 0.32 | 497128.27 | 2439035.5747 | 2553670.2467
CA3701005 | SPENCER VALLEY SCHOOL DISTRICT | 40 | 4 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | SAN DIEGO | 0.32 | 491634.34 | 2412080.9806 | 2525448.7867
CA3702364 | CLOVER FLAT ELEMENTARY SCHOOL | 160 | 5 | 1 | 1 | 24000 | 37.5 | 1200000 | 37.5 | 37705.875 | 121575.375 | 100000 | 85000 | 1544281.25 | 386070.3125 | 1930351.5625 | SAN DIEGO | 0.32 | 494170 | 2424521.5625 | 2538474.0759
CA3900756 | LINDEN USD-GLENWOOD SCHOOL | 100 | 1 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SAN JOAQUIN | 0 | 0 | 1925399.1016 | 2015892.8593
CA3900757 | LINDEN USD-WATERLOO ELEMENTARY | 225 | 1 | 1 | 1 | 33750 | 52.7344 | 1200000 | 52.7344 | 39915.0117 | 123658.3711 | 100000 | 85000 | 1548573.3828 | 387143.3457 | 1935716.7285 | SAN JOAQUIN | 0 | 0 | 1935716.7285 | 2026695.4148
CA3900846 | OAK VIEW UNION ELEMENTARY SCH | 350 | 1 | 1 | 1 | 52500 | 82.0312 | 1200000 | 82.0312 | 44163.3516 | 127664.1328 | 100000 | 85000 | 1556827.4844 | 389206.8711 | 1946034.3555 | SAN JOAQUIN | 0 | 0 | 1946034.3555 | 2037497.9702
CA3900848 | LODI USD-TURNER ACADEMY AT TOKAY COLONY | 166 | 2 | 1 | 1 | 24900 | 38.9062 | 1200000 | 38.9062 | 37909.7953 | 121767.6516 | 100000 | 85000 | 1544677.4469 | 386169.3617 | 1930846.8086 | SAN JOAQUIN | 0 | 0 | 1930846.8086 | 2021596.6086
CA3900849 | LODI USD-LIVE OAK SCHOOL | 100 | 1 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SAN JOAQUIN | 0 | 0 | 1925399.1016 | 2015892.8593
CA3900850 | LODI USD-HOUSTON SCHOOL | 405 | 4 | 1 | 1 | 60750 | 94.9219 | 1200000 | 94.9219 | 46032.6211 | 129426.668 | 100000 | 85000 | 1560459.2891 | 390114.8223 | 1950574.1113 | SAN JOAQUIN | 0 | 0 | 1950574.1113 | 2042251.0946
CA3900978 | SJ COUNTY-REDWOOD SCHOOL | 83 | 1 | 1 | 1 | 12450 | 19.4531 | 1200000 | 19.4531 | 35088.8977 | 119107.8258 | 100000 | 85000 | 1539196.7234 | 384799.1809 | 1923995.9043 | SAN JOAQUIN | 0 | 0 | 1923995.9043 | 2014423.7118
CA3900993 | NEW JERUSALEM SCHOOL | 210 | 1 | 1 | 1 | 31500 | 49.2188 | 1200000 | 49.2188 | 39405.2109 | 123177.6797 | 100000 | 85000 | 1547582.8906 | 386895.7227 | 1934478.6133 | SAN JOAQUIN | 0 | 0 | 1934478.6133 | 2025399.1081
CA3901014 | BANTA ELEMENTARY SCHOOL | 200 | 1 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | SAN JOAQUIN | 0 | 0 | 1933653.2031 | 2024534.9037
CA3901085 | LODI USD-DAVIS SCHOOL | 630 | 1 | 1 | 1 | 94500 | 147.6562 | 1200000 | 147.6562 | 53679.6328 | 136637.0391 | 100000 | 85000 | 1575316.6719 | 393829.168 | 1969145.8398 | SAN JOAQUIN | 0 | 0 | 1969145.8398 | 2061695.6943
CA3901090 | NORTH VALLEY SCHOOL PWS | 35 | 1 | 1 | 1 | 5250 | 8.2031 | 1200000 | 8.2031 | 33457.5352 | 117569.6133 | 100000 | 85000 | 1536027.1484 | 384006.7871 | 1920033.9355 | SAN JOAQUIN | 0 | 0 | 1920033.9355 | 2010275.5305
CA3901107 | JEFFERSON ESD-JEFFERSON SCHOOL | 60 | 1 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | SAN JOAQUIN | 0 | 0 | 1922097.4609 | 2012436.0416
CA3901163 | MUSD-NEW HAVEN SCHOOL | 300 | 3 | 1 | 1 | 45000 | 70.3125 | 1200000 | 70.3125 | 42464.0156 | 126061.8281 | 100000 | 85000 | 1553525.8438 | 388381.4609 | 1941907.3047 | SAN JOAQUIN | 0 | 0 | 1941907.3047 | 2033176.948
CA3901167 | EUSD-VAN ALLEN SCHOOL | 200 | 1 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | SAN JOAQUIN | 0 | 0 | 1933653.2031 | 2024534.9037
CA3901169 | MUSD-NILE GARDEN SCHOOL | 804 | 3 | 1 | 1 | 120600 | 188.4375 | 1200000 | 188.4375 | 59593.3219 | 142213.0594 | 100000 | 85000 | 1586806.3813 | 396701.5953 | 1983507.9766 | SAN JOAQUIN | 0 | 0 | 1983507.9766 | 2076732.8515
CA3901209 | ST MARYS HIGH SCHOOL | 950 | 11 | 1 | 1 | 142500 | 222.6562 | 1200000 | 222.6562 | 64555.3828 | 146891.7891 | 100000 | 85000 | 1596447.1719 | 399111.793 | 1995558.9648 | SAN JOAQUIN | 0 | 0 | 1995558.9648 | 2089350.2362
CA3901325 | RIPON CHRISTIAN SCHOOLS | 900 | 1 | 1 | 1 | 135000 | 210.9375 | 1200000 | 210.9375 | 62856.0469 | 145289.4844 | 100000 | 85000 | 1593145.5312 | 398286.3828 | 1991431.9141 | SAN JOAQUIN | 0 | 0 | 1991431.9141 | 2085029.214
CA3901331 | RIPON USD-COLONY OAK SCHOOL | 100 | 1 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SAN JOAQUIN | 0 | 0 | 1925399.1016 | 2015892.8593
CA3902136 | LINDEN USD-CHARTVILLE SCHOOL | 40 | 1 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | SAN JOAQUIN | 0 | 0 | 1920446.6406 | 2010707.6327
CA4000675 | BRANCH ELEMENTARY SCHOOL | 500 | 1 | 1 | 1 | 75000 | 117.1875 | 1200000 | 117.1875 | 49261.3594 | 132471.0469 | 100000 | 85000 | 1566732.4062 | 391683.1016 | 1958415.5078 | SAN LUIS OBISPO | 0.3 | 470019.7219 | 2428435.2297 | 2542571.6855
CA4000732 | CARRISA PLAINS ELEMENTARY | 65 | 1 | 1 | 1 | 9750 | 15.2344 | 1200000 | 15.2344 | 34477.1367 | 118530.9961 | 100000 | 85000 | 1538008.1328 | 384502.0332 | 1922510.166 | SAN LUIS OBISPO | 0.3 | 461402.4398 | 2383912.6059 | 2495956.4983
CA4000767 | SANTA LUCIA SCHOOL | 52 | 1 | 1 | 1 | 7800 | 12.1875 | 1200000 | 12.1875 | 34035.3094 | 118114.3969 | 100000 | 85000 | 1537149.7063 | 384287.4266 | 1921437.1328 | SAN LUIS OBISPO | 0.3 | 461144.9119 | 2382582.0447 | 2494563.4008
CA4100513 | PESCADERO HIGH SCHOOL | 192 | 1 | 1 | 1 | 28800 | 45 | 1200000 | 45 | 38793.45 | 122600.85 | 100000 | 85000 | 1546394.3 | 386598.575 | 1932992.875 | SAN MATEO | 0.32 | 494846.176 | 2427839.051 | 2541947.4864
CA4200833 | BONITA SCHOOL | 589 | 1 | 1 | 1 | 88350 | 138.0469 | 1200000 | 138.0469 | 52286.1773 | 135323.1492 | 100000 | 85000 | 1572609.3266 | 393152.3316 | 1965761.6582 | SANTA BARBARA | 0.3 | 471782.798 | 2437544.4562 | 2552109.0456
CA4200879 | CUYAMA ELEMENTARY SCHOOL | 250 | 1 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | SANTA BARBARA | 0.3 | 465067.2609 | 2402847.5148 | 2515781.348
CA4300605 | GILROY USD-RUCKER SCHOOL | 688 | 1 | 1 | 1 | 103200 | 161.25 | 1200000 | 161.25 | 55650.8625 | 138495.7125 | 100000 | 85000 | 1579146.575 | 394786.6437 | 1973933.2188 | SANTA CLARA | 0.32 | 505326.904 | 2479260.1228 | 2595785.3485
CA4300610 | ANCHORPOINT CHRISTIAN SCHOOL | 167 | 1 | 1 | 1 | 25050 | 39.1406 | 1200000 | 39.1406 | 37943.782 | 121799.6977 | 100000 | 85000 | 1544743.4797 | 386185.8699 | 1930929.3496 | SANTA CLARA | 0.32 | 494317.9135 | 2425247.2631 | 2539233.8845
CA4300779 | LAKESIDE SD-LAKESIDE SCHOOL | 127 | 4 | 1 | 1 | 19050 | 29.7656 | 1200000 | 29.7656 | 36584.3133 | 120517.8539 | 100000 | 85000 | 1542102.1672 | 385525.5418 | 1927627.709 | SANTA CLARA | 0.32 | 493472.6935 | 2421100.4025 | 2534892.1214
CA4400751 | BONNY DOON SCHOOL | 160 | 10 | 1 | 1 | 24000 | 37.5 | 1200000 | 37.5 | 37705.875 | 121575.375 | 100000 | 85000 | 1544281.25 | 386070.3125 | 1930351.5625 | SANTA CRUZ | 0.3 | 463284.375 | 2393635.9375 | 2506136.8266
CA4400756 | MOUNTAIN ELEMENTARY SCHOOL | 250 | 1 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | SANTA CRUZ | 0.3 | 465067.2609 | 2402847.5148 | 2515781.348
CA4400757 | ALIANZA CHARTER SCHOOL/WCSA | 967 | 3 | 1 | 1 | 145050 | 226.6406 | 1200000 | 226.6406 | 65133.157 | 147436.5727 | 100000 | 85000 | 1597569.7297 | 399392.4324 | 1996962.1621 | SANTA CRUZ | 0.3 | 479270.9189 | 2476233.081 | 2592616.0358
CA4400758 | RENAISSANCE HIGH SCHOOL | 250 | 2 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | SANTA CRUZ | 0.3 | 465067.2609 | 2402847.5148 | 2515781.348
CA4500160 | PACHECO ELEMENTARY SCHOOL | 400 | 2 | 1 | 1 | 60000 | 93.75 | 1200000 | 93.75 | 45862.6875 | 129266.4375 | 100000 | 85000 | 1560129.125 | 390032.2812 | 1950161.4062 | SHASTA | 0 | 0 | 1950161.4062 | 2041818.9923
CA4500161 | PRAIRIE ELEMENTARY SCHOOL | 375 | 1 | 1 | 1 | 56250 | 87.8906 | 1200000 | 87.8906 | 45013.0195 | 128465.2852 | 100000 | 85000 | 1558478.3047 | 389619.5762 | 1948097.8809 | SHASTA | 0 | 0 | 1948097.8809 | 2039658.4813
CA4500162 | INDIAN SPRINGS SCHOOL | 25 | 1 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | SHASTA | 0 | 0 | 1919208.5254 | 2009411.3261
CA4500170 | MONTGOMERY CREEK SCHOOL | 95 | 1 | 1 | 1 | 14250 | 22.2656 | 1200000 | 22.2656 | 35496.7383 | 119492.3789 | 100000 | 85000 | 1539989.1172 | 384997.2793 | 1924986.3965 | SHASTA | 0 | 0 | 1924986.3965 | 2015460.7571
CA4500180 | MILLVILLE ELEMENTARY SCHOOL | 110 | 2 | 1 | 1 | 16500 | 25.7812 | 1200000 | 25.7812 | 36006.5391 | 119973.0703 | 100000 | 85000 | 1540979.6094 | 385244.9023 | 1926224.5117 | SHASTA | 0 | 0 | 1926224.5117 | 2016757.0638
CA4500183 | BLACK BUTTE ELEMENTARY SCHOOL | 250 | 1 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | SHASTA | 0 | 0 | 1937780.2539 | 2028855.9258
CA4500190 | OAK RUN ELEMENTARY SCHOOL | 125 | 1 | 1 | 1 | 18750 | 29.2969 | 1200000 | 29.2969 | 36516.3398 | 120453.7617 | 100000 | 85000 | 1541970.1016 | 385492.5254 | 1927462.627 | SHASTA | 0 | 0 | 1927462.627 | 2018053.3704
CA4500193 | VERDE VALE ELEMENTARY SCHOOL | 290 | 1 | 1 | 1 | 43500 | 67.9688 | 1200000 | 67.9688 | 42124.1484 | 125741.3672 | 100000 | 85000 | 1552865.5156 | 388216.3789 | 1941081.8945 | SHASTA | 0 | 0 | 1941081.8945 | 2032312.7436
CA4500214 | WEST VALLEY HIGH SCHOOL | 850 | 1 | 1 | 1 | 127500 | 199.2188 | 1200000 | 199.2188 | 61156.7109 | 143687.1797 | 100000 | 85000 | 1589843.8906 | 397460.9727 | 1987304.8633 | SHASTA | 0 | 0 | 1987304.8633 | 2080708.1919
CA4500322 | BLACK BUTTE JUNIOR HIGH SCHOOL | 100 | 1 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SHASTA | 0 | 0 | 1925399.1016 | 2015892.8593
CA4700559 | BUTTEVILLE UNION SCHOOL | 165 | 2 | 1 | 1 | 24750 | 38.6719 | 1200000 | 38.6719 | 37875.8086 | 121735.6055 | 100000 | 85000 | 1544611.4141 | 386152.8535 | 1930764.2676 | SISKIYOU | 0 | 0 | 1930764.2676 | 2021510.1882
CA4700569 | WILLOW CREEK SCHOOL | 100 | 1 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SISKIYOU | 0 | 0 | 1925399.1016 | 2015892.8593
CA4700577 | BIG SPRINGS UNION ELEM. SCHOOL | 95 | 2 | 1 | 1 | 14250 | 22.2656 | 1200000 | 22.2656 | 35496.7383 | 119492.3789 | 100000 | 85000 | 1539989.1172 | 384997.2793 | 1924986.3965 | SISKIYOU | 0 | 0 | 1924986.3965 | 2015460.7571
CA4700582 | GAZELLE SCHOOL | 60 | 1 | 1 | 1 | 9000 | 14.0625 | 1200000 | 14.0625 | 34307.2031 | 118370.7656 | 100000 | 85000 | 1537677.9688 | 384419.4922 | 1922097.4609 | SISKIYOU | 0 | 0 | 1922097.4609 | 2012436.0416
CA4700585 | JUNCTION ELEMENTARY SCHOOL | 40 | 1 | 1 | 1 | 6000 | 9.375 | 1200000 | 9.375 | 33627.4688 | 117729.8438 | 100000 | 85000 | 1536357.3125 | 384089.3281 | 1920446.6406 | SISKIYOU | 0 | 0 | 1920446.6406 | 2010707.6327
CA4700591 | DELPHIC ELEMENTARY SCHOOL | 50 | 1 | 1 | 1 | 7500 | 11.7188 | 1200000 | 11.7188 | 33967.3359 | 118050.3047 | 100000 | 85000 | 1537017.6406 | 384254.4102 | 1921272.0508 | SISKIYOU | 0 | 0 | 1921272.0508 | 2011571.8372
CA4900679 | FORT ROSS SCHOOL DISTRICT | 100 | 2 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SONOMA | 0.3 | 462095.7844 | 2387494.8859 | 2499707.1456
CA4900693 | BELLEVUE UNION SCH DIST-BELLEVUE SCHOOL | 591 | 2 | 1 | 1 | 88650 | 138.5156 | 1200000 | 138.5156 | 52354.1508 | 135387.2414 | 100000 | 85000 | 1572741.3922 | 393185.348 | 1965926.7402 | SONOMA | 0.3 | 471822.4177 | 2437749.1579 | 2552323.3683
CA4900694 | WRIGHT ELEMENTARY SCHOOL | 500 | 11 | 1 | 1 | 75000 | 117.1875 | 1200000 | 117.1875 | 49261.3594 | 132471.0469 | 100000 | 85000 | 1566732.4062 | 391683.1016 | 1958415.5078 | SONOMA | 0.3 | 470019.7219 | 2428435.2297 | 2542571.6855
CA4900695 | NORTHWEST PREP | 325 | 1 | 1 | 1 | 48750 | 76.1719 | 1200000 | 76.1719 | 43313.6836 | 126862.9805 | 100000 | 85000 | 1555176.6641 | 388794.166 | 1943970.8301 | SONOMA | 0.3 | 466552.9992 | 2410523.8293 | 2523818.4493
CA4900699 | OLIVET ELEMENTARY SCHOOL | 400 | 6 | 1 | 1 | 60000 | 93.75 | 1200000 | 93.75 | 45862.6875 | 129266.4375 | 100000 | 85000 | 1560129.125 | 390032.2812 | 1950161.4062 | SONOMA | 0.3 | 468038.7375 | 2418200.1437 | 2531855.5505
CA4900704 | ALEXANDER VALLEY UNION SCHOOL DISTRICT | 200 | 5 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | SONOMA | 0.3 | 464076.7687 | 2397729.9719 | 2510423.2806
CA4900705 | GEYSERVILLE NEWTECH ACADEMY | 200 | 1 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | SONOMA | 0.3 | 464076.7687 | 2397729.9719 | 2510423.2806
CA4900707 | TWIN HILLS SCHOOL DIST-TWIN HILLS SCHOOL | 400 | 2 | 1 | 1 | 60000 | 93.75 | 1200000 | 93.75 | 45862.6875 | 129266.4375 | 100000 | 85000 | 1560129.125 | 390032.2812 | 1950161.4062 | SONOMA | 0.3 | 468038.7375 | 2418200.1437 | 2531855.5505
CA4900708 | GRAVENSTEIN SCHOOL DISTRICT-GRAVENSTEIN | 398 | 7 | 1 | 1 | 59700 | 93.2812 | 1200000 | 93.2812 | 45794.7141 | 129202.3453 | 100000 | 85000 | 1559997.0594 | 389999.2648 | 1949996.3242 | SONOMA | 0.3 | 467999.1178 | 2417995.442 | 2531641.2278
CA4900710 | TWIN HILLS SCHOOL DIST-APPLE BLOSSOM SCH | 400 | 1 | 1 | 1 | 60000 | 93.75 | 1200000 | 93.75 | 45862.6875 | 129266.4375 | 100000 | 85000 | 1560129.125 | 390032.2812 | 1950161.4062 | SONOMA | 0.3 | 468038.7375 | 2418200.1437 | 2531855.5505
CA4900711 | GRAVENSTEIN SCHOOL DISTRICT-HILLCREST | 289 | 1 | 1 | 1 | 43350 | 67.7344 | 1200000 | 67.7344 | 42090.1617 | 125709.3211 | 100000 | 85000 | 1552799.4828 | 388199.8707 | 1940999.3535 | SONOMA | 0.3 | 465839.8448 | 2406839.1984 | 2519960.6407
CA4900714 | LIBERTY SCHOOL | 225 | 3 | 1 | 1 | 33750 | 52.7344 | 1200000 | 52.7344 | 39915.0117 | 123658.3711 | 100000 | 85000 | 1548573.3828 | 387143.3457 | 1935716.7285 | SONOMA | 0.3 | 464572.0148 | 2400288.7434 | 2513102.3143
CA4900716 | CINNABAR ELEMENTARY SCHOOL | 228 | 2 | 1 | 1 | 34200 | 53.4375 | 1200000 | 53.4375 | 40016.9719 | 123754.5094 | 100000 | 85000 | 1548771.4812 | 387192.8703 | 1935964.3516 | SONOMA | 0.3 | 464631.4444 | 2400595.7959 | 2513423.7983
CA4900719 | WEST SIDE UNION SCHOOL DISTRICT | 200 | 5 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | SONOMA | 0.3 | 464076.7687 | 2397729.9719 | 2510423.2806
CA4900739 | DUNHAM SCHOOL | 200 | 2 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | SONOMA | 0.3 | 464076.7687 | 2397729.9719 | 2510423.2806
CA4900907 | SUMMERFIELD WALDORF SCHOOL | 299 | 13 | 1 | 1 | 44850 | 70.0781 | 1200000 | 70.0781 | 42430.0289 | 126029.782 | 100000 | 85000 | 1553459.8109 | 388364.9527 | 1941824.7637 | SONOMA | 0.3 | 466037.9433 | 2407862.707 | 2521032.2542
CA4900945 | PRESENTATION SCHOOL | 200 | 4 | 1 | 1 | 30000 | 46.875 | 1200000 | 46.875 | 39065.3438 | 122857.2188 | 100000 | 85000 | 1546922.5625 | 386730.6406 | 1933653.2031 | SONOMA | 0.3 | 464076.7687 | 2397729.9719 | 2510423.2806
CA4901156 | WILLOWSIDE SCHOOL | 460 | 5 | 1 | 1 | 69000 | 107.8125 | 1200000 | 107.8125 | 47901.8906 | 131189.2031 | 100000 | 85000 | 1564091.0938 | 391022.7734 | 1955113.8672 | SONOMA | 0.3 | 469227.3281 | 2424341.1953 | 2538285.2315
CA4901168 | SALMON CREEK MIDDLE SCHOOL | 300 | 14 | 1 | 1 | 45000 | 70.3125 | 1200000 | 70.3125 | 42464.0156 | 126061.8281 | 100000 | 85000 | 1553525.8438 | 388381.4609 | 1941907.3047 | SONOMA | 0.3 | 466057.7531 | 2407965.0578 | 2521139.4155
CA4901190 | LIETO WATER SYSTEM (REACH CHARTR SCHOOL) | 134 | 2 | 1 | 1 | 20100 | 31.4062 | 1200000 | 31.4062 | 36822.2203 | 120742.1766 | 100000 | 85000 | 1542564.3969 | 385641.0992 | 1928205.4961 | SONOMA | 0.3 | 462769.3191 | 2390974.8152 | 2503350.6315
CA4901215 | PLUMFIELD ACADEMY (OCCIDENTAL RD.) | 30 | 1 | 1 | 1 | 4500 | 7.0312 | 1200000 | 7.0312 | 33287.6016 | 117409.3828 | 100000 | 85000 | 1535696.9844 | 383924.2461 | 1919621.2305 | SONOMA | 0.3 | 460709.0953 | 2380330.3258 | 2492205.8511
CA4901436 | SEBASTOPOL CHARTER SCHOOL | 360 | 1 | 1 | 1 | 54000 | 84.375 | 1200000 | 84.375 | 44503.2188 | 127984.5938 | 100000 | 85000 | 1557487.8125 | 389371.9531 | 1946859.7656 | SONOMA | 0.3 | 467246.3438 | 2414106.1094 | 2527569.0965
CA5000101 | CHATOM SCHOOL (EH) | 500 | 1 | 1 | 1 | 75000 | 117.1875 | 1200000 | 117.1875 | 49261.3594 | 132471.0469 | 100000 | 85000 | 1566732.4062 | 391683.1016 | 1958415.5078 | STANISLAUS | 0 | 0 | 1958415.5078 | 2050461.0367
CA5000109 | CERES UNIFIED/WESTPORT SCHOOL | 450 | 1 | 1 | 1 | 67500 | 105.4688 | 1200000 | 105.4688 | 47562.0234 | 130868.7422 | 100000 | 85000 | 1563430.7656 | 390857.6914 | 1954288.457 | STANISLAUS | 0 | 0 | 1954288.457 | 2046140.0145
CA5000132 | VALLEY HOME SCHOOL TEXAS | 80 | 1 | 1 | 1 | 12000 | 18.75 | 1200000 | 18.75 | 34986.9375 | 119011.6875 | 100000 | 85000 | 1538998.625 | 384749.6562 | 1923748.2812 | STANISLAUS | 0 | 0 | 1923748.2812 | 2014164.4505
CA5000133 | HART- RANSOM UNION SCHOOL & DISTRICT | 650 | 4 | 1 | 1 | 97500 | 152.3438 | 1200000 | 152.3438 | 54359.3672 | 137277.9609 | 100000 | 85000 | 1576637.3281 | 394159.332 | 1970796.6602 | STANISLAUS | 0 | 0 | 1970796.6602 | 2063424.1032
CA5000155 | ROBERTS FERRY SCHOOL CAFETERIA | 100 | 2 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | STANISLAUS | 0 | 0 | 1925399.1016 | 2015892.8593
CA5000249 | STANISLAUS UNION SCHOOL DIST | 390 | 1 | 1 | 1 | 58500 | 91.4062 | 1200000 | 91.4062 | 45522.8203 | 128945.9766 | 100000 | 85000 | 1559468.7969 | 389867.1992 | 1949335.9961 | STANISLAUS | 0 | 0 | 1949335.9961 | 2040954.7879
CA5000273 | GRATTON SCHOOL | 110 | 2 | 1 | 1 | 16500 | 25.7812 | 1200000 | 25.7812 | 36006.5391 | 119973.0703 | 100000 | 85000 | 1540979.6094 | 385244.9023 | 1926224.5117 | STANISLAUS | 0 | 0 | 1926224.5117 | 2016757.0638
CA5000274 | PARADISE SCHOOL | 152 | 4 | 1 | 1 | 22800 | 35.625 | 1200000 | 35.625 | 37433.9812 | 121319.0063 | 100000 | 85000 | 1543752.9875 | 385938.2469 | 1929691.2344 | STANISLAUS | 0 | 0 | 1929691.2344 | 2020386.7224
CA5000277 | VALLEY HOME SCHOOL PIONEER | 26 | 1 | 1 | 1 | 3900 | 6.0938 | 1200000 | 6.0938 | 33151.6547 | 117281.1984 | 100000 | 85000 | 1535432.8531 | 383858.2133 | 1919291.0664 | STANISLAUS | 0 | 0 | 1919291.0664 | 2009497.7465
CA5000295 | SHILOH SCHOOL DISTRICT | 105 | 7 | 1 | 1 | 15750 | 24.6094 | 1200000 | 24.6094 | 35836.6055 | 119812.8398 | 100000 | 85000 | 1540649.4453 | 385162.3613 | 1925811.8066 | STANISLAUS | 0 | 0 | 1925811.8066 | 2016324.9616
CA5000335 | BRETHREN HERITAGE SCHOOL, INC | 25 | 2 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | STANISLAUS | 0 | 0 | 1919208.5254 | 2009411.3261
CA5000404 | WOOD COLONY CHRISTIAN SCHOOL | 90 | 2 | 1 | 1 | 13500 | 21.0938 | 1200000 | 21.0938 | 35326.8047 | 119332.1484 | 100000 | 85000 | 1539658.9531 | 384914.7383 | 1924573.6914 | STANISLAUS | 0 | 0 | 1924573.6914 | 2015028.6549
CA5000568 | GREGORI HIGH SCHOOL | 2000 | 9 | 1 | 1 | 300000 | 468.75 | 1200000 | 468.75 | 100241.4375 | 180540.1875 | 100000 | 85000 | 1665781.625 | 416445.4062 | 2082227.0312 | STANISLAUS | 0 | 0 | 2082227.0312 | 2180091.7017
CA5000584 | MESA ELEMENTARY SCHOOL | 860 | 5 | 1 | 1 | 129000 | 201.5625 | 1200000 | 201.5625 | 61496.5781 | 144007.6406 | 100000 | 85000 | 1590504.2188 | 397626.0547 | 1988130.2734 | STANISLAUS | 0 | 0 | 1988130.2734 | 2081572.3963
CA5100136 | EAST NICOLAUS JOINT UNION HIGH SCHOOL | 338 | 1 | 1 | 1 | 50700 | 79.2188 | 1200000 | 79.2188 | 43755.5109 | 127279.5797 | 100000 | 85000 | 1556035.0906 | 389008.7727 | 1945043.8633 | SUTTER | 0 | 0 | 1945043.8633 | 2036460.9249
CA5100138 | BROWNS ELEMENTARY SCHOOL | 160 | 1 | 1 | 1 | 24000 | 37.5 | 1200000 | 37.5 | 37705.875 | 121575.375 | 100000 | 85000 | 1544281.25 | 386070.3125 | 1930351.5625 | SUTTER | 0 | 0 | 1930351.5625 | 2021078.0859
CA5100140 | MARCUM ILLINOIS ELEMENTARY SCHOOL | 185 | 7 | 1 | 1 | 27750 | 43.3594 | 1200000 | 43.3594 | 38555.543 | 122376.5273 | 100000 | 85000 | 1545932.0703 | 386483.0176 | 1932415.0879 | SUTTER | 0 | 0 | 1932415.0879 | 2023238.597
CA5100141 | MERIDIAN ELEMENTARY SCHOOL | 100 | 1 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | SUTTER | 0 | 0 | 1925399.1016 | 2015892.8593
CA5100142 | NUESTRO SCHOOL | 120 | 1 | 1 | 1 | 18000 | 28.125 | 1200000 | 28.125 | 36346.4062 | 120293.5312 | 100000 | 85000 | 1541639.9375 | 385409.9844 | 1927049.9219 | SUTTER | 0 | 0 | 1927049.9219 | 2017621.2682
CA5100143 | PLEASANT GROVE ELEM. SCHOOL | 185 | 1 | 1 | 1 | 27750 | 43.3594 | 1200000 | 43.3594 | 38555.543 | 122376.5273 | 100000 | 85000 | 1545932.0703 | 386483.0176 | 1932415.0879 | SUTTER | 0 | 0 | 1932415.0879 | 2023238.597
CA5100149 | BARRY ELEMENTARY SCHOOL | 650 | 1 | 1 | 1 | 97500 | 152.3438 | 1200000 | 152.3438 | 54359.3672 | 137277.9609 | 100000 | 85000 | 1576637.3281 | 394159.332 | 1970796.6602 | SUTTER | 0 | 0 | 1970796.6602 | 2063424.1032
CA5100172 | ENCINAL ELEMENTARY SCHOOL | 128 | 1 | 1 | 1 | 19200 | 30 | 1200000 | 30 | 36618.3 | 120549.9 | 100000 | 85000 | 1542168.2 | 385542.05 | 1927710.25 | SUTTER | 0 | 0 | 1927710.25 | 2018312.6317
CA5200506 | PLUM VALLEY ELEM SCHOOL (NEW SCHOOL) | 70 | 1 | 1 | 1 | 10500 | 16.4062 | 1200000 | 16.4062 | 34647.0703 | 118691.2266 | 100000 | 85000 | 1538338.2969 | 384584.5742 | 1922922.8711 | TEHAMA | 0 | 0 | 1922922.8711 | 2013300.246
CA5200507 | BERRENDOS SCHOOL | 325 | 4 | 1 | 1 | 48750 | 76.1719 | 1200000 | 76.1719 | 43313.6836 | 126862.9805 | 100000 | 85000 | 1555176.6641 | 388794.166 | 1943970.8301 | TEHAMA | 0 | 0 | 1943970.8301 | 2035337.4591
CA5200511 | BEND ELEMENTARY SCHOOL | 100 | 5 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | TEHAMA | 0 | 0 | 1925399.1016 | 2015892.8593
CA5200518 | FLOURNOY SCHOOL | 32 | 2 | 1 | 1 | 4800 | 7.5 | 1200000 | 7.5 | 33355.575 | 117473.475 | 100000 | 85000 | 1535829.05 | 383957.2625 | 1919786.3125 | TEHAMA | 0 | 0 | 1919786.3125 | 2010016.2692
CA5200519 | GERBER UNION ELEMENTARY SCHOOL DISTRICT | 625 | 1 | 1 | 1 | 93750 | 146.4844 | 1200000 | 146.4844 | 53509.6992 | 136476.8086 | 100000 | 85000 | 1574986.5078 | 393746.627 | 1968733.1348 | TEHAMA | 0 | 0 | 1968733.1348 | 2061263.5921
CA5200520 | KIRKWOOD ELEMENTARY SCHOOL | 111 | 4 | 1 | 1 | 16650 | 26.0156 | 1200000 | 26.0156 | 36040.5258 | 120005.1164 | 100000 | 85000 | 1541045.6422 | 385261.4105 | 1926307.0527 | TEHAMA | 0 | 0 | 1926307.0527 | 2016843.4842
CA5200538 | LASSEN VIEW UNION ELEMENTARY SCHOOL DIST | 350 | 4 | 1 | 1 | 52500 | 82.0312 | 1200000 | 82.0312 | 44163.3516 | 127664.1328 | 100000 | 85000 | 1556827.4844 | 389206.8711 | 1946034.3555 | TEHAMA | 0 | 0 | 1946034.3555 | 2037497.9702
CA5200540 | REEDS CREEK SCHOOL | 196 | 7 | 1 | 1 | 29400 | 45.9375 | 1200000 | 45.9375 | 38929.3969 | 122729.0344 | 100000 | 85000 | 1546658.4312 | 386664.6078 | 1933323.0391 | TEHAMA | 0 | 0 | 1933323.0391 | 2024189.2219
CA5200544 | VINA ELEMENTARY SCHOOL | 90 | 2 | 1 | 1 | 13500 | 21.0938 | 1200000 | 21.0938 | 35326.8047 | 119332.1484 | 100000 | 85000 | 1539658.9531 | 384914.7383 | 1924573.6914 | TEHAMA | 0 | 0 | 1924573.6914 | 2015028.6549
CA5200565 | RICHFIELD ELEMENTARY SCHOOL | 280 | 9 | 1 | 1 | 42000 | 65.625 | 1200000 | 65.625 | 41784.2812 | 125420.9062 | 100000 | 85000 | 1552205.1875 | 388051.2969 | 1940256.4844 | TEHAMA | 0 | 0 | 1940256.4844 | 2031448.5391
CA5205007 | RANCHO TEHAMA ELEM SCHOOL | 90 | 5 | 1 | 1 | 13500 | 21.0938 | 1200000 | 21.0938 | 35326.8047 | 119332.1484 | 100000 | 85000 | 1539658.9531 | 384914.7383 | 1924573.6914 | TEHAMA | 0 | 0 | 1924573.6914 | 2015028.6549
CA5304105 | BURNT RANCH SCHOOL | 125 | 2 | 1 | 1 | 18750 | 29.2969 | 1200000 | 29.2969 | 36516.3398 | 120453.7617 | 100000 | 85000 | 1541970.1016 | 385492.5254 | 1927462.627 | TRINITY | 0 | 0 | 1927462.627 | 2018053.3704
CA5305107 | SO TRINITY UNIFIED SCHOOL DIST. | 100 | 6 | 1 | 1 | 15000 | 23.4375 | 1200000 | 23.4375 | 35666.6719 | 119652.6094 | 100000 | 85000 | 1540319.2812 | 385079.8203 | 1925399.1016 | TRINITY | 0 | 0 | 1925399.1016 | 2015892.8593
CA5400519 | PALO VERDE SCHOOL | 500 | 26 | 1 | 1 | 75000 | 117.1875 | 1200000 | 117.1875 | 49261.3594 | 132471.0469 | 100000 | 85000 | 1566732.4062 | 391683.1016 | 1958415.5078 | TULARE | 0 | 0 | 1958415.5078 | 2050461.0367
CA5400538 | ACCELERATED CHARTER HIGH SCHOOL | 172 | 10 | 1 | 1 | 25800 | 40.3125 | 1200000 | 40.3125 | 38113.7156 | 121959.9281 | 100000 | 85000 | 1545073.6438 | 386268.4109 | 1931342.0547 | TULARE | 0 | 0 | 1931342.0547 | 2022115.1313
CA5400558 | SAUCELITO ELEMENTARY SCHOOL | 91 | 11 | 1 | 1 | 13650 | 21.3281 | 1200000 | 21.3281 | 35360.7914 | 119364.1945 | 100000 | 85000 | 1539724.9859 | 384931.2465 | 1924656.2324 | TULARE | 0 | 0 | 1924656.2324 | 2015115.0753
CA5400620 | GRAND VIEW SCHOOL | 400 | 9 | 1 | 1 | 60000 | 93.75 | 1200000 | 93.75 | 45862.6875 | 129266.4375 | 100000 | 85000 | 1560129.125 | 390032.2812 | 1950161.4062 | TULARE | 0 | 0 | 1950161.4062 | 2041818.9923
CA5400624 | KINGS RIVER ELEMENTARY SCHOOL | 550 | 9 | 1 | 1 | 82500 | 128.9062 | 1200000 | 128.9062 | 50960.6953 | 134073.3516 | 100000 | 85000 | 1570034.0469 | 392508.5117 | 1962542.5586 | TULARE | 0 | 0 | 1962542.5586 | 2054782.0588
CA5400636 | OROSI HIGH SCHOOL | 1200 | 8 | 1 | 1 | 180000 | 281.25 | 1200000 | 281.25 | 73052.0625 | 154903.3125 | 100000 | 85000 | 1612955.375 | 403238.8438 | 2016194.2188 | TULARE | 0 | 0 | 2016194.2188 | 2110955.347
CA5400704 | THREE RIVERS ELEMENTARY SCHOOL | 180 | 6 | 1 | 1 | 27000 | 42.1875 | 1200000 | 42.1875 | 38385.6094 | 122216.2969 | 100000 | 85000 | 1545601.9062 | 386400.4766 | 1932002.3828 | TULARE | 0 | 0 | 1932002.3828 | 2022806.4948
CA5400709 | SEQUOIA UNION ELEMENTARY SCHOOL | 400 | 26 | 1 | 1 | 60000 | 93.75 | 1200000 | 93.75 | 45862.6875 | 129266.4375 | 100000 | 85000 | 1560129.125 | 390032.2812 | 1950161.4062 | TULARE | 0 | 0 | 1950161.4062 | 2041818.9923
CA5400711 | SIERRA VIEW JR ACADEMY | 104 | 5 | 1 | 1 | 15600 | 24.375 | 1200000 | 24.375 | 35802.6188 | 119780.7937 | 100000 | 85000 | 1540583.4125 | 385145.8531 | 1925729.2656 | TULARE | 0 | 0 | 1925729.2656 | 2016238.5411
CA5400713 | OAK VALLEY SCHOOL | 652 | 10 | 1 | 1 | 97800 | 152.8125 | 1200000 | 152.8125 | 54427.3406 | 137342.0531 | 100000 | 85000 | 1576769.3938 | 394192.3484 | 1970961.7422 | TULARE | 0 | 0 | 1970961.7422 | 2063596.9441
CA5400714 | SUNDALE UNION SCHOOL | 827 | 11 | 1 | 1 | 124050 | 193.8281 | 1200000 | 193.8281 | 60375.0164 | 142950.1195 | 100000 | 85000 | 1588325.1359 | 397081.284 | 1985406.4199 | TULARE | 0 | 0 | 1985406.4199 | 2078720.5217
CA5400795 | WAUKENA ELEMENTARY SCHOOL | 255 | 7 | 1 | 1 | 38250 | 59.7656 | 1200000 | 59.7656 | 40934.6133 | 124619.7539 | 100000 | 85000 | 1550554.3672 | 387638.5918 | 1938192.959 | TULARE | 0 | 0 | 1938192.959 | 2029288.0281
CA5400844 | ELBOW CREEK SCHOOL | 530 | 11 | 1 | 1 | 79500 | 124.2188 | 1200000 | 124.2188 | 50280.9609 | 133432.4297 | 100000 | 85000 | 1568713.3906 | 392178.3477 | 1960891.7383 | TULARE | 0 | 0 | 1960891.7383 | 2053053.65
CA5400846 | ELBOW SCHOOL | 95 | 3 | 1 | 1 | 14250 | 22.2656 | 1200000 | 22.2656 | 35496.7383 | 119492.3789 | 100000 | 85000 | 1539989.1172 | 384997.2793 | 1924986.3965 | TULARE | 0 | 0 | 1924986.3965 | 2015460.7571
CA5400850 | PACKWOOD SCHOOL | 105 | 2 | 1 | 1 | 15750 | 24.6094 | 1200000 | 24.6094 | 35836.6055 | 119812.8398 | 100000 | 85000 | 1540649.4453 | 385162.3613 | 1925811.8066 | TULARE | 0 | 0 | 1925811.8066 | 2016324.9616
CA5400873 | UNION SCHOOL | 330 | 1 | 1 | 1 | 49500 | 77.3438 | 1200000 | 77.3438 | 43483.6172 | 127023.2109 | 100000 | 85000 | 1555506.8281 | 388876.707 | 1944383.5352 | TULARE | 0 | 0 | 1944383.5352 | 2035769.5613
CA5400882 | PLEASANT VIEW WEST SCHOOL | 220 | 9 | 1 | 1 | 33000 | 51.5625 | 1200000 | 51.5625 | 39745.0781 | 123498.1406 | 100000 | 85000 | 1548243.2188 | 387060.8047 | 1935304.0234 | TULARE | 0 | 0 | 1935304.0234 | 2026263.3125
CA5400884 | ROCKFORD SCHOOL | 285 | 4 | 1 | 1 | 42750 | 66.7969 | 1200000 | 66.7969 | 41954.2148 | 125581.1367 | 100000 | 85000 | 1552535.3516 | 388133.8379 | 1940669.1895 | TULARE | 0 | 0 | 1940669.1895 | 2031880.6414
CA5400886 | COLUMBINE SCHOOL | 250 | 8 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | TULARE | 0 | 0 | 1937780.2539 | 2028855.9258
CA5400972 | OUTSIDE CREEK SCHOOL | 125 | 2 | 1 | 1 | 18750 | 29.2969 | 1200000 | 29.2969 | 36516.3398 | 120453.7617 | 100000 | 85000 | 1541970.1016 | 385492.5254 | 1927462.627 | TULARE | 0 | 0 | 1927462.627 | 2018053.3704
CA5400994 | HOPE ELEMENTARY SCHOOL | 275 | 7 | 1 | 1 | 41250 | 64.4531 | 1200000 | 64.4531 | 41614.3477 | 125260.6758 | 100000 | 85000 | 1551875.0234 | 387968.7559 | 1939843.7793 | TULARE | 0 | 0 | 1939843.7793 | 2031016.4369
CA5402008 | HOT SPRINGS SCHOOL | 42 | 1 | 1 | 1 | 6300 | 9.8438 | 1200000 | 9.8438 | 33695.4422 | 117793.9359 | 100000 | 85000 | 1536489.3781 | 384122.3445 | 1920611.7227 | TULARE | 0 | 0 | 1920611.7227 | 2010880.4736
CA5403130 | ELEANOR ROOSEVELT COMM LEARNING CTR | 295 | 5 | 1 | 1 | 44250 | 69.1406 | 1200000 | 69.1406 | 42294.082 | 125901.5977 | 100000 | 85000 | 1553195.6797 | 388298.9199 | 1941494.5996 | TULARE | 0 | 0 | 1941494.5996 | 2032744.8458
CA5403146 | LIBERTY ELEMENTARY SCHOOL | 500 | 5 | 1 | 1 | 75000 | 117.1875 | 1200000 | 117.1875 | 49261.3594 | 132471.0469 | 100000 | 85000 | 1566732.4062 | 391683.1016 | 1958415.5078 | TULARE | 0 | 0 | 1958415.5078 | 2050461.0367
CA5500148 | CHINESE CAMP SCHOOL | 35 | 1 | 1 | 1 | 5250 | 8.2031 | 1200000 | 8.2031 | 33457.5352 | 117569.6133 | 100000 | 85000 | 1536027.1484 | 384006.7871 | 1920033.9355 | TUOLUMNE | 0 | 0 | 1920033.9355 | 2010275.5305
CA5500152 | CURTIS CREEK ELEMENTARY SCHOOL | 546 | 1 | 1 | 1 | 81900 | 127.9688 | 1200000 | 127.9688 | 50824.7484 | 133945.1672 | 100000 | 85000 | 1569769.9156 | 392442.4789 | 1962212.3945 | TUOLUMNE | 0 | 0 | 1962212.3945 | 2054436.3771
CA5500221 | PINECREST ELEMENTARY SCHOOL | 25 | 10 | 1 | 1 | 3750 | 5.8594 | 1200000 | 5.8594 | 33117.668 | 117249.1523 | 100000 | 85000 | 1535366.8203 | 383841.7051 | 1919208.5254 | TUOLUMNE | 0 | 0 | 1919208.5254 | 2009411.3261
CA5500242 | SIERRA WALDORF SCHOOL | 132 | 17 | 1 | 1 | 19800 | 30.9375 | 1200000 | 30.9375 | 36754.2469 | 120678.0844 | 100000 | 85000 | 1542432.3313 | 385608.0828 | 1928040.4141 | TUOLUMNE | 0 | 0 | 1928040.4141 | 2018658.3135
CA5601405 | SANTA CLARA SCHOOL | 39 | 1 | 1 | 1 | 5850 | 9.1406 | 1200000 | 9.1406 | 33593.482 | 117697.7977 | 100000 | 85000 | 1536291.2797 | 384072.8199 | 1920364.0996 | VENTURA | 0.32 | 491613.2095 | 2411977.3091 | 2525340.2426
CA5602403 | LAGUNA VISTA SCHOOL/OCEANVIEW SCHOOL DIS | 600 | 1 | 1 | 1 | 90000 | 140.625 | 1200000 | 140.625 | 52660.0312 | 135675.6562 | 100000 | 85000 | 1573335.6875 | 393333.9219 | 1966669.6094 | VENTURA | 0.32 | 503467.42 | 2470137.0294 | 2586233.4698
CA5700509 | CLARKSBURG MIDDLE SCHOOL | 460 | 3 | 1 | 1 | 69000 | 107.8125 | 1200000 | 107.8125 | 47901.8906 | 131189.2031 | 100000 | 85000 | 1564091.0938 | 391022.7734 | 1955113.8672 | YOLO | 0 | 0 | 1955113.8672 | 2047004.2189
CA5700510 | DELTA HIGH SCHOOL | 250 | 7 | 1 | 1 | 37500 | 58.5938 | 1200000 | 58.5938 | 40764.6797 | 124459.5234 | 100000 | 85000 | 1550224.2031 | 387556.0508 | 1937780.2539 | YOLO | 0 | 0 | 1937780.2539 | 2028855.9258
CA5700623 | DAVIS JUSD - FAIRFIELD SCHOOL | 65 | 1 | 1 | 1 | 9750 | 15.2344 | 1200000 | 15.2344 | 34477.1367 | 118530.9961 | 100000 | 85000 | 1538008.1328 | 384502.0332 | 1922510.166 | YOLO | 0 | 0 | 1922510.166 | 2012868.1438
CA5700643 | PLAINFIELD ELEM SCHOOL - WATER | 400 | 17 | 1 | 1 | 60000 | 93.75 | 1200000 | 93.75 | 45862.6875 | 129266.4375 | 100000 | 85000 | 1560129.125 | 390032.2812 | 1950161.4062 | YOLO | 0 | 0 | 1950161.4062 | 2041818.9923
CA5800006 | YES CHARTER ACADEMY | 125 | 1 | 1 | 1 | 18750 | 29.2969 | 1200000 | 29.2969 | 36516.3398 | 120453.7617 | 100000 | 85000 | 1541970.1016 | 385492.5254 | 1927462.627 | YUBA | 0 | 0 | 1927462.627 | 2018053.3704
CA5800840 | MJUSD CORDUA SCHOOL | 110 | 3 | 1 | 1 | 16500 | 25.7812 | 1200000 | 25.7812 | 36006.5391 | 119973.0703 | 100000 | 85000 | 1540979.6094 | 385244.9023 | 1926224.5117 | YUBA | 0 | 0 | 1926224.5117 | 2016757.0638
CA5800843 | MJUSD FOOTHILL INTERMEDIATE SCHOOL | 325 | 2 | 1 | 1 | 48750 | 76.1719 | 1200000 | 76.1719 | 43313.6836 | 126862.9805 | 100000 | 85000 | 1555176.6641 | 388794.166 | 1943970.8301 | YUBA | 0 | 0 | 1943970.8301 | 2035337.4591
CA5800844 | MJUSD BROWNS VALLEY SCHOOL | 155 | 5 | 1 | 1 | 23250 | 36.3281 | 1200000 | 36.3281 | 37535.9414 | 121415.1445 | 100000 | 85000 | 1543951.0859 | 385987.7715 | 1929938.8574 | YUBA | 0 | 0 | 1929938.8574 | 2020645.9837
CA5800845 | MJUSD DOBBINS SCHOOL | 85 | 3 | 1 | 1 | 12750 | 19.9219 | 1200000 | 19.9219 | 35156.8711 | 119171.918 | 100000 | 85000 | 1539328.7891 | 384832.1973 | 1924160.9863 | YUBA | 0 | 0 | 1924160.9863 | 2014596.5527
CA5800847 | MJUSD LOMA RICA SCHOOL | 150 | 6 | 1 | 1 | 22500 | 35.1562 | 1200000 | 35.1562 | 37366.0078 | 121254.9141 | 100000 | 85000 | 1543620.9219 | 385905.2305 | 1929526.1523 | YUBA | 0 | 0 | 1929526.1523 | 2020213.8815
Total | [20 empty] | 1651624740.3029

## Generator Cost
PWSID | WATER SYSTEM NAME | COUNTY | POPULATION | TOTAL SERVICE CONNECTIONS | Does your water system have backup power for: 1. Sources: - FROM EAR | ADD (gpd) | MDD (gpm) | Equation Cost ($) | Cost with Permitting muliplier ($) | County Multiplier | Cost with Multiplier ($) | Cost before inflation ($) | Final Cost with inflation ($)
CA1910012 | BELLFLOWER HOME GARDEN WATER COMPANY | LOS ANGELES | 1129 | 342 | None | 169350 | 264.6094 | 120365.7969 | 126384.0867 | 0.32 | 38517.055 | 164901.1417 | 172651.4954
CA1502315 | CAMP OWEN WATER SYSTEM | KERN | 225 | 23 | Some | 33750 | 52.7344 | 48116.4219 | 50522.243 | 0 | 0 | 50522.243 | 52896.7884
CA1500447 | SIERRA BREEZE MUTUAL WATER COMPANY | KERN | 150 | 60 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA4510003 | BURNEY WATER DISTRICT | SHASTA | 3154 | 1413 | Some | 473100 | 739.2188 | 282207.5938 | 296317.9734 | 0 | 0 | 296317.9734 | 310244.9182
CA5510005 | TWAIN HARTE COMMUNITY SERVICES DISTRICT | TUOLUMNE | 2226 | 1582 | Some | 333900 | 521.7188 | 208040.0938 | 218442.0984 | 0 | 0 | 218442.0984 | 228708.8771
CA4100533 | SKYLONDA MUTUAL | SAN MATEO | 420 | 154 | None | 63000 | 98.4375 | 63701.1875 | 66886.2469 | 0.32 | 20384.38 | 87270.6269 | 91372.3463
CA1009051 | CANTUA CREEK VINEYARDS, IV, LLC. | FRESNO | 50 | 16 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA1000039 | FCSA #10/CUMORAH KNOLLS | FRESNO | 132 | 47 | None | 19800 | 30.9375 | 40683.6875 | 42717.8719 | 0 | 0 | 42717.8719 | 44725.6119
CA2400053 | EL NIDO MOBILE HOME PARK | MERCED | 137 | 50 | Some | 20550 | 32.1094 | 41083.2969 | 43137.4617 | 0 | 0 | 43137.4617 | 45164.9224
CA2010013 | CAL AM - COARSEGOLD | MADERA | 83 | 25 |  | 12450 | 19.4531 | 36767.5156 | 38605.8914 | 0 | 0 | 38605.8914 | 40420.3683
CA2300502 | ALBION MUTUAL WATER COMPANY | MENDOCINO | 40 | 27 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0 | 0 | 34997.4187 | 36642.2974
CA5200504 | CITY OF TEHAMA | TEHAMA | 445 | 195 | None | 66750 | 104.2969 | 65699.2344 | 68984.1961 | 0 | 0 | 68984.1961 | 72226.4533
CA1500448 | HILLVIEW ACRES MUTUAL WATER COMPANY | KERN | 36 | 47 | Some | 5400 | 8.4375 | 33011.1875 | 34661.7469 | 0 | 0 | 34661.7469 | 36290.849
CA3600383 | MWD OF SO CAL GENE PLANT | SAN BERNARDINO | 109 | 61 | None | 16350 | 25.5469 | 38845.4844 | 40787.7586 | 0.3 | 11653.6453 | 52441.4039 | 54906.1499
CA4300978 | BRUSH AND OLD WELL MUTUAL WATER COMPANY | SANTA CLARA | 70 | 27 |  | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0.32 | 11433.13 | 48948.0878 | 51248.6479
CA5000048 | LAZY B MOBILEHOME PARK | STANISLAUS | 125 | 49 | None | 18750 | 29.2969 | 40124.2344 | 42130.4461 | 0 | 0 | 42130.4461 | 44110.5771
CA4910701 | U.S. COAST GUARD TRAINING CENTER | SONOMA | 1422 | 217 | None | 213300 | 333.2812 | 143782.9062 | 150972.0516 | 0.3 | 43134.8719 | 194106.9234 | 203229.9488
CA1200701 | ORICK C.S.D. | HUMBOLDT | 450 | 141 | None | 67500 | 105.4688 | 66098.8438 | 69403.7859 | 0 | 0 | 69403.7859 | 72665.7639
CA2700678 | PARADISE RD WS #05 | MONTEREY | 42 | 15 | None | 6300 | 9.8438 | 33490.7188 | 35165.2547 | 0.3 | 10047.2156 | 45212.4703 | 47337.4564
CA2701647 | GREEN ACRES WA | MONTEREY | 50 | 20 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0.3 | 10239.0281 | 46075.6266 | 48241.181
CA4000203 | IRISH HILLS MUTUAL WATER CO | SAN LUIS OBISPO | 135 | 58 |  | 20250 | 31.6406 | 40923.4531 | 42969.6258 | 0.3 | 12277.0359 | 55246.6617 | 57843.2548
CA4100582 | COUNTY SERVICE AREA 11 | SAN MATEO | 450 | 102 | None | 67500 | 105.4688 | 66098.8438 | 69403.7859 | 0.32 | 21151.63 | 90555.4159 | 94811.5205
CA4000202 | EDNA VALLEY RANCH EAST | SAN LUIS OBISPO | 148 | 40 |  | 22200 | 34.6875 | 41962.4375 | 44060.5594 | 0.3 | 12588.7313 | 56649.2906 | 59311.8073
CA5500124 | MONO VISTA RANCH MHP | TUOLUMNE | 105 | 30 | None | 15750 | 24.6094 | 38525.7969 | 40452.0867 | 0 | 0 | 40452.0867 | 42353.3348
CA0400021 | ROBINSON'S CORNER MHP | BUTTE | 20 | 22 | None | 3000 | 4.6875 | 31732.4375 | 33319.0594 | 0 | 0 | 33319.0594 | 34885.0552
CA5500071 | RAWHIDE INVESTMENT COMPANY | TUOLUMNE | 269 | 100 | Some | 40350 | 63.0469 | 51632.9844 | 54214.6336 | 0 | 0 | 54214.6336 | 56762.7214
CA5510015 | TUD - CEDAR RIDGE WATER SYSTEM | TUOLUMNE | 1645 | 676 | NULL | 246750 | 385.5469 | 161605.4844 | 169685.7586 | 0 | 0 | 169685.7586 | 177660.9892
CA3900568 | CARIBOU MOBILE PARK PWS | SAN JOAQUIN | 180 | 72 | Some | 27000 | 42.1875 | 44519.9375 | 46745.9344 | 0 | 0 | 46745.9344 | 48942.9933
CA3400331 | WESTERNER MOBILE HOME PARK | SACRAMENTO | 65 | 49 | Some | 9750 | 15.2344 | 35328.9219 | 37095.368 | 0.32 | 11305.255 | 48400.623 | 50675.4522
CA1000546 | FCSA #49/ FIVE POINTS | FRESNO | 445 | 46 | None | 66750 | 104.2969 | 65699.2344 | 68984.1961 | 0 | 0 | 68984.1961 | 72226.4533
CA3400130 | THE COURTLAND GROUP | SACRAMENTO | 40 | 34 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0.32 | 10665.88 | 45663.2988 | 47809.4738
CA1300018 | GATEWAY | IMPERIAL | 1800 | 48 | None | 270000 | 421.875 | 173993.375 | 182693.0438 | 0 | 0 | 182693.0438 | 191279.6168
CA4400595 | VILLA DEL MONTE MWC | SANTA CRUZ | 419 | 127 | None | 62850 | 98.2031 | 63621.2656 | 66802.3289 | 0.3 | 19086.3797 | 85888.7086 | 89925.4779
CA3600345 | WEST END MWC | SAN BERNARDINO | 63 | 31 |  | 9450 | 14.7656 | 35169.0781 | 36927.532 | 0.3 | 10550.7234 | 47478.2555 | 49709.7335
CA2700838 | SPRING CANYON WA | MONTEREY | 99 | 33 | None | 14850 | 23.2031 | 38046.2656 | 39948.5789 | 0.3 | 11413.8797 | 51362.4586 | 53776.4941
CA2710702 | FORT HUNTER LIGGETT | MONTEREY | 5000 | 160 | Some | 750000 | 1171.875 | 429743.375 | 451230.5438 | 0.3 | 128923.0125 | 580153.5563 | 607420.7734
CA3600184 | NORTH SHORE MWC | SAN BERNARDINO | 25 | 32 | None | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0.3 | 9639.6141 | 43378.2633 | 45417.0417
CA1502690 | DUNE 3 MUTUAL WATER COMPANY, LLC | KERN | 119 | 36 | None | 17850 | 27.8906 | 39644.7031 | 41626.9383 | 0 | 0 | 41626.9383 | 43583.4044
CA3500511 | CASA DE FRUTA ORCHARDS | SAN BENITO | 53 | 20 | None | 7950 | 12.4219 | 34369.8594 | 36088.3523 | 0.3 | 10310.9578 | 46399.3102 | 48580.0777
CA1400020 | ABERDEEN WATER SYSTEM | INYO | 23 | 75 | None | 3450 | 5.3906 | 31972.2031 | 33570.8133 | 0 | 0 | 33570.8133 | 35148.6415
CA3410022 | OLYMPIA MOBILODGE | SACRAMENTO | 450 | 200 | None | 67500 | 105.4688 | 66098.8438 | 69403.7859 | 0.32 | 21151.63 | 90555.4159 | 94811.5205
CA4310021 | PURISSIMA HILLS WATER DISTRICT | SANTA CLARA | 6190 | 2132 | Some | 928500 | 1450.7812 | 524850.4062 | 551092.9266 | 0.32 | 167952.13 | 719045.0566 | 752840.1742
CA5010029 | CITY OF MODESTO - DEL RIO | STANISLAUS | 1274 | 401 | Some | 191100 | 298.5938 | 131954.4688 | 138552.1922 | 0 | 0 | 138552.1922 | 145064.1452
CA4900578 | CARMET BY THE SEA WATER COMPANY | SONOMA | 280 | 64 | None | 42000 | 65.625 | 52512.125 | 55137.7312 | 0.3 | 15753.6375 | 70891.3687 | 74223.2631
CA3301630 | BLYTHE - HIDDEN BEACHES | RIVERSIDE | 383 | 116 | Some | 57450 | 89.7656 | 60744.0781 | 63781.282 | 0.32 | 19438.105 | 83219.387 | 87130.6982
CA1000299 | THREE PALMS MOBILEHOME PARK | FRESNO | 300 | 105 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 59486.4469
CA5200534 | PASKENTA COMM. SERVICES DIST. | TEHAMA | 244 | 74 |  | 36600 | 57.1875 | 49634.9375 | 52116.6844 | 0 | 0 | 52116.6844 | 54566.1685
CA3700900 | LAKE HENSHAW RESORT INC. | SAN DIEGO | 300 | 101 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0.32 | 17315.38 | 74131.4706 | 77615.6497
CA2010012 | CAL AM - RAYMOND | MADERA | 317 | 96 | Some | 47550 | 74.2969 | 55469.2344 | 58242.6961 | 0 | 0 | 58242.6961 | 60980.1028
CA1500550 | WEST VALLEY MUTUAL WATER COMPANY | KERN | 70 | 41 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0 | 0 | 37514.9578 | 39278.1608
CA1900636 | EL RANCHO MOBILE HOME PARK | LOS ANGELES | 215 | 76 | None | 32250 | 50.3906 | 47317.2031 | 49683.0633 | 0.32 | 15141.505 | 64824.5683 | 67871.323
CA5200010 | WOODSON BRIDGE RV PARK | TEHAMA | 45 | 46 | NULL | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0 | 0 | 35417.0086 | 37081.608
CA3701837 | WYNOLA WATER DISTRICT | SAN DIEGO | 120 | 73 | Some | 18000 | 28.125 | 39724.625 | 41710.8562 | 0.32 | 12711.88 | 54422.7363 | 56980.6049
CA2010014 | CAL AM - GOLDSIDE | MADERA | 1020 | 309 |  | 153000 | 239.0625 | 111654.3125 | 117237.0281 | 0 | 0 | 117237.0281 | 122747.1684
CA1500436 | HUNGRY GULCH MWC | KERN | 74 | 36 | None | 11100 | 17.3438 | 36048.2188 | 37850.6297 | 0 | 0 | 37850.6297 | 39629.6093
CA4000670 | WALNUT HILLS MUTUAL WATER CO | SAN LUIS OBISPO | 486 | 26 | None | 72900 | 113.9062 | 68976.0312 | 72424.8328 | 0.3 | 20692.8094 | 93117.6422 | 97494.1714
CA2000832 | SKP PARK OF THE SIERRAS INC | MADERA | 450 | 261 | Some | 67500 | 105.4688 | 66098.8438 | 69403.7859 | 0 | 0 | 69403.7859 | 72665.7639
CA5610056 | VINEYARD AVE ESTATES MWC | VENTURA | 1200 | 342 | None | 180000 | 281.25 | 126040.25 | 132342.2625 | 0.32 | 40332.88 | 172675.1425 | 180790.8742
CA2702388 | ROYAL OAK PLACE WS | MONTEREY | 60 | 20 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA4300792 | ABORN HEIGHTS WATER MUTUAL ASSOCIATION | SANTA CLARA | 45 | 19 | None | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0.32 | 10793.755 | 46210.7636 | 48382.6695
CA2000592 | TWO TWENTY FOUR MOBILE HOME PK | MADERA | 35 | 15 | None | 5250 | 8.2031 | 32931.2656 | 34577.8289 | 0 | 0 | 34577.8289 | 36202.9869
CA1500475 | KRISTA MUTUAL WATER COMPANY | KERN | 501 | 179 | None | 75150 | 117.4219 | 70174.8594 | 73683.6023 | 0 | 0 | 73683.6023 | 77146.7317
CA5800863 | FELLOWSHIP OF FRIENDS | YUBA | 325 | 30 | Some | 48750 | 76.1719 | 56108.6094 | 58914.0398 | 0 | 0 | 58914.0398 | 61682.9997
CA1300575 | DATE GARDENS MOBILE HOME PARK | IMPERIAL | 101 | 72 | None | 15150 | 23.6719 | 38206.1094 | 40116.4148 | 0 | 0 | 40116.4148 | 42001.8863
CA3100023 | AUBURN MOBILE HOME VILLAGE | PLACER | 59 | 23 |  | 8850 | 13.8281 | 34849.3906 | 36591.8602 | 0 | 0 | 36591.8602 | 38311.6776
CA3810001 | SAN FRANCISCO REGIONAL WATER SYSTEM | SAN FRANCISCO | 600 | 257 | None | 90000 | 140.625 | 78087.125 | 81991.4812 | 0.32 | 24987.88 | 106979.3613 | 112007.3912
CA1500340 | WEST TEHACHAPI MUTUAL | KERN | 150 | 36 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA1210010 | SCOTIA CSD | HUMBOLDT | 850 | 304 | None | 127500 | 199.2188 | 98067.5938 | 102970.9734 | 0 | 0 | 102970.9734 | 107810.6092
CA1910203 | LOS ANGELES CWWD 40, R 24,27,33-PEARBLSM | LOS ANGELES | 10854 | 2862 | None | 1628100 | 2543.9062 | 897606.0312 | 942486.3328 | 0.32 | 287233.93 | 1229720.2628 | 1287517.1152
CA1500575 | SAN JOAQUIN ESTATES MUTUAL WATER COMPANY | KERN | 165 | 61 | None | 24750 | 38.6719 | 43321.1094 | 45487.1648 | 0 | 0 | 45487.1648 | 47625.0616
CA3900755 | SHADY REST TRAILER COURT | SAN JOAQUIN | 120 | 49 |  | 18000 | 28.125 | 39724.625 | 41710.8562 | 0 | 0 | 41710.8562 | 43671.2665
CA5410014 | TIPTON COMMUNITY SERVICES DIST | TULARE | 1998 | 608 |  | 299700 | 468.2812 | 189817.9062 | 199308.8016 | 0 | 0 | 199308.8016 | 208676.3152
CA3900719 | MOKELUMNE MOBILE SENIOR PARK | SAN JOAQUIN | 55 | 25 | NULL | 8250 | 12.8906 | 34529.7031 | 36256.1883 | 0 | 0 | 36256.1883 | 37960.2291
CA1500507 | ST. CLAIR RANCHOS MUTUAL WATER CO. | KERN | 105 | 32 | None | 15750 | 24.6094 | 38525.7969 | 40452.0867 | 0 | 0 | 40452.0867 | 42353.3348
CA2702198 | FOOTHILL ESTATES WS | MONTEREY | 183 | 41 | None | 27450 | 42.8906 | 44759.7031 | 46997.6883 | 0.3 | 13427.9109 | 60425.5992 | 63265.6024
CA0105008 | CASTLEWOOD DOMESTIC WATER SYSTEM | ALAMEDA | 524 | 206 |  | 78600 | 122.8125 | 72013.0625 | 75613.7156 | 0.3 | 21603.9188 | 97217.6344 | 101786.8632
CA4000214 | BARON CANYON MUTUAL WATER CO. | SAN LUIS OBISPO | 81 | 25 | None | 12150 | 18.9844 | 36607.6719 | 38438.0555 | 0.3 | 10982.3016 | 49420.357 | 51743.1138
CA4000648 | KEN MAR GARDENS | SAN LUIS OBISPO | 84 | 45 |  | 12600 | 19.6875 | 36847.4375 | 38689.8094 | 0.3 | 11054.2313 | 49744.0406 | 52082.0105
CA5700554 | CAMPERS INN - RV & GOLF COURSE | YOLO | 120 | 68 | None | 18000 | 28.125 | 39724.625 | 41710.8562 | 0 | 0 | 41710.8562 | 43671.2665
CA2000534 | LEISURE ACRES MUTUAL WATER COMPANY | MADERA | 45 | 24 | None | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0 | 0 | 35417.0086 | 37081.608
CA0300019 | FIDDLETOWN COMMUNITY SERVICE | AMADOR | 100 | 66 |  | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA0310006 | RIVER PINES PUD | AMADOR | 510 | 215 | Some | 76500 | 119.5312 | 70894.1562 | 74438.8641 | 0 | 0 | 74438.8641 | 77937.4907
CA2701935 | MOUNT TORO RANCHOS MWA | MONTEREY | 45 | 19 | None | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0.3 | 10119.1453 | 45536.1539 | 47676.3531
CA5500125 | MOTHER LODE MOBILE ESTATES | TUOLUMNE | 210 | 75 |  | 31500 | 49.2188 | 46917.5938 | 49263.4734 | 0 | 0 | 49263.4734 | 51578.8567
CA3103310 | EMIGRANT GAP MUTUAL WATER CO. | PLACER | 125 | 43 |  | 18750 | 29.2969 | 40124.2344 | 42130.4461 | 0 | 0 | 42130.4461 | 44110.5771
CA3301803 | CASTRO TRAILER PARK | RIVERSIDE | 180 | 44 |  | 27000 | 42.1875 | 44519.9375 | 46745.9344 | 0.32 | 14246.38 | 60992.3144 | 63858.9532
CA3610002 | ALPINE WATER USERS ASSOCIATION | SAN BERNARDINO | 2534 | 931 | None | 380100 | 593.9062 | 232656.0312 | 244288.8328 | 0.3 | 69796.8094 | 314085.6422 | 328847.6674
CA2701742 | CALIFORNIA ORCHARD WS | MONTEREY | 150 | 50 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0.3 | 12636.6844 | 56865.0797 | 59537.7384
CA2710005 | CASTROVILLE COMMUNITY SERVICES DISTRICT | MONTEREY | 6897 | 1884 | Some | 1034550 | 1616.4844 | 581355.1719 | 610422.9305 | 0.3 | 174406.5516 | 784829.482 | 821716.4677
CA1400111 | MEADOWCREEK MUTUAL WATER COMPANY | INYO | 764 | 284 | Some | 114600 | 179.0625 | 91194.3125 | 95754.0281 | 0 | 0 | 95754.0281 | 100254.4674
CA5610005 | MEINERS OAKS CWD | VENTURA | 4200 | 1279 | Some | 630000 | 984.375 | 365805.875 | 384096.1688 | 0.32 | 117057.88 | 501154.0488 | 524708.289
CA4200721 | NAPLES | SANTA BARBARA | 67 | 23 | None | 10050 | 15.7031 | 35488.7656 | 37263.2039 | 0.3 | 10646.6297 | 47909.8336 | 50161.5958
CA1710010 | LOWER LAKE COUNTY WATER DISTRICT | LAKE | 1355 | 794 | NULL | 203250 | 317.5781 | 138428.1406 | 145349.5477 | 0 | 0 | 145349.5477 | 152180.9764
CA3701747 | NORTH PEAK MUTUAL WATER COMPANY | SAN DIEGO | 25 | 89 |  | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0.32 | 10282.255 | 44020.9042 | 46089.8867
CA4210002 | LOS ALAMOS COMMUNITY SERVICES DISTRICT | SANTA BARBARA | 1800 | 613 | Some | 270000 | 421.875 | 173993.375 | 182693.0438 | 0.3 | 52198.0125 | 234891.0562 | 245930.9359
CA4900728 | EVERGREEN MOBILE ESTATES | SONOMA | 70 | 23 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0.3 | 10718.5594 | 48233.5172 | 50500.4925
CA5710004 | KNIGHTS LANDING SVC. DIST. | YOLO | 1300 | 287 | Some | 195000 | 304.6875 | 134032.4375 | 140734.0594 | 0 | 0 | 140734.0594 | 147348.5602
CA2701897 | BERRY DR WS #02 | MONTEREY | 50 | 19 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0.3 | 10239.0281 | 46075.6266 | 48241.181
CA4200800 | EAST VALLEY FARMS MUTUAL WATER COMPANY | SANTA BARBARA | 132 | 41 | None | 19800 | 30.9375 | 40683.6875 | 42717.8719 | 0.3 | 12205.1063 | 54922.9781 | 57504.3581
CA1500211 | STOCKDALE ANNEX MUTUAL WATER | KERN | 433 | 143 | Some | 64950 | 101.4844 | 64740.1719 | 67977.1805 | 0 | 0 | 67977.1805 | 71172.108
CA5700712 | CAL AM - DUNNIGAN | YOLO | 400 | 150 | None | 60000 | 93.75 | 62102.75 | 65207.8875 | 0 | 0 | 65207.8875 | 68272.6582
CA1900817 | CLEAR SKIES MOBILE HOME PARK | LOS ANGELES | 131 | 47 | None | 19650 | 30.7031 | 40603.7656 | 42633.9539 | 0.32 | 12993.205 | 55627.1589 | 58241.6354
CA4310019 | CITY OF SAN JOSE - NSJ/ALVISO | SANTA CLARA | 15300 | 2200 | Some | 2295000 | 3585.9375 | 1252938.6875 | 1315585.6219 | 0.32 | 400940.38 | 1716526.0019 | 1797202.724
CA2702608 | THIMIO MWC | MONTEREY | 60 | 21 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA4910024 | CALIFORNIA-AMERICAN GEYSERVILLE (PUC) | SONOMA | 1014 | 306 | None | 152100 | 237.6562 | 111174.7812 | 116733.5203 | 0.3 | 33352.4344 | 150085.9547 | 157139.9946
CA3610031 | MUSCOY MWC NO. 1 | SAN BERNARDINO | 13000 | 1407 | None | 1950000 | 3046.875 | 1069118.375 | 1122574.2937 | 0.3 | 320735.5125 | 1443309.8062 | 1511145.3671
CA2600501 | BIRCHIM COMMUNITY SERVICE DISTRICT | MONO | 150 | 76 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA1502564 | SIERRA MEADOWS | KERN | 68 | 51 | Some | 10200 | 15.9375 | 35568.6875 | 37347.1219 | 0 | 0 | 37347.1219 | 39102.4366
CA1510033 | CWS - KERNVILLE | KERN | 2520 | 1903 | Some | 378000 | 590.625 | 231537.125 | 243113.9813 | 0 | 0 | 243113.9813 | 254540.3384
CA4010003 | SAN MIGUELITO MWC | SAN LUIS OBISPO | 1758 | 693 | Some | 263700 | 412.0312 | 170636.6562 | 179168.4891 | 0.3 | 51190.9969 | 230359.4859 | 241186.3818
CA1510016 | RAND COMMUNITIES WATER DISTRICT | KERN | 303 | 284 | None | 45450 | 71.0156 | 54350.3281 | 57067.8445 | 0 | 0 | 57067.8445 | 59750.0332
CA5500042 | BELLEVIEW OAKS MUTUAL WATER CO | TUOLUMNE | 468 | 168 | Some | 70200 | 109.6875 | 67537.4375 | 70914.3094 | 0 | 0 | 70914.3094 | 74247.2819
CA5602101 | ESTERINA PROPERTIES | VENTURA | 50 | 16 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0.32 | 10921.63 | 46758.2284 | 48955.8652
CA4000200 | BASSI RANCH MUTUAL WATER CO. | SAN LUIS OBISPO | 85 | 24 | None | 12750 | 19.9219 | 36927.3594 | 38773.7273 | 0.3 | 11078.2078 | 49851.9352 | 52194.9761
CA4700513 | HORNBROOK C.S.D. | SISKIYOU | 280 | 147 | None | 42000 | 65.625 | 52512.125 | 55137.7312 | 0 | 0 | 55137.7312 | 57729.2046
CA1200587 | BRICELAND C.S.D. | HUMBOLDT | 75 | 26 | None | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0 | 0 | 37934.5477 | 39717.4714
CA3900813 | HAVEN ACRES RIVER CLUB INC | SAN JOAQUIN | 100 | 51 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA3701995 | WILLOWSIDE TERRACE WATER ASSOCIATION | SAN DIEGO | 100 | 32 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.32 | 12200.38 | 52232.8769 | 54687.8221
CA2900529 | GOLD COUNTRY HOME PARK - WATER SYSTEM | NEVADA | 60 | 27 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 38399.5397
CA1900804 | EVERGREEN MUTUAL WATER COMPANY | LOS ANGELES | 95 | 46 |  | 14250 | 22.2656 | 37726.5781 | 39612.907 | 0.32 | 12072.505 | 51685.412 | 54114.6264
CA4900587 | BRAND WATER COMPANY | SONOMA | 112 | 34 | None | 16800 | 26.25 | 39085.25 | 41039.5125 | 0.3 | 11725.575 | 52765.0875 | 55245.0466
CA1910020 | CAL-AM WATER COMPANY - EAST PASADENA | LOS ANGELES | 9887 | 2996 | Some | 1483050 | 2317.2656 | 820321.5781 | 861337.657 | 0.32 | 262502.905 | 1123840.562 | 1176661.0684
CA2700638 | MAHER RD WS #05 | MONTEREY | 65 | 17 | None | 9750 | 15.2344 | 35328.9219 | 37095.368 | 0.3 | 10598.6766 | 47694.0445 | 49935.6646
CA2700665 | OAK HEIGHTS W & R CO INC | MONTEREY | 105 | 35 | None | 15750 | 24.6094 | 38525.7969 | 40452.0867 | 0.3 | 11557.7391 | 52009.8258 | 54454.2876
CA3301115 | CHIRIACO SUMMIT WATER DIST. | RIVERSIDE | 534 | 37 | None | 80100 | 125.1562 | 72812.2812 | 76452.8953 | 0.32 | 23299.93 | 99752.8253 | 104441.2081
CA1009232 | SUMNER PECK RANCH | FRESNO | 85 | 19 | None | 12750 | 19.9219 | 36927.3594 | 38773.7273 | 0 | 0 | 38773.7273 | 40596.0925
CA4900901 | SOBRE VISTA WATER COMPANY | SONOMA | 80 | 26 | None | 12000 | 18.75 | 36527.75 | 38354.1375 | 0.3 | 10958.325 | 49312.4625 | 51630.1482
CA1000078 | FCWWD #42/ALLUVIAL & FANCHER | FRESNO | 291 | 104 |  | 43650 | 68.2031 | 53391.2656 | 56060.8289 | 0 | 0 | 56060.8289 | 58695.6879
CA2400201 | VOLTA COMMUNITY SD | MERCED | 156 | 44 | None | 23400 | 36.5625 | 42601.8125 | 44731.9031 | 0 | 0 | 44731.9031 | 46834.3026
CA4700523 | GRENADA SANITARY DISTRICT | SISKIYOU | 280 | 103 |  | 42000 | 65.625 | 52512.125 | 55137.7312 | 0 | 0 | 55137.7312 | 57729.2046
CA1300620 | RIO BEND RV GOLF RESORT & STORM CROSSING | IMPERIAL | 500 | 68 | None | 75000 | 117.1875 | 70094.9375 | 73599.6844 | 0 | 0 | 73599.6844 | 77058.8695
CA1910061 | LAS FLORES WATER CO. | LOS ANGELES | 4844 | 1479 | Some | 726600 | 1135.3125 | 417275.5625 | 438139.3406 | 0.32 | 133528.18 | 571667.5206 | 598535.8941
CA2700522 | CABANA HOLIDAY WS | MONTEREY | 400 | 146 | None | 60000 | 93.75 | 62102.75 | 65207.8875 | 0.3 | 18630.825 | 83838.7125 | 87779.132
CA2710009 | CWSC KING CITY | MONTEREY | 14441 | 2749 | Some | 2166150 | 3384.6094 | 1184285.7969 | 1243500.0867 | 0.3 | 355285.7391 | 1598785.8258 | 1673928.7596
CA3900733 | COUNTRY CLUB VISTA MUTUAL WATER CO | SAN JOAQUIN | 75 | 31 |  | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0 | 0 | 37934.5477 | 39717.4714
CA4900736 | CLEAR CREEK WATER COMPANY | SONOMA | 40 | 19 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0.3 | 9999.2625 | 44996.6813 | 47111.5253
CA2000544 | MADERA CO MD1-HIDDEN LAKE ESTATES | MADERA | 162 | 49 | None | 24300 | 37.9688 | 43081.3438 | 45235.4109 | 0 | 0 | 45235.4109 | 47361.4753
CA1910103 | PALM RANCH IRRIGATION DIST. | LOS ANGELES | 5564 | 1702 | None | 834600 | 1304.0625 | 474819.3125 | 498560.2781 | 0.32 | 151942.18 | 650502.4581 | 681076.0737
CA2010016 | RIVERSTONE/ROOTCREEK WATER DISTRICT | MADERA | 2270 | 742 | Some | 340500 | 532.0312 | 211556.6562 | 222134.4891 | 0 | 0 | 222134.4891 | 232574.81
CA4900660 | YULUPA MUTUAL WATER COMPANY | SONOMA | 200 | 59 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.3 | 13835.5125 | 62259.8063 | 65186.0171
CA5010034 | CITY OF MODESTO - NORTH TURLOCK | STANISLAUS | 145 | 52 | None | 21750 | 33.9844 | 41722.6719 | 43808.8055 | 0 | 0 | 43808.8055 | 45867.8193
CA1510014 | MOJAVE PUD | KERN | 4200 | 1200 | Some | 630000 | 984.375 | 365805.875 | 384096.1688 | 0 | 0 | 384096.1688 | 402148.6887
CA3110028 | NORTHSTAR C.S.D. | PLACER | 300 | 933 | Some | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 59486.4469
CA1410007 | HIGHLAND MOBILE HOME PARK | INYO | 1400 | 500 | Some | 210000 | 328.125 | 142024.625 | 149125.8563 | 0 | 0 | 149125.8563 | 156134.7715
CA1510038 | BEAR VALLEY CSD | KERN | 8170 | 2851 | Some | 1225500 | 1914.8438 | 683095.7188 | 717250.5047 | 0 | 0 | 717250.5047 | 750961.2784
CA3700937 | LAZY H MUTUAL WATER COMPANY | SAN DIEGO | 70 | 43 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0.32 | 11433.13 | 48948.0878 | 51248.6479
CA0310012 | AWA BUCKHORN PLANT | AMADOR | 8809 | 2743 | None | 1321350 | 2064.6094 | 734165.7969 | 770874.0867 | 0 | 0 | 770874.0867 | 807105.1688
CA5010033 | CITY OF MODESTO - GRAYSON | STANISLAUS | 871 | 277 | None | 130650 | 204.1406 | 99745.9531 | 104733.2508 | 0 | 0 | 104733.2508 | 109655.7136
CA5601125 | COMMUNITY MUTUAL WATER CO | VENTURA | 53 | 36 | None | 7950 | 12.4219 | 34369.8594 | 36088.3523 | 0.32 | 10998.355 | 47086.7073 | 49299.7826
CA2701257 | CAL AM WATER COMPANY - GARRAPATA | MONTEREY | 30 | 47 |  | 4500 | 7.0312 | 32531.6562 | 34158.2391 | 0.3 | 9759.4969 | 43917.7359 | 45981.8695
CA5500077 | SLIDE INN SNOWBOWL WATER CO | TUOLUMNE | 417 | 153 | None | 62550 | 97.7344 | 63461.4219 | 66634.493 | 0 | 0 | 66634.493 | 69766.3141
CA5210002 | GERBER LAS FLORES CSD | TEHAMA | 1200 | 399 | Some | 180000 | 281.25 | 126040.25 | 132342.2625 | 0 | 0 | 132342.2625 | 138562.3488
CA1500561 | ROUND MOUNTAIN WATER COMPANY | KERN | 50 | 18 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA5610003 | VENTURA CWWD NO. 17 - BELL CANYON | VENTURA | 2049 | 710 | None | 307350 | 480.2344 | 193893.9219 | 203588.618 | 0.32 | 62046.055 | 265634.673 | 278119.5026
CA4900599 | RANDAL'S RANCHETTE MUTUAL WATER COMPANY | SONOMA | 100 | 29 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.3 | 11437.8563 | 51470.3531 | 53889.4597
CA4300526 | OAKMONT WATER SYSTEM | SANTA CLARA | 63 | 25 | None | 9450 | 14.7656 | 35169.0781 | 36927.532 | 0.32 | 11254.105 | 48181.637 | 50446.174
CA5301104 | COVINGTON MILL MWC-DIVISION B | TRINITY | 59 | 99 | None | 8850 | 13.8281 | 34849.3906 | 36591.8602 | 0 | 0 | 36591.8602 | 38311.6776
CA4010028 | SLO CSA NO. 16 - SHANDON | SAN LUIS OBISPO | 1347 | 340 | Some | 202050 | 315.7031 | 137788.7656 | 144678.2039 | 0.3 | 41336.6297 | 186014.8336 | 194757.5308
CA2310009 | BROOKTRAILS TOWNSHIP CSD | MENDOCINO | 3800 | 1554 | Some | 570000 | 890.625 | 333837.125 | 350528.9813 | 0 | 0 | 350528.9813 | 367003.8434
CA5301010 | BUD FINE MWC | TRINITY | 43 | 40 | None | 6450 | 10.0781 | 33570.6406 | 35249.1727 | 0 | 0 | 35249.1727 | 36905.8838
CA1710009 | UPPER LAKE COUNTY WATER DISTRICT | LAKE | 989 | 401 | Some | 148350 | 231.7969 | 109176.7344 | 114635.5711 | 0 | 0 | 114635.5711 | 120023.4429
CA3310026 | NUEVO WATER COMPANY | RIVERSIDE | 7033 | 1882 | Some | 1054950 | 1648.3594 | 592224.5469 | 621835.7742 | 0.32 | 189511.855 | 811347.6292 | 849480.9678
CA4400558 | SAN ANDREAS MUTUAL WATER CO | SANTA CRUZ | 350 | 135 | Some | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0.3 | 17431.9969 | 78443.9859 | 82130.8533
CA5010021 | DENAIR COMMUNITY SERVICES DISTRICT | STANISLAUS | 5189 | 1674 | Some | 778350 | 1216.1719 | 444848.6094 | 467091.0398 | 0 | 0 | 467091.0398 | 489044.3187
CA1502659 | OWENS PEAK SOUTH | KERN | 40 | 17 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0 | 0 | 34997.4187 | 36642.2974
CA0510002 | CALAVERAS PUD | CALAVERAS | 6286 | 1906 | Some | 942900 | 1473.2812 | 532522.9062 | 559149.0516 | 0 | 0 | 559149.0516 | 585429.057
CA1200588 | SEAWOOD ESTATES MUTUAL WATER COMPANY | HUMBOLDT | 60 | 23 |  | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 38399.5397
CA5200570 | SURREY VILLAGE WATER CO. INC. | TEHAMA | 145 | 75 | Some | 21750 | 33.9844 | 41722.6719 | 43808.8055 | 0 | 0 | 43808.8055 | 45867.8193
CA4900585 | BENNETT RIDGE MUTUAL WATER COMPANY | SONOMA | 446 | 135 | None | 66900 | 104.5312 | 65779.1562 | 69068.1141 | 0.3 | 19733.7469 | 88801.8609 | 92975.5484
CA5200584 | LITTLE AVENUE WATER SYSTEM | TEHAMA | 53 | 16 |  | 7950 | 12.4219 | 34369.8594 | 36088.3523 | 0 | 0 | 36088.3523 | 37784.5049
CA4500204 | WHITE OAK MUTUAL WATER COMPANY | SHASTA | 415 | 126 | Some | 62250 | 97.2656 | 63301.5781 | 66466.657 | 0 | 0 | 66466.657 | 69590.5899
CA3700924 | LAKE MORENA VIEWS MWC | SAN DIEGO | 360 | 123 | None | 54000 | 84.375 | 58905.875 | 61851.1687 | 0.32 | 18849.88 | 80701.0488 | 84493.998
CA1500349 | STOCKDALE MUTUAL WATER CO. | KERN | 200 | 81 |  | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA0400019 | OROVILLE MOBILE HOME PARK | BUTTE | 74 | 35 | None | 11100 | 17.3438 | 36048.2188 | 37850.6297 | 0 | 0 | 37850.6297 | 39629.6093
CA1200643 | BEACH CREEK MOBILE HOME PARK | HUMBOLDT | 67 | 24 |  | 10050 | 15.7031 | 35488.7656 | 37263.2039 | 0 | 0 | 37263.2039 | 39014.5745
CA4900584 | TIMBER COVE COUNTY WATER DISTRICT | SONOMA | 271 | 189 | None | 40650 | 63.5156 | 51792.8281 | 54382.4695 | 0.3 | 15537.8484 | 69920.318 | 73206.5729
CA2000551 | MD 07 MARINA VIEW HEIGHTS | MADERA | 200 | 83 |  | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA4500018 | SALT CREEK SUMMER HOMES | SHASTA | 151 | 47 | None | 22650 | 35.3906 | 42202.2031 | 44312.3133 | 0 | 0 | 44312.3133 | 46394.992
CA3400149 | RANCHO MARINA | SACRAMENTO | 250 | 77 |  | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0.32 | 16036.63 | 68656.8222 | 71883.6928
CA4900543 | SONOMA COUNTY CSA 41-SALMON CREEK | SONOMA | 427 | 99 | None | 64050 | 100.0781 | 64260.6406 | 67473.6727 | 0.3 | 19278.1922 | 86751.8648 | 90829.2025
CA1910054 | LA CANADA IRRIGATION DIST. | LOS ANGELES | 9300 | 2946 | Some | 1395000 | 2179.6875 | 773407.4375 | 812077.8094 | 0.32 | 247490.38 | 1059568.1894 | 1109367.8943
CA2701731 | BRANDON CREEK MWS | MONTEREY | 41 | 26 | Some | 6150 | 9.6094 | 33410.7969 | 35081.3367 | 0.3 | 10023.2391 | 45104.5758 | 47224.4908
CA4210019 | MISSION HILLS CSD | SANTA BARBARA | 3600 | 1271 | Some | 540000 | 843.75 | 317852.75 | 333745.3875 | 0.3 | 95355.825 | 429101.2125 | 449268.9695
CA4900551 | MELITA HEIGHTS MUTUAL WATER COMPANY | SONOMA | 64 | 25 | None | 9600 | 15 | 35249 | 37011.45 | 0.3 | 10574.7 | 47586.15 | 49822.6991
CA5810700 | BEALE AIR FORCE BASE | YUBA | 7252 | 841 | Some | 1087800 | 1699.6875 | 609727.4375 | 640213.8094 | 0 | 0 | 640213.8094 | 670303.8584
CA2000727 | MD 36 EASTIN ARCOLA | MADERA | 80 | 16 |  | 12000 | 18.75 | 36527.75 | 38354.1375 | 0 | 0 | 38354.1375 | 40156.782
CA4900560 | KELLY MUTUAL WATER COMPANY | SONOMA | 135 | 41 | None | 20250 | 31.6406 | 40923.4531 | 42969.6258 | 0.3 | 12277.0359 | 55246.6617 | 57843.2548
CA2000293 | MD 46 AHWAHNEE RESORTS | MADERA | 300 | 90 |  | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 59486.4469
CA1009179 | BRITZ/FIVE POINT SYSTEM | FRESNO | 76 | 23 | None | 11400 | 17.8125 | 36208.0625 | 38018.4656 | 0 | 0 | 38018.4656 | 39805.3335
CA3301355 | ANZA RV RESORT | RIVERSIDE | 120 | 101 | None | 18000 | 28.125 | 39724.625 | 41710.8562 | 0.32 | 12711.88 | 54422.7363 | 56980.6049
CA3500505 | THOUSAND TRAILS SAN BENITO PRESERVE | SAN BENITO | 1025 | 365 | None | 153750 | 240.2344 | 112053.9219 | 117656.618 | 0.3 | 33616.1766 | 151272.7945 | 158382.6159
CA1800523 | PINEVIEW MOBILE HOME PARK | LASSEN | 113 | 52 | None | 16950 | 26.4844 | 39165.1719 | 41123.4305 | 0 | 0 | 41123.4305 | 43056.2317
CA3600270 | GOLDEN STATE WATER MORONGO DELNORTE | SAN BERNARDINO | 870 | 165 | Some | 130500 | 203.9062 | 99666.0312 | 104649.3328 | 0.3 | 29899.8094 | 134549.1422 | 140872.9519
CA2000552 | MD 24 TEAFORD MEADOW LAKES | MADERA | 150 | 66 |  | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA3700936 | RANCHO ESTATES MUTUAL WATER CO. | SAN DIEGO | 200 | 89 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.32 | 14757.88 | 63182.1738 | 66151.7359
CA1500209 | ALTA SIERRA MUTUAL WATER CO. | KERN | 143 | 225 | None | 21450 | 33.5156 | 41562.8281 | 43640.9695 | 0 | 0 | 43640.9695 | 45692.0951
CA2701367 | TIERRA MEADOWS HOA WS | MONTEREY | 63 | 21 | None | 9450 | 14.7656 | 35169.0781 | 36927.532 | 0.3 | 10550.7234 | 47478.2555 | 49709.7335
CA4710006 | MCCLOUD C.S.D. | SISKIYOU | 1300 | 730 |  | 195000 | 304.6875 | 134032.4375 | 140734.0594 | 0 | 0 | 140734.0594 | 147348.5602
CA2000524 | SKY ACRES MUTUAL WATER CORP | MADERA | 175 | 64 | None | 26250 | 41.0156 | 44120.3281 | 46326.3445 | 0 | 0 | 46326.3445 | 48503.6827
CA3301682 | TRAILS END MUTUAL WATER COMPANY | RIVERSIDE | 52 | 34 | None | 7800 | 12.1875 | 34289.9375 | 36004.4344 | 0.32 | 10972.78 | 46977.2144 | 49185.1435
CA2800625 | ADVENTIST HEALTH - ST. HELENA HOSPITAL | NAPA | 860 | 227 | Some | 129000 | 201.5625 | 98866.8125 | 103810.1531 | 0.3 | 29660.0438 | 133470.1969 | 139743.2961
CA4810025 | SID - PLEASANT HILLS RANCH | SOLANO | 73 | 27 | NULL | 10950 | 17.1094 | 35968.2969 | 37766.7117 | 0.3 | 10790.4891 | 48557.2008 | 50839.3892
CA5402036 | R-RANCH IN THE SEQUOIAS | TULARE | 330 | 115 | Some | 49500 | 77.3438 | 56508.2188 | 59333.6297 | 0 | 0 | 59333.6297 | 62122.3103
CA3600087 | DEER LODGE WATER SYSTEM | SAN BERNARDINO | 745 | 193 | None | 111750 | 174.6094 | 89675.7969 | 94159.5867 | 0.3 | 26902.7391 | 121062.3258 | 126752.2551
CA1910025 | LOS ANGELES CWWD 40, REG. 39-ROCK CREEK | LOS ANGELES | 1326 | 350 |  | 198900 | 310.7812 | 136110.4062 | 142915.9266 | 0.32 | 43555.33 | 186471.2566 | 195235.4056
CA4900532 | SONOMA COUNTY CSA 41-JENNER | SONOMA | 406 | 123 | None | 60900 | 95.1562 | 62582.2812 | 65711.3953 | 0.3 | 18774.6844 | 84486.0797 | 88456.9254
CA3900637 | BIG WHEEL MOBILE HOME PARK | SAN JOAQUIN | 120 | 63 |  | 18000 | 28.125 | 39724.625 | 41710.8562 | 0 | 0 | 41710.8562 | 43671.2665
CA4900562 | DIAMOND A MUTUAL WATER COMPANY | SONOMA | 420 | 190 | None | 63000 | 98.4375 | 63701.1875 | 66886.2469 | 0.3 | 19110.3563 | 85996.6031 | 90038.4435
CA3710011 | JACUMBA COMMUNITY SD | SAN DIEGO | 561 | 248 | Some | 84150 | 131.4844 | 74970.1719 | 78718.6805 | 0.32 | 23990.455 | 102709.1355 | 107536.4648
CA4300992 | GOLDEN HEIGHTS MUTUAL WATER COMPANY | SANTA CLARA | 66 | 21 | None | 9900 | 15.4688 | 35408.8438 | 37179.2859 | 0.32 | 11330.83 | 48510.1159 | 50790.0914
CA4000631 | ALMIRA WATER ASSOCIATION | SAN LUIS OBISPO | 40 | 20 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0.3 | 9999.2625 | 44996.6813 | 47111.5253
CA2701570 | LOS CARNEROS MWA | MONTEREY | 105 | 24 | None | 15750 | 24.6094 | 38525.7969 | 40452.0867 | 0.3 | 11557.7391 | 52009.8258 | 54454.2876
CA1500579 | LIFE WATER CO-OP | KERN | 27 | 18 | None | 4050 | 6.3281 | 32291.8906 | 33906.4852 | 0 | 0 | 33906.4852 | 35500.09
CA5602104 | DEL NORTE MUTUAL WATER CO. | VENTURA | 211 | 84 | None | 31650 | 49.4531 | 46997.5156 | 49347.3914 | 0.32 | 15039.205 | 64386.5964 | 67412.7664
CA1900794 | ANTELOPE PARK MUTUAL WATER COMPANY | LOS ANGELES | 445 | 145 |  | 66750 | 104.2969 | 65699.2344 | 68984.1961 | 0.32 | 21023.755 | 90007.9511 | 94238.3248
CA5610069 | VENTURA CWWD NO. 38 - LAKE SHERWOOD | VENTURA | 1527 | 777 | Some | 229050 | 357.8906 | 152174.7031 | 159783.4383 | 0.32 | 48695.905 | 208479.3433 | 218277.8724
CA5010009 | KEYES COMMUNITY SERVICES DIST. | STANISLAUS | 5999 | 1370 | Some | 899850 | 1406.0156 | 509585.3281 | 535064.5945 | 0 | 0 | 535064.5945 | 560212.6305
CA2700702 | PRUNEDALE MWC | MONTEREY | 277 | 84 | NULL | 41550 | 64.9219 | 52272.3594 | 54885.9773 | 0.3 | 15681.7078 | 70567.6852 | 73884.3664
CA2700772 | STRUVE RD WS #02 | MONTEREY | 166 | 105 | None | 24900 | 38.9062 | 43401.0312 | 45571.0828 | 0.3 | 13020.3094 | 58591.3922 | 61345.1876
CA4900673 | ATHENA TERRACE MUTUAL WATER COMPANY | SONOMA | 74 | 23 |  | 11100 | 17.3438 | 36048.2188 | 37850.6297 | 0.3 | 10814.4656 | 48665.0953 | 50952.3548
CA0400026 | MEADOWBROOK OAKS | BUTTE | 50 | 26 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA0310008 | CAMANCHE NORTH SHORE INC. | AMADOR | 1184 | 211 | Some | 177600 | 277.5 | 124761.5 | 130999.575 | 0 | 0 | 130999.575 | 137156.555
CA5510028 | TUD-APPLE VALLEY ESTATES | TUOLUMNE | 507 | 245 | NULL | 76050 | 118.8281 | 70654.3906 | 74187.1102 | 0 | 0 | 74187.1102 | 77673.9043
CA5500104 | CASCADE ESTATES | TUOLUMNE | 316 | 113 | Some | 47400 | 74.0625 | 55389.3125 | 58158.7781 | 0 | 0 | 58158.7781 | 60892.2407
CA4500247 | WEST COTTONWOOD APARTMENTS | SHASTA | 35 | 17 | None | 5250 | 8.2031 | 32931.2656 | 34577.8289 | 0 | 0 | 34577.8289 | 36202.9869
CA5000090 | RIVERVIEW MOBILE HOME ESTATES | STANISLAUS | 250 | 175 | Some | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 55093.3412
CA1010028 | RIVERDALE PUBLIC UTILITY DISTRICT | FRESNO | 3145 | 928 | Some | 471750 | 737.1094 | 281488.2969 | 295562.7117 | 0 | 0 | 295562.7117 | 309454.1592
CA5010023 | CITY OF MODESTO - SOUTH TURLOCK | STANISLAUS | 1079 | 332 | None | 161850 | 252.8906 | 116369.7031 | 122188.1883 | 0 | 0 | 122188.1883 | 127931.0331
CA4200924 | EL RANCHO TAJIGUAS | SANTA BARBARA | 40 | 20 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0.3 | 9999.2625 | 44996.6813 | 47111.5253
CA1500398 | FRONTIER TRAILS HOMEOWNERS ASSOC INC. | KERN | 32 | 32 | Some | 4800 | 7.5 | 32691.5 | 34326.075 | 0 | 0 | 34326.075 | 35939.4005
CA5200531 | RIVER POINTE LANDING MHP | TEHAMA | 104 | 40 | NULL | 15600 | 24.375 | 38445.875 | 40368.1687 | 0 | 0 | 40368.1687 | 42265.4727
CA1510045 | GOLDEN HILLS CSD | KERN | 9640 | 2921 | Some | 1446000 | 2259.375 | 800580.875 | 840609.9187 | 0 | 0 | 840609.9187 | 880118.5849
CA1500393 | RAINBIRD VALLEY MUTUAL WATER COMPANY | KERN | 238 | 85 | NULL | 35700 | 55.7812 | 49155.4062 | 51613.1766 | 0 | 0 | 51613.1766 | 54038.9959
CA0300011 | SUTTER PINES MHP | AMADOR | 40 | 19 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0 | 0 | 34997.4187 | 36642.2974
CA3500006 | CSA NO. 31 STONEGATE WS | SAN BENITO | 252 | 77 | None | 37800 | 59.0625 | 50274.3125 | 52788.0281 | 0.3 | 15082.2938 | 67870.3219 | 71060.227
CA4900846 | ROLLING OAKS ROAD ASSOCIATION | SONOMA | 25 | 16 | None | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0.3 | 9639.6141 | 43378.2633 | 45417.0417
CA5500243 | RAMBLING HILLS ESTATES | TUOLUMNE | 78 | 38 | None | 11700 | 18.2812 | 36367.9062 | 38186.3016 | 0 | 0 | 38186.3016 | 39981.0577
CA3000585 | PAGE AVENUE MUTUAL WATER COMPANY | ORANGE | 115 | 36 | None | 17250 | 26.9531 | 39325.0156 | 41291.2664 | 0.3 | 11797.5047 | 53088.7711 | 55583.9433
CA4400764 | MOUNT MADONNA CENTER | SANTA CRUZ | 165 | 31 | Some | 24750 | 38.6719 | 43321.1094 | 45487.1648 | 0.3 | 12996.3328 | 58483.4977 | 61232.222
CA1400078 | SCE BISHOP CREEK PLANT 4 | INYO | 38 | 15 |  | 5700 | 8.9062 | 33171.0312 | 34829.5828 | 0 | 0 | 34829.5828 | 36466.5732
CA5610035 | RIO MANOR MUTUAL WATER CO | VENTURA | 983 | 295 | None | 147450 | 230.3906 | 108697.2031 | 114132.0633 | 0.32 | 34783.105 | 148915.1683 | 155914.1812
CA3310051 | MYOMA DUNES MUTUAL WATER COMPANY | RIVERSIDE | 8948 | 2551 | Some | 1342200 | 2097.1875 | 745274.9375 | 782538.6844 | 0.32 | 238487.98 | 1021026.6644 | 1069014.9176
CA2700594 | HIDDEN VALLEY WA | MONTEREY | 164 | 32 |  | 24600 | 38.4375 | 43241.1875 | 45403.2469 | 0.3 | 12972.3563 | 58375.6031 | 61119.2565
CA3900831 | ARBOR MOBILE HOME PARK WS | SAN JOAQUIN | 340 | 173 |  | 51000 | 79.6875 | 57307.4375 | 60172.8094 | 0 | 0 | 60172.8094 | 63000.9314
CA1910029 | CITY OF INDUSTRY WATERWORKS SYSTEMS | LOS ANGELES | 6151 | 1864 | None | 922650 | 1441.6406 | 521733.4531 | 547820.1258 | 0.32 | 166954.705 | 714774.8308 | 748369.2478
CA1510800 | CCI - TEHACHAPI | KERN | 4482 | 1806 | None | 672300 | 1050.4688 | 388343.8438 | 407761.0359 | 0 | 0 | 407761.0359 | 426925.8046
CA4010024 | SLO CWWD NO. 23 - SANTA MARGARITA | SAN LUIS OBISPO | 1259 | 503 | None | 188850 | 295.0781 | 130755.6406 | 137293.4227 | 0.3 | 39226.6922 | 176520.1148 | 184816.5602
CA1100445 | ORLAND MOBILE H.P. | GLENN | 178 | 54 |  | 26700 | 41.7188 | 44360.0938 | 46578.0984 | 0 | 0 | 46578.0984 | 48767.2691
CA1500458 | R.S. MUTUAL WATER COMPANY | KERN | 67 | 24 | None | 10050 | 15.7031 | 35488.7656 | 37263.2039 | 0 | 0 | 37263.2039 | 39014.5745
CA1500466 | A.F.P. MUTUAL WATER COMPANY | KERN | 710 | 216 | Some | 106500 | 166.4062 | 86878.5312 | 91222.4578 | 0 | 0 | 91222.4578 | 95509.9133
CA5100107 | SUTTER CO. WWD#1 (ROBBINS) | SUTTER | 339 | 94 |  | 50850 | 79.4531 | 57227.5156 | 60088.8914 | 0 | 0 | 60088.8914 | 62913.0693
CA5110001 | CITY OF LIVE OAK | SUTTER | 8912 | 2407 | Some | 1336800 | 2088.75 | 742397.75 | 779517.6375 | 0 | 0 | 779517.6375 | 816154.9665
CA2700731 | Z RANCH MWC | MONTEREY | 62 | 27 | None | 9300 | 14.5312 | 35089.1562 | 36843.6141 | 0.3 | 10526.7469 | 47370.3609 | 49596.7679
CA4500014 | LAKESHORE HEIGHTS MUTUAL WATER | SHASTA | 264 | 66 | None | 39600 | 61.875 | 51233.375 | 53795.0437 | 0 | 0 | 53795.0437 | 56323.4108
CA0610002 | CITY OF COLUSA | COLUSA | 6175 | 2205 | Some | 926250 | 1447.2656 | 523651.5781 | 549834.157 | 0 | 0 | 549834.157 | 575676.3624
CA4000789 | SPANISH LAKES MUTUAL WATER CO | SAN LUIS OBISPO | 125 | 45 | None | 18750 | 29.2969 | 40124.2344 | 42130.4461 | 0.3 | 12037.2703 | 54167.7164 | 56713.5991
CA4510004 | SHASTA CSA - JONES VALLEY, #6 | SHASTA | 1119 | 479 | None | 167850 | 262.2656 | 119566.5781 | 125544.907 | 0 | 0 | 125544.907 | 131445.5177
CA5610058 | CRESTVIEW MUTUAL WATER CO | VENTURA | 2040 | 620 | None | 306000 | 478.125 | 193174.625 | 202833.3563 | 0.32 | 61815.88 | 264649.2363 | 277087.7504
CA4010019 | TEMPLETON CSD | SAN LUIS OBISPO | 9322 | 2957 | Some | 1398300 | 2184.8438 | 775165.7188 | 813924.0047 | 0.3 | 232549.7156 | 1046473.7203 | 1095657.9852
CA3200104 | GRIZZLY LAKE CSD-DELLEKER | PLUMAS | 657 | 350 | None | 98550 | 153.9844 | 82642.6719 | 86774.8055 | 0 | 0 | 86774.8055 | 90853.2213
CA3200107 | GRIZZLY LAKE CSD-CROCKER/WELCH | PLUMAS | 215 | 70 | None | 32250 | 50.3906 | 47317.2031 | 49683.0633 | 0 | 0 | 49683.0633 | 52018.1673
CA1502750 | RIVERVIEW HOMEOWNERS ASSOCIATION | KERN | 40 | 20 | Some | 6000 | 9.375 | 33330.875 | 34997.4187 | 0 | 0 | 34997.4187 | 36642.2974
CA1910075 | LOS ANGELES CWWD 21-KAGEL CANYON | LOS ANGELES | 559 | 250 | None | 83850 | 131.0156 | 74810.3281 | 78550.8445 | 0.32 | 23939.305 | 102490.1495 | 107307.1866
CA2801080 | MILTON ROAD WATER COMPANY | NAPA | 55 | 24 | None | 8250 | 12.8906 | 34529.7031 | 36256.1883 | 0.3 | 10358.9109 | 46615.0992 | 48806.0089
CA2000527 | YOSEMITE FORKS EST MUTUAL | MADERA | 110 | 99 | None | 16500 | 25.7812 | 38925.4062 | 40871.6766 | 0 | 0 | 40871.6766 | 42792.6454
CA3010008 | EASTSIDE WATER ASSOCIATION | ORANGE | 2000 | 333 |  | 300000 | 468.75 | 189977.75 | 199476.6375 | 0.3 | 56993.325 | 256469.9625 | 268524.0507
CA4901071 | BOULEVARD HEIGHTS MUTUAL WATER | SONOMA | 60 | 18 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA2300730 | WESTPORT COUNTY WATER DISTRICT | MENDOCINO | 369 | 73 | None | 55350 | 86.4844 | 59625.1719 | 62606.4305 | 0 | 0 | 62606.4305 | 65548.9327
CA3610108 | GOLDEN STATE WATER CO - LUCERNE | SAN BERNARDINO | 751 | 317 | Some | 112650 | 176.0156 | 90155.3281 | 94663.0945 | 0.3 | 27046.5984 | 121709.693 | 127430.0485
CA4500246 | EL RIO ESTATES | SHASTA | 434 | 155 | Some | 65100 | 101.7188 | 64820.0938 | 68061.0984 | 0 | 0 | 68061.0984 | 71259.9701
CA2700536 | CORRAL DE TIERRA ESTATES WC | MONTEREY | 45 | 16 | None | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0.3 | 10119.1453 | 45536.1539 | 47676.3531
CA1910064 | LITTLEROCK CREEK IRRIGATION DIST. | LOS ANGELES | 3488 | 1352 | Some | 523200 | 817.5 | 308901.5 | 324346.575 | 0.32 | 98848.48 | 423195.055 | 443085.2226
CA2000737 | MD 42 STILL MEADOW | MADERA | 100 | 34 |  | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA5000099 | DEL RIO EAST HOA WATER SYSTEM | STANISLAUS | 110 | 55 |  | 16500 | 25.7812 | 38925.4062 | 40871.6766 | 0 | 0 | 40871.6766 | 42792.6454
CA0800825 | JED SMITH HOMEOWNERS ASSN. | DEL NORTE | 58 | 27 | Some | 8700 | 13.5938 | 34769.4688 | 36507.9422 | 0 | 0 | 36507.9422 | 38223.8155
CA3900732 | V & P TRAILER COURT WATER SYSTEM | SAN JOAQUIN | 35 | 15 |  | 5250 | 8.2031 | 32931.2656 | 34577.8289 | 0 | 0 | 34577.8289 | 36202.9869
CA0400091 | DEL ORO WATER COMPANY - BUZZTAIL DIST. | BUTTE | 99 | 30 | None | 14850 | 23.2031 | 38046.2656 | 39948.5789 | 0 | 0 | 39948.5789 | 41826.1621
CA5210001 | CITY OF CORNING | TEHAMA | 7663 | 2378 | Some | 1149450 | 1796.0156 | 642575.3281 | 674704.0945 | 0 | 0 | 674704.0945 | 706415.187
CA4410008 | MT. HERMON ASSOCIATION, INC. | SANTA CRUZ | 2850 | 494 | Some | 427500 | 667.9688 | 257911.3438 | 270806.9109 | 0.3 | 77373.4031 | 348180.3141 | 364544.7888
CA5510002 | TUD - PONDEROSA | TUOLUMNE | 1647 | 640 |  | 247050 | 386.0156 | 161765.3281 | 169853.5945 | 0 | 0 | 169853.5945 | 177836.7135
CA5200545 | MODERN VILLAGE MWC | TEHAMA | 85 | 19 |  | 12750 | 19.9219 | 36927.3594 | 38773.7273 | 0 | 0 | 38773.7273 | 40596.0925
CA3600010 | LIBERTY UTILITIES APPLE VALLEY | SAN BERNARDINO | 170 | 50 | None | 25500 | 39.8438 | 43720.7188 | 45906.7547 | 0.3 | 13116.2156 | 59022.9703 | 61797.0499
CA4510008 | FALL RIVER VALLEY CSD | SHASTA | 1535 | 482 | Some | 230250 | 359.7656 | 152814.0781 | 160454.782 | 0 | 0 | 160454.782 | 167996.1568
CA3610063 | GOLDEN STATE WATER CO - MORONGO DEL SUR | SAN BERNARDINO | 1748 | 818 | Some | 262200 | 409.6875 | 169837.4375 | 178329.3094 | 0.3 | 50951.2312 | 229280.5406 | 240056.726
CA5400505 | HARTLAND CHRISTIAN CAMP | TULARE | 250 | 54 |  | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 55093.3412
CA4810021 | CITY OF VALLEJO-LAKES SYSTEM | SOLANO | 2800 | 854 | None | 420000 | 656.25 | 253915.25 | 266611.0125 | 0.3 | 76174.575 | 342785.5875 | 358896.5101
CA4500203 | RAPID RIVER MOBILEHOME PARK | SHASTA | 92 | 44 |  | 13800 | 21.5625 | 37486.8125 | 39361.1531 | 0 | 0 | 39361.1531 | 41211.1273
CA4900723 | SHAMROCK MOBILE HOME PARK | SONOMA | 188 | 127 | None | 28200 | 44.0625 | 45159.3125 | 47417.2781 | 0.3 | 13547.7938 | 60965.0719 | 63830.4303
CA4000802 | SANTA YSABEL RANCH MWC | SAN LUIS OBISPO | 238 | 151 |  | 35700 | 55.7812 | 49155.4062 | 51613.1766 | 0.3 | 14746.6219 | 66359.7984 | 69478.709
CA3301380 | SAINT ANTHONY TRAILER PARK | RIVERSIDE | 340 | 68 |  | 51000 | 79.6875 | 57307.4375 | 60172.8094 | 0.32 | 18338.38 | 78511.1894 | 82201.2153
CA4900553 | PARK ROYAL MUTUAL WATER COMPANY | SONOMA | 75 | 27 | None | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0.3 | 10838.4422 | 48772.9898 | 51065.3204
CA2900541 | CHRISTIAN ENCOUNTER MINISTRIES | NEVADA | 35 | 16 | None | 5250 | 8.2031 | 32931.2656 | 34577.8289 | 0 | 0 | 34577.8289 | 36202.9869
CA3301491 | ALPINE VILLAGE | RIVERSIDE | 198 | 60 | Some | 29700 | 46.4062 | 45958.5312 | 48256.4578 | 0.32 | 14706.73 | 62963.1878 | 65922.4576
CA3301676 | THOMAS MOUNTAIN WATER COMPANY | RIVERSIDE | 162 | 57 | Some | 24300 | 37.9688 | 43081.3438 | 45235.4109 | 0.32 | 13786.03 | 59021.4409 | 61795.4487
CA4300522 | LAKE CANYON MUTUAL WATER COMPANY | SANTA CLARA | 156 | 56 | None | 23400 | 36.5625 | 42601.8125 | 44731.9031 | 0.32 | 13632.58 | 58364.4831 | 61107.6138
CA2000690 | MD 73 QUARTZ MOUNTAIN | MADERA | 375 | 127 |  | 56250 | 87.8906 | 60104.7031 | 63109.9383 | 0 | 0 | 63109.9383 | 66076.1054
CA2600714 | WHEELER CREST CSD | MONO | 86 | 43 |  | 12900 | 20.1562 | 37007.2812 | 38857.6453 | 0 | 0 | 38857.6453 | 40683.9546
CA2210001 | MARIPOSA PUBLIC UTILITY DIST | MARIPOSA | 2000 | 677 | Some | 300000 | 468.75 | 189977.75 | 199476.6375 | 0 | 0 | 199476.6375 | 208852.0395
CA5000313 | BUEHNER WATER SYSTEM | STANISLAUS | 150 | 50 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA1900146 | SUNNYSIDE FARMS MUTUAL WATER COMPANY | LOS ANGELES | 326 | 158 | None | 48900 | 76.4062 | 56188.5312 | 58997.9578 | 0.32 | 17980.33 | 76978.2878 | 80596.2673
CA1000213 | HARRIS FARMS/HORSE BARN | FRESNO | 100 | 20 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA5400537 | LINDYS LANDING | TULARE | 49 | 177 | None | 7350 | 11.4844 | 34050.1719 | 35752.6805 | 0 | 0 | 35752.6805 | 37433.0565
CA3610046 | VALLEY VIEW PARK MWC | SAN BERNARDINO | 499 | 218 | None | 74850 | 116.9531 | 70015.0156 | 73515.7664 | 0.3 | 21004.5047 | 94520.2711 | 98962.7238
CA1500459 | LAKE OF THE WOODS MOBILE VILLAGE | KERN | 82 | 86 | None | 12300 | 19.2188 | 36687.5938 | 38521.9734 | 0 | 0 | 38521.9734 | 40332.5062
CA3310048 | COACHELLA VWD: I.D. NO. 8 | RIVERSIDE | 4300 | 1603 | Some | 645000 | 1007.8125 | 373798.0625 | 392487.9656 | 0.32 | 119615.38 | 512103.3456 | 536172.2029
CA3301226 | MWD - EAGLE MOUNTAIN | RIVERSIDE | 16 | 25 | None | 2400 | 3.75 | 31412.75 | 32983.3875 | 0.32 | 10052.08 | 43035.4675 | 45058.1345
CA3710036 | BORREGO WD | SAN DIEGO | 3429 | 2033 | Some | 514350 | 803.6719 | 304186.1094 | 319395.4148 | 0.32 | 97339.555 | 416734.9698 | 436321.5134
CA5500040 | BLUEBELL VALLEY MWC | TUOLUMNE | 282 | 91 | Some | 42300 | 66.0938 | 52671.9688 | 55305.5672 | 0 | 0 | 55305.5672 | 57904.9288
CA4500015 | SHASTA CSA - CASTELLA, #3 | SHASTA | 252 | 101 | None | 37800 | 59.0625 | 50274.3125 | 52788.0281 | 0 | 0 | 52788.0281 | 55269.0654
CA2701046 | CAMPHORA APARTMENTS | MONTEREY | 126 | 42 | None | 18900 | 29.5312 | 40204.1562 | 42214.3641 | 0.3 | 12061.2469 | 54275.6109 | 56826.5647
CA1510801 | WASCO ST. PRISON RECEPTION CTR | KERN | 6068 | 1768 | Some | 910200 | 1422.1875 | 515099.9375 | 540854.9344 | 0 | 0 | 540854.9344 | 566275.1163
CA4000554 | GREEN RIVER MUTUAL WATER CO. | SAN LUIS OBISPO | 350 | 124 | None | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0.3 | 17431.9969 | 78443.9859 | 82130.8533
CA4200702 | VIEJA MUTUAL WATER COMPANY | SANTA BARBARA | 60 | 26 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA2410008 | CAL AM - MEADOWBROOK | MERCED | 5650 | 1713 | None | 847500 | 1324.2188 | 481692.5938 | 505777.2234 | 0 | 0 | 505777.2234 | 529548.7529
CA1500380 | DE RANCHO Y MOBILE VILLA WATER | KERN | 200 | 90 | Some | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA4410018 | CENTRAL WATER DISTRICT | SANTA CRUZ | 2715 | 817 | Some | 407250 | 636.3281 | 247121.8906 | 259477.9852 | 0.3 | 74136.5672 | 333614.5523 | 349294.4363
CA1910050 | COMMERCE-CITY, WATER DEPT. | LOS ANGELES | 4203 | 991 | Some | 630450 | 985.0781 | 366045.6406 | 384347.9227 | 0.32 | 117134.605 | 501482.5277 | 525052.2065
CA1510042 | MOUNTAIN MESA WC | KERN | 777 | 375 | NULL | 116550 | 182.1094 | 92233.2969 | 96844.9617 | 0 | 0 | 96844.9617 | 101396.6749
CA3600009 | APPLE VALLEY HEIGHTS CWD | SAN BERNARDINO | 986 | 296 | None | 147900 | 231.0938 | 108936.9688 | 114383.8172 | 0.3 | 32681.0906 | 147064.9078 | 153976.9585
CA3710700 | CAMP PENDLETON (NORTH) | SAN DIEGO | 26355 | 1605 | Some | 3953250 | 6176.9531 | 2136475.0156 | 2243298.7664 | 0.32 | 683672.005 | 2926970.7714 | 3064538.3977
CA4300577 | RANCHO ROBLES MUTUAL WATER COMPANY | SANTA CLARA | 103 | 37 | None | 15450 | 24.1406 | 38365.9531 | 40284.2508 | 0.32 | 12277.105 | 52561.3558 | 55031.7395
CA3500509 | TRES PINOS CWD | SAN BENITO | 350 | 121 | None | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0.3 | 17431.9969 | 78443.9859 | 82130.8533
CA3702354 | WARNER SPRINGS ESTATES | SAN DIEGO | 443 | 307 | Some | 66450 | 103.8281 | 65539.3906 | 68816.3602 | 0.32 | 20972.605 | 89788.9652 | 94009.0465
CA1000445 | LINDA VISTA FARMS | FRESNO | 63 | 17 | None | 9450 | 14.7656 | 35169.0781 | 36927.532 | 0 | 0 | 36927.532 | 38663.126
CA5200508 | RIO VISTA MOBILE HOME PARK | TEHAMA | 543 | 195 |  | 81450 | 127.2656 | 73531.5781 | 77208.157 | 0 | 0 | 77208.157 | 80836.9404
CA4500173 | CASSEL PARK MUTUAL WATER CO | SHASTA | 131 | 71 | None | 19650 | 30.7031 | 40603.7656 | 42633.9539 | 0 | 0 | 42633.9539 | 44637.7497
CA4000805 | CALLENDER GROVE MUTUAL WATER | SAN LUIS OBISPO | 30 | 37 |  | 4500 | 7.0312 | 32531.6562 | 34158.2391 | 0.3 | 9759.4969 | 43917.7359 | 45981.8695
CA1910249 | WHITE FENCE FARMS MWC NO. 1 | LOS ANGELES | 1362 | 454 | Some | 204300 | 319.2188 | 138987.5938 | 145936.9734 | 0.32 | 44476.03 | 190413.0034 | 199362.4146
CA5410025 | WOODVILLE PUBLIC UTILITY DIST | TULARE | 1673 | 467 | Some | 250950 | 392.1094 | 163843.2969 | 172035.4617 | 0 | 0 | 172035.4617 | 180121.1284
CA4900644 | BRIDGEHAVEN PARK | SONOMA | 70 | 31 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0.3 | 10718.5594 | 48233.5172 | 50500.4925
CA4910016 | COTATI, CITY OF | SONOMA | 7653 | 2669 | Some | 1147950 | 1793.6719 | 641776.1094 | 673864.9148 | 0.3 | 192532.8328 | 866397.7477 | 907118.4418
CA1010035 | DEL REY COMMUNITY SERV DIST | FRESNO | 1500 | 312 | Some | 225000 | 351.5625 | 150016.8125 | 157517.6531 | 0 | 0 | 157517.6531 | 164920.9828
CA0600008 | COLUSA CO. WWD #1 - GRIMES | COLUSA | 305 | 123 | Some | 45750 | 71.4844 | 54510.1719 | 57235.6805 | 0 | 0 | 57235.6805 | 59925.7575
CA2700523 | CALERA CANYON HEIGHTS HOA | MONTEREY | 74 | 17 | None | 11100 | 17.3438 | 36048.2188 | 37850.6297 | 0.3 | 10814.4656 | 48665.0953 | 50952.3548
CA5400666 | DEL ORO GRANDVIEW GARDENS DISTRICT | TULARE | 327 | 98 | None | 49050 | 76.6406 | 56268.4531 | 59081.8758 | 0 | 0 | 59081.8758 | 61858.7239
CA5601201 | LIMONEIRA RANCH #1 | VENTURA | 832 | 232 |  | 124800 | 195 | 96629 | 101460.45 | 0.32 | 30921.28 | 132381.73 | 138603.6713
CA2701926 | MORO RD WS #09 | MONTEREY | 210 | 65 | None | 31500 | 49.2188 | 46917.5938 | 49263.4734 | 0.3 | 14075.2781 | 63338.7516 | 66315.6729
CA2000728 | MD 37 LA VINA | MADERA | 350 | 100 |  | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0 | 0 | 61011.9891 | 63879.5525
CA5000055 | OLIVE LANE MOBILEHOME PARK | STANISLAUS | 153 | 51 |  | 22950 | 35.8594 | 42362.0469 | 44480.1492 | 0 | 0 | 44480.1492 | 46570.7162
CA0707573 | DELTA MUTUAL WATER COMPANY | CONTRA COSTA | 225 | 119 |  | 33750 | 52.7344 | 48116.4219 | 50522.243 | 0.3 | 14434.9266 | 64957.1695 | 68010.1565
CA4000563 | HIGUERA APARTMENTS | SAN LUIS OBISPO | 30 | 24 |  | 4500 | 7.0312 | 32531.6562 | 34158.2391 | 0.3 | 9759.4969 | 43917.7359 | 45981.8695
CA1500591 | SWEET WATER CO-OP | KERN | 47 | 15 | None | 7050 | 11.0156 | 33890.3281 | 35584.8445 | 0 | 0 | 35584.8445 | 37257.3322
CA1910053 | HEMLOCK MUTUAL WATER CO. | LOS ANGELES | 686 | 208 | None | 102900 | 160.7812 | 84960.4062 | 89208.4266 | 0.32 | 27187.33 | 116395.7566 | 121866.3571
CA1910247 | SANTA CLARITA VALLEY W.A.-CASTAIC DIV. | LOS ANGELES | 9820 | 1910 | Some | 1473000 | 2301.5625 | 814966.8125 | 855715.1531 | 0.32 | 260789.38 | 1116504.5331 | 1168980.2462
CA1910250 | SANTA CLARITA VALLEY W.A.-PINETREE DIV. | LOS ANGELES | 15219 | 2821 | Some | 2282850 | 3566.9531 | 1246465.0156 | 1308788.2664 | 0.32 | 398868.805 | 1707657.0714 | 1787916.9538
CA2000865 | MD 58 SIERRA HIGHLANDS | MADERA | 75 | 25 |  | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0 | 0 | 37934.5477 | 39717.4714
CA4510011 | CENTERVILLE C.S.D. | SHASTA | 4211 | 1257 | Some | 631650 | 986.9531 | 366685.0156 | 385019.2664 | 0 | 0 | 385019.2664 | 403115.1719
CA1000057 | DEL ORO WATER CO - METROPOLITAN DISTRICT | FRESNO | 96 | 29 | None | 14400 | 22.5 | 37806.5 | 39696.825 | 0 | 0 | 39696.825 | 41562.5758
CA2300644 | WOODSIDE RV PARK | MENDOCINO | 280 | 58 | NULL | 42000 | 65.625 | 52512.125 | 55137.7312 | 0 | 0 | 55137.7312 | 57729.2046
CA4901445 | JAMES COURT WATER SYSTEM | SONOMA | 205 | 40 | None | 30750 | 48.0469 | 46517.9844 | 48843.8836 | 0.3 | 13955.3953 | 62799.2789 | 65750.845
CA2000688 | ECCO | MADERA | 100 | 15 | Some | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA2701403 | PINE ST WS #01 | MONTEREY | 36 | 17 | None | 5400 | 8.4375 | 33011.1875 | 34661.7469 | 0.3 | 9903.3563 | 44565.1031 | 46659.663
CA4700551 | COPCO LAKE MWC | SISKIYOU | 181 | 61 |  | 27150 | 42.4219 | 44599.8594 | 46829.8523 | 0 | 0 | 46829.8523 | 49030.8554
CA2900530 | ROUGH & READY MOBILEHOME VILLAGE | NEVADA | 268 | 56 | None | 40200 | 62.8125 | 51553.0625 | 54130.7156 | 0 | 0 | 54130.7156 | 56674.8593
CA4010040 | GOLDEN STATE WATER COMPANY-CYPRESS RIDGE | SAN LUIS OBISPO | 2559 | 959 | Some | 383850 | 599.7656 | 234654.0781 | 246386.782 | 0.3 | 70396.2234 | 316783.0055 | 331671.8067
CA2410006 | DELHI CWD | MERCED | 7784 | 2303 | Some | 1167600 | 1824.375 | 652245.875 | 684858.1687 | 0 | 0 | 684858.1687 | 717046.5027
CA3303003 | GALINDO HOUSING FACILITY | RIVERSIDE | 50 | 38 |  | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0.32 | 10921.63 | 46758.2284 | 48955.8652
CA1502449 | CYPRESS CANYON WATER SYSTEM | KERN | 44 | 16 |  | 6600 | 10.3125 | 33650.5625 | 35333.0906 | 0 | 0 | 35333.0906 | 36993.7459
CA4200851 | ROLLING HILLS MUTUAL WATER COMPANY | SANTA BARBARA | 66 | 21 | None | 9900 | 15.4688 | 35408.8438 | 37179.2859 | 0.3 | 10622.6531 | 47801.9391 | 50048.6302
CA2300596 | BIG RIVER VISTA MUTUAL WATER COMPANY | MENDOCINO | 36 | 19 |  | 5400 | 8.4375 | 33011.1875 | 34661.7469 | 0 | 0 | 34661.7469 | 36290.849
CA5400968 | IMPROVEMENT DISTRICT NO. 1 | TULARE | 200 | 80 |  | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA2300638 | WILDWOOD CAMPGROUND | MENDOCINO | 150 | 50 |  | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA1500543 | AGAPE MUTUAL WATER SYSTEM | KERN | 60 | 16 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 38399.5397
CA3610109 | SHEEP CREEK WATER COMPANY | SAN BERNARDINO | 3623 | 1191 | Some | 543450 | 849.1406 | 319690.9531 | 335675.5008 | 0.3 | 95907.2859 | 431582.7867 | 451867.1777
CA1910018 | BELLFLOWER MUNICIPAL WATER SYSTEM | LOS ANGELES | 5967 | 1826 | Some | 895050 | 1398.5156 | 507027.8281 | 532379.2195 | 0.32 | 162248.905 | 694628.1245 | 727275.6464
CA4210024 | LA CUMBRE MUTUAL WATER CO | SANTA BARBARA | 4861 | 1470 | Some | 729150 | 1139.2969 | 418634.2344 | 439565.9461 | 0.3 | 125590.2703 | 565156.2164 | 591718.5586
CA1910248 | LOS ANGELES CWWD 37-ACTON | LOS ANGELES | 6600 | 1484 | None | 990000 | 1546.875 | 557618.375 | 585499.2937 | 0.32 | 178437.88 | 763937.1737 | 799842.2209
CA4900667 | COLLEGE PARK MUTUAL WATER COMPANY | SONOMA | 237 | 72 |  | 35550 | 55.5469 | 49075.4844 | 51529.2586 | 0.3 | 14722.6453 | 66251.9039 | 69365.7434
CA4800531 | VACA VILLA APARTMENTS | SOLANO | 60 | 40 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA3600399 | PARADISE MOBILE ESTATES | SAN BERNARDINO | 190 | 38 | Some | 28500 | 44.5312 | 45319.1562 | 47585.1141 | 0.3 | 13595.7469 | 61180.8609 | 64056.3614
CA1500554 | EAST INYOKERN MUTUAL WATER | KERN | 87 | 28 | Some | 13050 | 20.3906 | 37087.2031 | 38941.5633 | 0 | 0 | 38941.5633 | 40771.8168
CA4300770 | THREE SPRINGS RANCH MUTUAL WATER COMPANY | SANTA CLARA | 110 | 33 | None | 16500 | 25.7812 | 38925.4062 | 40871.6766 | 0.32 | 12456.13 | 53327.8066 | 55834.2135
CA5500363 | TUD-WARDS FERRY RANCHES | TUOLUMNE | 63 | 23 | NULL | 9450 | 14.7656 | 35169.0781 | 36927.532 | 0 | 0 | 36927.532 | 38663.126
CA1800503 | SUSAN RIVER PARK WATER CO. | LASSEN | 140 | 50 | None | 21000 | 32.8125 | 41323.0625 | 43389.2156 | 0 | 0 | 43389.2156 | 45428.5088
CA3310082 | NORTH PERRIS WATER SYSTEM | RIVERSIDE | 4500 | 1389 | Some | 675000 | 1054.6875 | 389782.4375 | 409271.5594 | 0.32 | 124730.38 | 534001.9394 | 559100.0305
CA4210700 | AMERICAN WATER O&M, LLC - VAFB | SANTA BARBARA | 14971 | 1161 | Some | 2245650 | 3508.8281 | 1226644.3906 | 1287976.6102 | 0.3 | 367993.3172 | 1655969.9273 | 1733800.5139
CA2702003 | VIERRA MEADOWS MWC | MONTEREY | 65 | 25 | None | 9750 | 15.2344 | 35328.9219 | 37095.368 | 0.3 | 10598.6766 | 47694.0445 | 49935.6646
CA4400613 | LAS COLINAS ROAD & WATER ASSN | SANTA CRUZ | 70 | 24 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0.3 | 10718.5594 | 48233.5172 | 50500.4925
CA0400030 | GOLDEN FEATHER MHP | BUTTE | 275 | 101 | None | 41250 | 64.4531 | 52112.5156 | 54718.1414 | 0 | 0 | 54718.1414 | 57289.8941
CA5000008 | KNIGHTS FERRY COMM. SVC. DIST. | STANISLAUS | 168 | 67 | None | 25200 | 39.375 | 43560.875 | 45738.9187 | 0 | 0 | 45738.9187 | 47888.6479
CA3901217 | HAYNES BOARD & CARE HOME | SAN JOAQUIN | 41 | 15 | Some | 6150 | 9.6094 | 33410.7969 | 35081.3367 | 0 | 0 | 35081.3367 | 36730.1595
CA2700674 | PARADISE LAKE MUTUAL WATER CO. | MONTEREY | 180 | 76 | Some | 27000 | 42.1875 | 44519.9375 | 46745.9344 | 0.3 | 13355.9813 | 60101.9156 | 62926.7057
CA4100529 | CAMP LOMA MAR | SAN MATEO | 186 | 21 | None | 27900 | 43.5938 | 44999.4688 | 47249.4422 | 0.32 | 14399.83 | 61649.2722 | 64546.788
CA3410012 | CALAM - ISLETON | SACRAMENTO | 1581 | 480 | Some | 237150 | 370.5469 | 156490.4844 | 164315.0086 | 0.32 | 50076.955 | 214391.9636 | 224468.3859
CA4400642 | CATHEDRAL WOOD MUTUAL WATER COMPANY | SANTA CRUZ | 60 | 20 | Some | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA4000716 | AVILA VALLEY MUTUAL WATER CO | SAN LUIS OBISPO | 75 | 29 | Some | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0.3 | 10838.4422 | 48772.9898 | 51065.3204
CA1000484 | FCSA #34/ MILLERTON NEW TOWN | FRESNO | 1100 | 394 | None | 165000 | 257.8125 | 118048.0625 | 123950.4656 | 0 | 0 | 123950.4656 | 129776.1375
CA4900653 | LONE PINE MUTUAL WATER COMPANY | SONOMA | 65 | 28 | None | 9750 | 15.2344 | 35328.9219 | 37095.368 | 0.3 | 10598.6766 | 47694.0445 | 49935.6646
CA4700541 | CHATEAU SHASTA MOBILE HOME & RV PARK | SISKIYOU | 55 | 63 |  | 8250 | 12.8906 | 34529.7031 | 36256.1883 | 0 | 0 | 36256.1883 | 37960.2291
CA0600005 | COLUSA CO. SERVICE AREA #2-STONYFORD | COLUSA | 250 | 63 |  | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 55093.3412
CA3601010 | CRYSTAL LAKE PROPERTY OWNERS | SAN BERNARDINO | 213 | 59 | None | 31950 | 49.9219 | 47157.3594 | 49515.2273 | 0.3 | 14147.2078 | 63662.4352 | 66654.5696
CA1500485 | ANTELOPE VALLEY MOBILE ESTATES | KERN | 60 | 28 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 38399.5397
CA1910242 | CALIFORNIA WATER SERVICE CO-LAKE HUGHES | LOS ANGELES | 952 | 209 | None | 142800 | 223.125 | 106219.625 | 111530.6062 | 0.32 | 33990.28 | 145520.8863 | 152360.3679
CA0400040 | ALMOND GROVE MOBILE PARK | BUTTE | 250 | 175 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 55093.3412
CA0400023 | GOLDEN OAKS MOBILE ESTATES | BUTTE | 34 | 52 |  | 5100 | 7.9688 | 32851.3438 | 34493.9109 | 0 | 0 | 34493.9109 | 36115.1248
CA5400616 | LEMON COVE WATER CO | TULARE | 109 | 60 | None | 16350 | 25.5469 | 38845.4844 | 40787.7586 | 0 | 0 | 40787.7586 | 42704.7832
CA5601401 | KROTONA INSTITUTE | VENTURA | 31 | 31 | None | 4650 | 7.2656 | 32611.5781 | 34242.157 | 0.32 | 10435.705 | 44677.862 | 46777.7215
CA4100509 | COUNTY SERVICE AREA 7 | SAN MATEO | 300 | 68 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0.32 | 17315.38 | 74131.4706 | 77615.6497
CA3310019 | IDYLLWILD WATER DISTRICT | RIVERSIDE | 2500 | 1665 | Some | 375000 | 585.9375 | 229938.6875 | 241435.6219 | 0.32 | 73580.38 | 315016.0019 | 329821.754
CA4900843 | SONOMA RANCH MUTUAL WATER COMPANY | SONOMA | 178 | 54 | NULL | 26700 | 41.7188 | 44360.0938 | 46578.0984 | 0.3 | 13308.0281 | 59886.1266 | 62700.7745
CA4300525 | MELODY WOODS WATER COMPANY | SANTA CLARA | 168 | 51 | None | 25200 | 39.375 | 43560.875 | 45738.9187 | 0.32 | 13939.48 | 59678.3988 | 62483.2835
CA5200539 | FRIENDLY ACRES MHP | TEHAMA | 75 | 51 | None | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0 | 0 | 37934.5477 | 39717.4714
CA2010006 | MADERA CO SA3-PARKSDALE | MADERA | 1789 | 542 |  | 268350 | 419.2969 | 173114.2344 | 181769.9461 | 0 | 0 | 181769.9461 | 190313.1336
CA1910035 | KINNELOA IRRIGATION DIST. | LOS ANGELES | 1940 | 588 | Some | 291000 | 454.6875 | 185182.4375 | 194441.5594 | 0.32 | 59258.38 | 253699.9394 | 265623.8365
CA1910244 | GREEN VALLEY CWD | LOS ANGELES | 1190 | 499 | Some | 178500 | 278.9062 | 125241.0312 | 131503.0828 | 0.32 | 40077.13 | 171580.2128 | 179644.4828
CA3600152 | LOMA LINDA UNIVERSITY | SAN BERNARDINO | 8500 | 95 | Some | 1275000 | 1992.1875 | 709469.9375 | 744943.4344 | 0.3 | 212840.9813 | 957784.4156 | 1002800.2832
CA5800824 | COUNTRY VILLAGE MOBILE HOME PARK | YUBA | 50 | 45 | NULL | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA1100436 | ORLAND OAKS MHP | GLENN | 186 | 83 | Some | 27900 | 43.5938 | 44999.4688 | 47249.4422 | 0 | 0 | 47249.4422 | 49470.166
CA5510011 | COLD SPRINGS WATER CO | TUOLUMNE | 153 | 535 | Some | 22950 | 35.8594 | 42362.0469 | 44480.1492 | 0 | 0 | 44480.1492 | 46570.7162
CA2701929 | COUNTRY MEADOWS MWC | MONTEREY | 621 | 107 | Some | 93150 | 145.5469 | 79765.4844 | 83753.7586 | 0.3 | 23929.6453 | 107683.4039 | 112744.5239
CA4500006 | SHASTA CSA - SUGARLOAF, #2 | SHASTA | 160 | 61 | None | 24000 | 37.5 | 42921.5 | 45067.575 | 0 | 0 | 45067.575 | 47185.751
CA5410009 | PIXLEY PUBLIC UTIL DIST | TULARE | 2772 | 840 | None | 415800 | 649.6875 | 251677.4375 | 264261.3094 | 0 | 0 | 264261.3094 | 276681.5909
CA2700622 | OUTLOOK WA | MONTEREY | 45 | 18 | None | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0.3 | 10119.1453 | 45536.1539 | 47676.3531
CA4300912 | MECCHI WATER COMPANY | SANTA CLARA | 104 | 27 | None | 15600 | 24.375 | 38445.875 | 40368.1687 | 0.32 | 12302.68 | 52670.8487 | 55146.3786
CA0707576 | PLEASANTIMES MUTUAL WATER CO | CONTRA COSTA | 380 | 195 | Some | 57000 | 89.0625 | 60504.3125 | 63529.5281 | 0.3 | 18151.2938 | 81680.8219 | 85519.8205
CA1500584 | GOOSELAKE WATER COMPANY | KERN | 90 | 32 | None | 13500 | 21.0938 | 37326.9688 | 39193.3172 | 0 | 0 | 39193.3172 | 41035.4031
CA3400169 | SPINDRIFT MARINA | SACRAMENTO | 100 | 50 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.32 | 12200.38 | 52232.8769 | 54687.8221
CA3110026 | NEVADA ID - NORTH AUBURN | PLACER | 6719 | 2366 | Some | 1007850 | 1574.7656 | 567129.0781 | 595485.532 | 0 | 0 | 595485.532 | 623473.352
CA3610112 | HELENDALE COMMUNITY SERVICE DISTRICT | SAN BERNARDINO | 5849 | 2830 | None | 877350 | 1370.8594 | 497597.0469 | 522476.8992 | 0.3 | 149279.1141 | 671756.0133 | 703328.5459
CA5301102 | TRINITY KNOLLS MUTUAL WATER COMPANY | TRINITY | 338 | 66 | None | 50700 | 79.2188 | 57147.5938 | 60004.9734 | 0 | 0 | 60004.9734 | 62825.2072
CA4700549 | LAKE SISKIYOU M.W.C. | SISKIYOU | 240 | 84 | None | 36000 | 56.25 | 49315.25 | 51781.0125 | 0 | 0 | 51781.0125 | 54214.7201
CA1400099 | MOUNTAIN VIEW TRAILER COURT | INYO | 53 | 24 | None | 7950 | 12.4219 | 34369.8594 | 36088.3523 | 0 | 0 | 36088.3523 | 37784.5049
CA2600620 | MOUNTAIN MEADOWS MWC | MONO | 366 | 116 | Some | 54900 | 85.7812 | 59385.4062 | 62354.6766 | 0 | 0 | 62354.6766 | 65285.3464
CA2702554 | HIDDEN CANYON RANCH MWC | MONTEREY | 100 | 27 | Some | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.3 | 11437.8563 | 51470.3531 | 53889.4597
CA0910012 | TAHOE CITY PUD - RUBICON | EL DORADO | 703 | 625 | Some | 105450 | 164.7656 | 86319.0781 | 90635.032 | 0.3 | 25895.7234 | 116530.7555 | 122007.701
CA2700792 | SUMMERHILL MHP WS | MONTEREY | 95 | 34 | None | 14250 | 22.2656 | 37726.5781 | 39612.907 | 0.3 | 11317.9734 | 50930.8805 | 53324.6319
CA3310030 | PINE COVE WATER DISTRICT | RIVERSIDE | 1540 | 1107 | Some | 231000 | 360.9375 | 153213.6875 | 160874.3719 | 0.32 | 49028.38 | 209902.7519 | 219768.1812
CA2700740 | SAN MIGUEL WS #03 | MONTEREY | 45 | 16 | None | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0.3 | 10119.1453 | 45536.1539 | 47676.3531
CA5601122 | TICO MUTUAL WATER CO | VENTURA | 70 | 38 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0.32 | 11433.13 | 48948.0878 | 51248.6479
CA5510003 | TUD - TUOLUMNE WATER SYSTEM | TUOLUMNE | 1691 | 686 |  | 253650 | 396.3281 | 165281.8906 | 173545.9852 | 0 | 0 | 173545.9852 | 181702.6465
CA4900794 | SUNSET PARK COMMUNITY | SONOMA | 141 | 42 | None | 21150 | 33.0469 | 41402.9844 | 43473.1336 | 0.3 | 12420.8953 | 55894.0289 | 58521.0483
CA4900905 | MARK WEST MEADOWS MUTUAL WATER | SONOMA | 25 | 15 | None | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0.3 | 9639.6141 | 43378.2633 | 45417.0417
CA1500426 | ROSE VILLA APARTMENTS | KERN | 65 | 32 | None | 9750 | 15.2344 | 35328.9219 | 37095.368 | 0 | 0 | 37095.368 | 38838.8503
CA1500571 | KERN MOBILE ESTATES LLC | KERN | 73 | 60 | None | 10950 | 17.1094 | 35968.2969 | 37766.7117 | 0 | 0 | 37766.7117 | 39541.7472
CA1502232 | ROSAMOND MOBILEHOME PARK | KERN | 175 | 79 | None | 26250 | 41.0156 | 44120.3281 | 46326.3445 | 0 | 0 | 46326.3445 | 48503.6827
CA1910066 | LEISURE LAKE MOBILE ESTATES | LOS ANGELES | 325 | 211 | None | 48750 | 76.1719 | 56108.6094 | 58914.0398 | 0.32 | 17954.755 | 76868.7948 | 80481.6282
CA1900693 | DESERT PALMS MOBILE HOME PARK | LOS ANGELES | 140 | 56 | None | 21000 | 32.8125 | 41323.0625 | 43389.2156 | 0.32 | 13223.38 | 56612.5956 | 59273.3876
CA1900907 | SHERWOOD MOBILE HOME PARK | LOS ANGELES | 540 | 185 | None | 81000 | 126.5625 | 73291.8125 | 76956.4031 | 0.32 | 23453.38 | 100409.7831 | 105129.0429
CA3310017 | SOUTH MESA WC | RIVERSIDE | 11953 | 2978 | Some | 1792950 | 2801.4844 | 985440.1719 | 1034712.1805 | 0.32 | 315340.855 | 1350053.0355 | 1413505.5281
CA3110012 | AGATE BAY WATER COMPANY | PLACER | 2500 | 584 | NULL | 375000 | 585.9375 | 229938.6875 | 241435.6219 | 0 | 0 | 241435.6219 | 252783.0961
CA4300575 | TWIN VALLEY INC | SANTA CLARA | 317 | 96 | None | 47550 | 74.2969 | 55469.2344 | 58242.6961 | 0.32 | 17750.155 | 75992.8511 | 79564.5151
CA1900809 | LANDALE MUTUAL WATER COMPANY | LOS ANGELES | 752 | 172 | None | 112800 | 176.25 | 90235.25 | 94747.0125 | 0.32 | 28875.28 | 123622.2925 | 129432.5402
CA3500527 | VALENZUELA WATER SYSTEM | SAN BENITO | 55 | 17 | None | 8250 | 12.8906 | 34529.7031 | 36256.1883 | 0.3 | 10358.9109 | 46615.0992 | 48806.0089
CA3210011 | PLUMAS EUREKA CSD | PLUMAS | 1525 | 554 | Some | 228750 | 357.4219 | 152014.8594 | 159615.6023 | 0 | 0 | 159615.6023 | 167117.5357
CA4900787 | PLAZA MOBILE HOME PARK | SONOMA | 125 | 71 | None | 18750 | 29.2969 | 40124.2344 | 42130.4461 | 0.3 | 12037.2703 | 54167.7164 | 56713.5991
CA4900791 | WESTERN MOBILE HOME PARK | SONOMA | 225 | 73 |  | 33750 | 52.7344 | 48116.4219 | 50522.243 | 0.3 | 14434.9266 | 64957.1695 | 68010.1565
CA3301879 | SHARONDALE MESA HOA | RIVERSIDE | 330 | 244 | Some | 49500 | 77.3438 | 56508.2188 | 59333.6297 | 0.32 | 18082.63 | 77416.2597 | 81054.8239
CA5000058 | FISHERMAN'S BEND MHP | STANISLAUS | 120 | 66 | None | 18000 | 28.125 | 39724.625 | 41710.8562 | 0 | 0 | 41710.8562 | 43671.2665
CA1910099 | PARADISE RANCH MHP | LOS ANGELES | 345 | 95 | None | 51750 | 80.8594 | 57707.0469 | 60592.3992 | 0.32 | 18466.255 | 79058.6542 | 82774.411
CA1502247 | DESERT BREEZE MOBILE HOME ESTATES | KERN | 82 | 63 | Some | 12300 | 19.2188 | 36687.5938 | 38521.9734 | 0 | 0 | 38521.9734 | 40332.5062
CA4500098 | ANDERSON MOBILE HOME PARK | SHASTA | 70 | 21 |  | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0 | 0 | 37514.9578 | 39278.1608
CA1502663 | TOWN & COUNTRY WATER COMPANY | KERN | 73 | 22 |  | 10950 | 17.1094 | 35968.2969 | 37766.7117 | 0 | 0 | 37766.7117 | 39541.7472
CA2701676 | SAN LUCAS WD | MONTEREY | 315 | 98 | None | 47250 | 73.8281 | 55309.3906 | 58074.8602 | 0.3 | 16592.8172 | 74667.6773 | 78177.0582
CA4300563 | MT. PLEASANT WATER USERS ASSOCIATION | SANTA CLARA | 300 | 90 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0.32 | 17315.38 | 74131.4706 | 77615.6497
CA0409183 | SIERRA MOON WATER COMPANY | BUTTE | 120 | 86 | Some | 18000 | 28.125 | 39724.625 | 41710.8562 | 0 | 0 | 41710.8562 | 43671.2665
CA0400090 | MOUNTAIN VILLAGE HOMEOWNER'S ASSOC | BUTTE | 40 | 17 | Some | 6000 | 9.375 | 33330.875 | 34997.4187 | 0 | 0 | 34997.4187 | 36642.2974
CA5610015 | VENTURA CWWD NO. 19 - SOMIS | VENTURA | 3275 | 1085 | Some | 491250 | 767.5781 | 291878.1406 | 306472.0477 | 0.32 | 93401.005 | 399873.0527 | 418667.0861
CA1900046 | PETER PITCHESS HONOR RANCHO DETN. CTR | LOS ANGELES | 7000 | 1952 | Some | 1050000 | 1640.625 | 589587.125 | 619066.4812 | 0.32 | 188667.88 | 807734.3612 | 845697.8762
CA2702439 | WOODLAND HEIGHTS MWC | MONTEREY | 57 | 37 | None | 8550 | 13.3594 | 34689.5469 | 36424.0242 | 0.3 | 10406.8641 | 46830.8883 | 49031.94
CA1910195 | GSWC - HOLLYDALE | LOS ANGELES | 7691 | 1663 | Some | 1153650 | 1802.5781 | 644813.1406 | 677053.7977 | 0.32 | 206340.205 | 883394.0027 | 924913.5208
CA3910018 | SAN JOAQUIN RIVER CLUB INC | SAN JOAQUIN | 600 | 385 | None | 90000 | 140.625 | 78087.125 | 81991.4812 | 0 | 0 | 81991.4812 | 85845.0809
CA4900568 | VALLEY FORD WATER ASSOCIATION | SONOMA | 61 | 23 | None | 9150 | 14.2969 | 35009.2344 | 36759.6961 | 0.3 | 10502.7703 | 47262.4664 | 49483.8023
CA2700992 | MILLER'S LODGE WS | MONTEREY | 25 | 51 | None | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0.3 | 9639.6141 | 43378.2633 | 45417.0417
CA5200007 | HOWELL'S LAKESIDE WATER CO. | TEHAMA | 75 | 55 | None | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0 | 0 | 37934.5477 | 39717.4714
CA1502465 | PANAMA ROAD PROPERTY OWNERS ASSOC | KERN | 45 | 16 |  | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0 | 0 | 35417.0086 | 37081.608
CA3310033 | SANTA ANA RIVER WATER COMPANY | RIVERSIDE | 6774 | 2050 | None | 1016100 | 1587.6562 | 571524.7812 | 600101.0203 | 0.32 | 182887.93 | 782988.9503 | 819789.431
CA3210006 | LAKE ALMANOR COUNTRY CLUB MWC | PLUMAS | 6000 | 1688 | Some | 900000 | 1406.25 | 509665.25 | 535148.5125 | 0 | 0 | 535148.5125 | 560300.4926
CA2000512 | EAST ACRES MUTUAL WATER COMPANY | MADERA | 250 | 85 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 55093.3412
CA2000724 | SA 14 CHUK CHANSE SUBDIVISION | MADERA | 100 | 31 |  | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA4500101 | LAKE SHASTA PINES RV PARK & CAMPGROUND | SHASTA | 121 | 50 |  | 18150 | 28.3594 | 39804.5469 | 41794.7742 | 0 | 0 | 41794.7742 | 43759.1286
CA3010047 | GOLDEN STATE WC - COWAN HEIGHTS | ORANGE | 7236 | 2526 | Some | 1085400 | 1695.9375 | 608448.6875 | 638871.1219 | 0.3 | 182534.6063 | 821405.7281 | 860011.7973
CA4200703 | EL CAPITAN MUTUAL WATER COMPANY | SANTA BARBARA | 325 | 28 | Some | 48750 | 76.1719 | 56108.6094 | 58914.0398 | 0.3 | 16832.5828 | 75746.6227 | 79306.7139
CA5000005 | CROWS LANDING COMM SVC DISTRICT | STANISLAUS | 500 | 138 | None | 75000 | 117.1875 | 70094.9375 | 73599.6844 | 0 | 0 | 73599.6844 | 77058.8695
CA5500193 | TAMARRON MOBILE HOME PARK | TUOLUMNE | 225 | 100 | None | 33750 | 52.7344 | 48116.4219 | 50522.243 | 0 | 0 | 50522.243 | 52896.7884
CA1700546 | CLEAR WATER MUTUAL WATER COMPANY | LAKE | 252 | 89 | None | 37800 | 59.0625 | 50274.3125 | 52788.0281 | 0 | 0 | 52788.0281 | 55269.0654
CA2700682 | PARADISE RD WS #09 | MONTEREY | 206 | 17 |  | 30900 | 48.2812 | 46597.9062 | 48927.8016 | 0.3 | 13979.3719 | 62907.1734 | 65863.8106
CA2810002 | CALISTOGA, CITY OF | NAPA | 5610 | 1497 |  | 841500 | 1314.8438 | 478495.7188 | 502420.5047 | 0.3 | 143548.7156 | 645969.2203 | 676329.7737
CA4710009 | WEED, CITY OF | SISKIYOU | 2963 | 1110 |  | 444450 | 694.4531 | 266942.5156 | 280289.6414 | 0 | 0 | 280289.6414 | 293463.2546
CA1010006 | CITY OF FOWLER | FRESNO | 6600 | 1920 | Some | 990000 | 1546.875 | 557618.375 | 585499.2937 | 0 | 0 | 585499.2937 | 613017.7606
CA3210003 | CITY OF PORTOLA | PLUMAS | 1970 | 1153 | Some | 295500 | 461.7188 | 187580.0938 | 196959.0984 | 0 | 0 | 196959.0984 | 206216.1761
CA1000551 | FCSA #43/RAISIN CITY | FRESNO | 190 | 68 | None | 28500 | 44.5312 | 45319.1562 | 47585.1141 | 0 | 0 | 47585.1141 | 49821.6144
CA2010004 | MADERA CO CMD19-PARKWOOD | MADERA | 1637 | 496 |  | 245550 | 383.6719 | 160966.1094 | 169014.4148 | 0 | 0 | 169014.4148 | 176958.0923
CA4210020 | SANTA YNEZ RIVER WATER CONS. DIST. ID#1 | SANTA BARBARA | 6737 | 2600 | Some | 1010550 | 1578.9844 | 568567.6719 | 596996.0555 | 0.3 | 170570.3016 | 767566.357 | 803641.9758
CA5110007 | SUTTER COMMUNITY S.D. | SUTTER | 2904 | 1080 | Some | 435600 | 680.625 | 262227.125 | 275338.4813 | 0 | 0 | 275338.4813 | 288279.3899
CA2000554 | MD 33 FAIRMEAD | MADERA | 568 | 164 |  | 85200 | 133.125 | 75529.625 | 79306.1062 | 0 | 0 | 79306.1062 | 83033.4932
CA3301588 | ROYAL CARRIZO HOA | RIVERSIDE | 25 | 20 | None | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0.32 | 10282.255 | 44020.9042 | 46089.8867
CA5210005 | RIO ALTO WATER DISTRICT | TEHAMA | 3329 | 1378 | Some | 499350 | 780.2344 | 296193.9219 | 311003.618 | 0 | 0 | 311003.618 | 325620.788
CA4900789 | BLUE SPRUCE MOBILE HOME PARK | SONOMA | 90 | 56 | None | 13500 | 21.0938 | 37326.9688 | 39193.3172 | 0.3 | 11198.0906 | 50391.4078 | 52759.804
CA5401026 | DEER MEADOW MUTUAL WATER COMPANY | TULARE | 67 | 25 | None | 10050 | 15.7031 | 35488.7656 | 37263.2039 | 0 | 0 | 37263.2039 | 39014.5745
CA3301541 | RECHE CANYON MUTUAL WATER CO. | RIVERSIDE | 150 | 53 |  | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0.32 | 13479.13 | 57707.5253 | 60419.779
CA1900541 | WESTERN SKIES MOBILE HOME PARK | LOS ANGELES | 198 | 61 |  | 29700 | 46.4062 | 45958.5312 | 48256.4578 | 0.32 | 14706.73 | 62963.1878 | 65922.4576
CA5500096 | SIERRA TWAIN HARTE MHP | TUOLUMNE | 129 | 46 | None | 19350 | 30.2344 | 40443.9219 | 42466.118 | 0 | 0 | 42466.118 | 44462.0255
CA1910167 | VERNON-CITY, WATER DEPT. | LOS ANGELES | 28000 | 1077 | Some | 4200000 | 6562.5 | 2267946.5 | 2381343.825 | 0.32 | 725742.88 | 3107086.705 | 3253119.7801
CA4901246 | DOWNTOWN GRATON MUTUAL WATER SYSTEM | SONOMA | 118 | 24 | None | 17700 | 27.6562 | 39564.7812 | 41543.0203 | 0.3 | 11869.4344 | 53412.4547 | 55922.8401
CA5610702 | U.S.N., SAN NICOLAS ISLAND | VENTURA | 187 | 106 |  | 28050 | 43.8281 | 45079.3906 | 47333.3602 | 0.32 | 14425.405 | 61758.7652 | 64661.4271
CA3600504 | KNOLL ENTERPRISES | SAN BERNARDINO | 500 | 25 | Some | 75000 | 117.1875 | 70094.9375 | 73599.6844 | 0.3 | 21028.4813 | 94628.1656 | 99075.6894
CA1010053 | SHAVER LAKE HEIGHTS MWC | FRESNO | 1230 | 220 | None | 184500 | 288.2812 | 128437.9062 | 134859.8016 | 0 | 0 | 134859.8016 | 141198.2122
CA2000502 | BASS LAKE HEIGHTS MUTUAL WATER | MADERA | 250 | 90 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 55093.3412
CA5800803 | LOMA RICA WATER COMPANY | YUBA | 200 | 70 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA4500066 | CLEAR CREEK MOBILE PARK | SHASTA | 75 | 40 | None | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0 | 0 | 37934.5477 | 39717.4714
CA5510008 | LAKE DON PEDRO CSD | TUOLUMNE | 3240 | 1492 | None | 486000 | 759.375 | 289080.875 | 303534.9188 | 0 | 0 | 303534.9188 | 317801.0599
CA4901355 | TERRACE VIEW WATER SYSTEM | SONOMA | 60 | 16 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA1010051 | FCWWD #18/FRIANT | FRESNO | 772 | 251 | None | 115800 | 180.9375 | 91833.6875 | 96425.3719 | 0 | 0 | 96425.3719 | 100957.3644
CA3900559 | WINE COUNTRY APARTMENTS | SAN JOAQUIN | 40 | 16 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0 | 0 | 34997.4187 | 36642.2974
CA5000263 | OASIS INVESTMENTS | STANISLAUS | 75 | 31 | Some | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0 | 0 | 37934.5477 | 39717.4714
CA3900983 | CHERRY LANE TRAILER PARK | SAN JOAQUIN | 100 | 43 | Some | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA3901114 | KING ISLAND TRAILER PARK WATER SYSTEM | SAN JOAQUIN | 200 | 76 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA2710019 | CWSC OAK HILLS | MONTEREY | 3986 | 885 | Some | 597900 | 934.2188 | 348702.5938 | 366137.7234 | 0.3 | 104610.7781 | 470748.5016 | 492873.6811
CA2700511 | NORMCO WC | MONTEREY | 928 | 272 | None | 139200 | 217.5 | 104301.5 | 109516.575 | 0.3 | 31290.45 | 140807.025 | 147424.9552
CA4200619 | SANTA YNEZ RANCHO ESTATES | SANTA BARBARA | 304 | 92 |  | 45600 | 71.25 | 54430.25 | 57151.7625 | 0.3 | 16329.075 | 73480.8375 | 76934.4369
CA4300543 | WEST SAN MARTIN WATER WORKS INC | SANTA CLARA | 1173 | 317 | Some | 175950 | 274.9219 | 123882.3594 | 130076.4773 | 0.32 | 39642.355 | 169718.8323 | 177695.6175
CA5200008 | BREESE SUBDIVISION 2 | TEHAMA | 75 | 30 | None | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0 | 0 | 37934.5477 | 39717.4714
CA3400164 | VIEIRA'S RESORT, INC | SACRAMENTO | 150 | 107 | Some | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0.32 | 13479.13 | 57707.5253 | 60419.779
CA3900701 | CURRIER ESTATES WATER CORP | SAN JOAQUIN | 148 | 37 | Some | 22200 | 34.6875 | 41962.4375 | 44060.5594 | 0 | 0 | 44060.5594 | 46131.4057
CA4210013 | SOLVANG WATER DIVISION | SANTA BARBARA | 5792 | 2190 | Some | 868800 | 1357.5 | 493041.5 | 517693.575 | 0.3 | 147912.45 | 665606.025 | 696889.5082
CA5000072 | MULBERRY MHP | STANISLAUS | 148 | 53 | None | 22200 | 34.6875 | 41962.4375 | 44060.5594 | 0 | 0 | 44060.5594 | 46131.4057
CA3301529 | RAMONA WATER COMPANY | RIVERSIDE | 250 | 95 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0.32 | 16036.63 | 68656.8222 | 71883.6928
CA1500569 | VALLEY VIEW ESTATES MUTUAL WATER CO | KERN | 94 | 50 | None | 14100 | 22.0312 | 37646.6562 | 39528.9891 | 0 | 0 | 39528.9891 | 41386.8515
CA1500525 | LAKEVIEW RANCHOS MUTUAL WATER COMPANY | KERN | 120 | 71 | Some | 18000 | 28.125 | 39724.625 | 41710.8562 | 0 | 0 | 41710.8562 | 43671.2665
CA3310802 | CHUCKAWALLA VALLEY STATE PRISON | RIVERSIDE | 6507 | 1864 | Some | 976050 | 1525.0781 | 550185.6406 | 577694.9227 | 0.32 | 176059.405 | 753754.3277 | 789180.7811
CA1500374 | CWS-GRAND OAKS WATER SYSTEM | KERN | 149 | 45 | None | 22350 | 34.9219 | 42042.3594 | 44144.4773 | 0 | 0 | 44144.4773 | 46219.2678
CA5200558 | RIVER VIEW MHC LLC | TEHAMA | 100 | 55 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA2700709 | RANCHO BORROMEO MWS | MONTEREY | 100 | 36 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.3 | 11437.8563 | 51470.3531 | 53889.4597
CA5500080 | TWAIN HARTE VALLEY MWC | TUOLUMNE | 202 | 106 |  | 30300 | 47.3438 | 46278.2188 | 48592.1297 | 0 | 0 | 48592.1297 | 50875.9598
CA5000054 | MORNINGSIDE MOBILEHOME PARK | STANISLAUS | 67 | 49 | None | 10050 | 15.7031 | 35488.7656 | 37263.2039 | 0 | 0 | 37263.2039 | 39014.5745
CA2310001 | FORT BRAGG, CITY OF | MENDOCINO | 7250 | 2951 | Some | 1087500 | 1699.2188 | 609567.5938 | 640045.9734 | 0 | 0 | 640045.9734 | 670128.1342
CA5610068 | CLOVERDALE MUTUAL WATER CO. | VENTURA | 455 | 150 |  | 68250 | 106.6406 | 66498.4531 | 69823.3758 | 0.32 | 21279.505 | 91102.8808 | 95384.7162
CA2700669 | ORCHARD LN WS #02 | MONTEREY | 32 | 16 | None | 4800 | 7.5 | 32691.5 | 34326.075 | 0.3 | 9807.45 | 44133.525 | 46207.8007
CA2710006 | CAL AM WATER COMPANY - AMBLER PARK | MONTEREY | 980 | 412 | Some | 147000 | 229.6875 | 108457.4375 | 113880.3094 | 0.3 | 32537.2313 | 146417.5406 | 153299.165
CA1910243 | CALIFORNIA WATER SERVICE CO-LEONA VALLEY | LOS ANGELES | 900 | 429 | None | 135000 | 210.9375 | 102063.6875 | 107166.8719 | 0.32 | 32660.38 | 139827.2519 | 146399.1327
CA1100203 | ARTOIS COMMUNITY S.D. | GLENN | 198 | 58 | Some | 29700 | 46.4062 | 45958.5312 | 48256.4578 | 0 | 0 | 48256.4578 | 50524.5113
CA1100444 | ORLAND ESTATES MOBILE H.P. | GLENN | 200 | 74 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA4400631 | LAS CUMBRES MUTUAL WATER CO | SANTA CRUZ | 342 | 125 | Some | 51300 | 80.1562 | 57467.2812 | 60340.6453 | 0.3 | 17240.1844 | 77580.8297 | 81227.1287
CA3110042 | TAHOE SWISS VILLAGE UTILITY | PLACER | 300 | 395 | Some | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 59486.4469
CA1710004 | LAKEPORT, CITY OF | LAKE | 4762 | 2278 | Some | 714300 | 1116.0938 | 410721.9688 | 431258.0672 | 0 | 0 | 431258.0672 | 451527.1963
CA1300550 | COUNTRY LIFE MH & RV PARK | IMPERIAL | 600 | 306 | None | 90000 | 140.625 | 78087.125 | 81991.4812 | 0 | 0 | 81991.4812 | 85845.0809
CA1000053 | LANARE COMMUNITY SERVICES DIST | FRESNO | 660 | 156 | None | 99000 | 154.6875 | 82882.4375 | 87026.5594 | 0 | 0 | 87026.5594 | 91116.8077
CA5500128 | GOLD RUSH MOBILE HOME PARK | TUOLUMNE | 67 | 53 | None | 10050 | 15.7031 | 35488.7656 | 37263.2039 | 0 | 0 | 37263.2039 | 39014.5745
CA4900913 | ROBIN WAY WATER SYSTEM | SONOMA | 66 | 20 | None | 9900 | 15.4688 | 35408.8438 | 37179.2859 | 0.3 | 10622.6531 | 47801.9391 | 50048.6302
CA4900545 | BRANGER MUTUAL WATER COMPANY, INC. | SONOMA | 300 | 83 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0.3 | 16233.1688 | 73049.2594 | 76482.5746
CA2910014 | NEVADA ID - LAKE OF PINES | NEVADA | 6932 | 2441 | Some | 1039800 | 1624.6875 | 584152.4375 | 613360.0594 | 0 | 0 | 613360.0594 | 642187.9822
CA5010035 | CITY OF MODESTO - CENTRAL TURLOCK | STANISLAUS | 116 | 36 | None | 17400 | 27.1875 | 39404.9375 | 41375.1844 | 0 | 0 | 41375.1844 | 43319.818
CA2702110 | DELANY WC | MONTEREY | 60 | 17 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA3310036 | WESTERN MWD - MURRIETA DIVISION | RIVERSIDE | 12810 | 2828 | Some | 1921500 | 3002.3438 | 1053933.2188 | 1106629.8797 | 0.32 | 337258.63 | 1443888.5097 | 1511751.2696
CA1700606 | BAYCLIFF WATER | LAKE | 70 | 56 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0 | 0 | 37514.9578 | 39278.1608
CA5500048 | DON PEDRO REC AG:FLEM.MEADOWS | TUOLUMNE | 1041 | 18 | None | 156150 | 243.9844 | 113332.6719 | 118999.3055 | 0 | 0 | 118999.3055 | 124592.2728
CA4300611 | CASA DE FRUTA WATER SYSTEM | SANTA CLARA | 250 | 37 | Some | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0.32 | 16036.63 | 68656.8222 | 71883.6928
CA2210924 | YOSEMITE WEST WATER SYSTEM | MARIPOSA | 420 | 186 | None | 63000 | 98.4375 | 63701.1875 | 66886.2469 | 0 | 0 | 66886.2469 | 70029.9005
CA1410005 | INDIAN CREEK CSD | INYO | 1030 | 297 | Some | 154500 | 241.4062 | 112453.5312 | 118076.2078 | 0 | 0 | 118076.2078 | 123625.7896
CA3301294 | GLEN IVY HOT SPRINGS | RIVERSIDE | 653 | 49 | None | 97950 | 153.0469 | 82322.9844 | 86439.1336 | 0.32 | 26343.355 | 112782.4886 | 118083.2656
CA0707572 | BETHEL ISLAND MUTUAL WATER CO | CONTRA COSTA | 149 | 45 | None | 22350 | 34.9219 | 42042.3594 | 44144.4773 | 0.3 | 12612.7078 | 56757.1852 | 59424.7729
CA3110044 | TAHOE CITY PUD - ALPINE PEAKS | PLACER | 201 | 97 | None | 30150 | 47.1094 | 46198.2969 | 48508.2117 | 0 | 0 | 48508.2117 | 50788.0977
CA1400030 | GLENWOOD MOBILE ESTATES | INYO | 448 | 170 | None | 67200 | 105 | 65939 | 69235.95 | 0 | 0 | 69235.95 | 72490.0397
CA3301990 | AMEZCUA - GARCIA WATER | RIVERSIDE | 316 | 113 |  | 47400 | 74.0625 | 55389.3125 | 58158.7781 | 0.32 | 17724.58 | 75883.3581 | 79449.876
CA5601141 | SOUTH MOUNTAIN MUTUAL WATER CO | VENTURA | 58 | 27 | None | 8700 | 13.5938 | 34769.4688 | 36507.9422 | 0.32 | 11126.23 | 47634.1722 | 49872.9783
CA2700586 | GABILAN WC | MONTEREY | 535 | 162 | None | 80250 | 125.3906 | 72892.2031 | 76536.8133 | 0.3 | 21867.6609 | 98404.4742 | 103029.4845
CA2702466 | SAN VICENTE MWC | MONTEREY | 69 | 21 |  | 10350 | 16.1719 | 35648.6094 | 37431.0398 | 0.3 | 10694.5828 | 48125.6227 | 50387.5269
CA3110031 | WARD WELL WATER COMPANY | PLACER | 375 | 226 | Some | 56250 | 87.8906 | 60104.7031 | 63109.9383 | 0 | 0 | 63109.9383 | 66076.1054
CA1500557 | STOCKDALE RANCHOS MUTUAL WATER CO | KERN | 393 | 95 | None | 58950 | 92.1094 | 61543.2969 | 64620.4617 | 0 | 0 | 64620.4617 | 67657.6234
CA1500481 | RIVERNOOK CAMPGROUND | KERN | 877 | 290 | Some | 131550 | 205.5469 | 100225.4844 | 105236.7586 | 0 | 0 | 105236.7586 | 110182.8862
CA1500489 | BRITE LAKE MUTUAL WATER COMPANY | KERN | 89 | 27 | None | 13350 | 20.8594 | 37247.0469 | 39109.3992 | 0 | 0 | 39109.3992 | 40947.541
CA1910010 | CALIFORNIA WATER SERVICE CO.-LANCASTER | LOS ANGELES | 1422 | 673 | Some | 213300 | 333.2812 | 143782.9062 | 150972.0516 | 0.32 | 46010.53 | 196982.5816 | 206240.7629
CA3700074 | CUYAMACA WATER DISTRICT | SAN DIEGO | 200 | 159 | Some | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.32 | 14757.88 | 63182.1738 | 66151.7359
CA5610014 | OJAI WATER SYSTEM | VENTURA | 6712 | 2902 | Some | 1006800 | 1573.125 | 566569.625 | 594898.1062 | 0.32 | 181302.28 | 776200.3862 | 812681.8044
CA2300545 | SHORELANDS ROAD & WATER COMPANY | MENDOCINO | 85 | 47 | None | 12750 | 19.9219 | 36927.3594 | 38773.7273 | 0 | 0 | 38773.7273 | 40596.0925
CA1100254 | VOYLES TRAILER PARK | GLENN | 27 | 15 | None | 4050 | 6.3281 | 32291.8906 | 33906.4852 | 0 | 0 | 33906.4852 | 35500.09
CA5304102 | TRINITY VILLAGE MUTUAL WATER | TRINITY | 301 | 193 |  | 45150 | 70.5469 | 54190.4844 | 56900.0086 | 0 | 0 | 56900.0086 | 59574.309
CA1910027 | LOS ANGELES CWWD 40, REG. 35-N.E. L.A. | LOS ANGELES | 811 | 223 | None | 121650 | 190.0781 | 94950.6406 | 99698.1727 | 0.32 | 30384.205 | 130082.3777 | 136196.2494
CA3710041 | MAJESTIC PINES COMMUNITY SD | SAN DIEGO | 1502 | 706 | Some | 225300 | 352.0312 | 150176.6562 | 157685.4891 | 0.32 | 48056.53 | 205742.0191 | 215411.894
CA3710009 | DESCANSO COMMUNITY SERVICES DISTRICT | SAN DIEGO | 870 | 317 | None | 130500 | 203.9062 | 99666.0312 | 104649.3328 | 0.32 | 31893.13 | 136542.4628 | 142959.9586
CA2700548 | DOLAN RD MWC | MONTEREY | 120 | 40 | None | 18000 | 28.125 | 39724.625 | 41710.8562 | 0.3 | 11917.3875 | 53628.2438 | 56148.7712
CA1910072 | GSWC - WILLOWBROOK | LOS ANGELES | 11069 | 1450 | Some | 1660350 | 2594.2969 | 914789.2344 | 960528.6961 | 0.32 | 292732.555 | 1253261.2511 | 1312164.5299
CA4900536 | OCCIDENTAL COMMUNITY SERVICES DISTRICT | SONOMA | 383 | 109 | None | 57450 | 89.7656 | 60744.0781 | 63781.282 | 0.3 | 18223.2234 | 82004.5055 | 85858.7172
CA2700775 | TIERRA VERDE MWC | MONTEREY | 48 | 16 | None | 7200 | 11.25 | 33970.25 | 35668.7625 | 0.3 | 10191.075 | 45859.8375 | 48015.2499
CA5800823 | COUNTRY AIR MOBILE HOME PARK | YUBA | 100 | 35 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA2300892 | COVELO MOBILE HOME PARK | MENDOCINO | 30 | 30 |  | 4500 | 7.0312 | 32531.6562 | 34158.2391 | 0 | 0 | 34158.2391 | 35763.6763
CA5200255 | CORNING RV PARK | TEHAMA | 112 | 40 |  | 16800 | 26.25 | 39085.25 | 41039.5125 | 0 | 0 | 41039.5125 | 42968.3696
CA3600025 | BAR-LEN MWC | SAN BERNARDINO | 124 | 42 |  | 18600 | 29.0625 | 40044.3125 | 42046.5281 | 0.3 | 12013.2938 | 54059.8219 | 56600.6335
CA5200500 | REEDS CREEK ESTATES | TEHAMA | 70 | 25 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0 | 0 | 37514.9578 | 39278.1608
CA4100538 | CAMP JONES GULCH | SAN MATEO | 357 | 65 | None | 53550 | 83.6719 | 58666.1094 | 61599.4148 | 0.32 | 18773.155 | 80372.5698 | 84150.0806
CA3600382 | MWD OF SO CAL IRON MOUNTAIN | SAN BERNARDINO | 27 | 38 | None | 4050 | 6.3281 | 32291.8906 | 33906.4852 | 0.3 | 9687.5672 | 43594.0523 | 45642.9728
CA5602110 | NAVALAIR MOBILE HOME PARK | VENTURA | 160 | 52 | None | 24000 | 37.5 | 42921.5 | 45067.575 | 0.32 | 13734.88 | 58802.455 | 61566.1704
CA5602109 | GLENVIEW MOBILE PARK | VENTURA | 160 | 26 | None | 24000 | 37.5 | 42921.5 | 45067.575 | 0.32 | 13734.88 | 58802.455 | 61566.1704
CA3500910 | DUNNEVILLE ESTATES CSA #50 | SAN BENITO | 120 | 30 |  | 18000 | 28.125 | 39724.625 | 41710.8562 | 0.3 | 11917.3875 | 53628.2438 | 56148.7712
CA4100555 | PORTOLA IMPROVEMENT ASSOCIATION | SAN MATEO | 100 | 35 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.32 | 12200.38 | 52232.8769 | 54687.8221
CA2110007 | COAST SPRINGS - CAL. WATER SERVICE (PUC) | MARIN | 210 | 251 | Some | 31500 | 49.2188 | 46917.5938 | 49263.4734 | 0.3 | 14075.2781 | 63338.7516 | 66315.6729
CA3110020 | OLYMPIC VALLEY PSD | PLACER | 1366 | 865 | Some | 204900 | 320.1562 | 139307.2812 | 146272.6453 | 0 | 0 | 146272.6453 | 153147.4596
CA5710011 | WILD WINGS GOLF COMMUNITY | YOLO | 1115 | 352 | Some | 167250 | 261.3281 | 119246.8906 | 125209.2352 | 0 | 0 | 125209.2352 | 131094.0692
CA1805004 | CDCR-HIGH DESERT STATE PRISON | LASSEN | 8641 | 2724 | None | 1296150 | 2025.2344 | 720738.9219 | 756775.868 | 0 | 0 | 756775.868 | 792344.3338
CA5510021 | TUD-PEACEFUL PINES WATER SYSTEM | TUOLUMNE | 56 | 33 | NULL | 8400 | 13.125 | 34609.625 | 36340.1062 | 0 | 0 | 36340.1062 | 38048.0912
CA5200571 | MOUNTAIN VALLEY APTS & RVP | TEHAMA | 131 | 47 | None | 19650 | 30.7031 | 40603.7656 | 42633.9539 | 0 | 0 | 42633.9539 | 44637.7497
CA2702026 | APRICOT LN WS | MONTEREY | 53 | 16 | None | 7950 | 12.4219 | 34369.8594 | 36088.3523 | 0.3 | 10310.9578 | 46399.3102 | 48580.0777
CA3900602 | TAHAMA VILLAGE MOBILE HOME PARK | SAN JOAQUIN | 200 | 68 | Some | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA1900785 | MITCHELL'S AVENUE E MOBILE HOME PARK | LOS ANGELES | 24 | 24 | None | 3600 | 5.625 | 32052.125 | 33654.7312 | 0.32 | 10256.68 | 43911.4112 | 45975.2476
CA3410045 | CALAM - ARDEN | SACRAMENTO | 3908 | 1185 | Some | 586200 | 915.9375 | 342468.6875 | 359592.1219 | 0.32 | 109589.98 | 469182.1019 | 491233.6607
CA4910018 | ARMSTRONG VALLEY-CAL WATER SERVICE (PUC) | SONOMA | 424 | 269 | Some | 63600 | 99.375 | 64020.875 | 67221.9187 | 0.3 | 19206.2625 | 86428.1812 | 90490.3058
CA4400598 | PURESOURCE WATER, INC | SANTA CRUZ | 200 | 77 | Some | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.3 | 13835.5125 | 62259.8063 | 65186.0171
CA3400190 | IMPERIAL MANOR MOBILEHOME COMMUNITY | SACRAMENTO | 200 | 186 |  | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.32 | 14757.88 | 63182.1738 | 66151.7359
CA4000649 | LOS ROBLES MOBILE HOME ESTATES | SAN LUIS OBISPO | 420 | 160 | None | 63000 | 98.4375 | 63701.1875 | 66886.2469 | 0.3 | 19110.3563 | 85996.6031 | 90038.4435
CA1300628 | IMPERIAL LAKES INC. | IMPERIAL | 40 | 15 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0 | 0 | 34997.4187 | 36642.2974
CA4210018 | BUELLTON WATER DEPARTMENT | SANTA BARBARA | 5464 | 1831 | None | 819600 | 1280.625 | 466827.125 | 490168.4813 | 0.3 | 140048.1375 | 630216.6188 | 659836.7998
CA1500289 | ATHAL MUTUAL WATER SYSTEM | KERN | 150 | 55 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA1500546 | HARVEST MOON MUTUAL WATER CO | KERN | 138 | 49 | None | 20700 | 32.3438 | 41163.2188 | 43221.3797 | 0 | 0 | 43221.3797 | 45252.7845
CA3600070 | CENTER WATER CO | SAN BERNARDINO | 662 | 50 | None | 99300 | 155.1562 | 83042.2812 | 87194.3953 | 0.3 | 24912.6844 | 112107.0797 | 117376.1124
CA3910020 | STOCKTON VERDE MOBILE HOME PARK | SAN JOAQUIN | 712 | 293 | None | 106800 | 166.875 | 87038.375 | 91390.2937 | 0 | 0 | 91390.2937 | 95685.6376
CA3500524 | RIVER OAKS R.V.P. | SAN BENITO | 52 | 15 |  | 7800 | 12.1875 | 34289.9375 | 36004.4344 | 0.3 | 10286.9813 | 46291.4156 | 48467.1122
CA2610701 | USMC - HOUSING COLEVILLE | MONO | 325 | 116 | None | 48750 | 76.1719 | 56108.6094 | 58914.0398 | 0 | 0 | 58914.0398 | 61682.9997
CA3200138 | MEADOW EDGE MHP | PLUMAS | 53 | 31 | None | 7950 | 12.4219 | 34369.8594 | 36088.3523 | 0 | 0 | 36088.3523 | 37784.5049
CA4300571 | SULLIVAN MUTUAL WATER | SANTA CLARA | 53 | 16 |  | 7950 | 12.4219 | 34369.8594 | 36088.3523 | 0.32 | 10998.355 | 47086.7073 | 49299.7826
CA0510004 | CCWD - SHEEP RANCH | CALAVERAS | 134 | 48 |  | 20100 | 31.4062 | 40843.5312 | 42885.7078 | 0 | 0 | 42885.7078 | 44901.3361
CA1300546 | GOLD ROCK RANCH | IMPERIAL | 50 | 76 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA4200693 | ELLWOOD MUTUAL WATER COMPANY | SANTA BARBARA | 186 | 56 |  | 27900 | 43.5938 | 44999.4688 | 47249.4422 | 0.3 | 13499.8406 | 60749.2828 | 63604.4991
CA3901075 | FAIRWAY ESTATES PWS CSA-18 | SAN JOAQUIN | 68 | 47 | Some | 10200 | 15.9375 | 35568.6875 | 37347.1219 | 0 | 0 | 37347.1219 | 39102.4366
CA3500552 | VENTURE ESTATES MWC | SAN BENITO | 60 | 18 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA1400056 | BROOKSIDE ESTATES MUTUAL WATER COMPANY | INYO | 59 | 21 |  | 8850 | 13.8281 | 34849.3906 | 36591.8602 | 0 | 0 | 36591.8602 | 38311.6776
CA3400128 | HAPPY HARBOR (SWS) | SACRAMENTO | 60 | 45 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.32 | 11177.38 | 47853.1581 | 50102.2566
CA4900637 | MAGIC MOUNTAIN MUTUAL WATER COMPANY | SONOMA | 100 | 67 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.3 | 11437.8563 | 51470.3531 | 53889.4597
CA3600180 | NAVAJO MWC | SAN BERNARDINO | 276 | 80 | None | 41400 | 64.6875 | 52192.4375 | 54802.0594 | 0.3 | 15657.7313 | 70459.7906 | 73771.4008
CA5510007 | DEL ORO WATER COMPANY - STRAWBERRY DIV. | TUOLUMNE | 1283 | 388 | None | 192450 | 300.7031 | 132673.7656 | 139307.4539 | 0 | 0 | 139307.4539 | 145854.9042
CA1500465 | OAK KNOLLS MUTUAL WATER COMPANY | KERN | 123 | 47 | None | 18450 | 28.8281 | 39964.3906 | 41962.6102 | 0 | 0 | 41962.6102 | 43934.8528
CA4700627 | JUNIPER CREEK ESTATES | SISKIYOU | 130 | 51 |  | 19500 | 30.4688 | 40523.8438 | 42550.0359 | 0 | 0 | 42550.0359 | 44549.8876
CA4300603 | OAK DELL PARK | SANTA CLARA | 100 | 53 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.32 | 12200.38 | 52232.8769 | 54687.8221
CA1300622 | SPORTSMANS PARADISE | IMPERIAL | 60 | 30 |  | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 38399.5397
CA3100040 | SHADY GLEN COMM WATER SYSTEM | PLACER | 200 | 121 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA2000851 | MD 40 SUNSET RIDGE ESTATES | MADERA | 150 | 27 |  | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA1400070 | SIERRA GRANDE ESTATES MUTUAL WATER CO. | INYO | 200 | 49 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA3900579 | CENTURY MOBILE HOME PARK | SAN JOAQUIN | 50 | 19 | Some | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA5400670 | TRIPLE R MUTUAL WATER CO | TULARE | 408 | 154 | None | 61200 | 95.625 | 62742.125 | 65879.2312 | 0 | 0 | 65879.2312 | 68975.5551
CA5510013 | TUD - COLUMBIA WATER SYSTEM | TUOLUMNE | 4352 | 1925 | NULL | 652800 | 1020 | 377954 | 396851.7 | 0 | 0 | 396851.7 | 415503.7299
CA5510033 | TUD-SCENIC VIEW/SCENIC BROOK | TUOLUMNE | 365 | 174 | NULL | 54750 | 85.5469 | 59305.4844 | 62270.7586 | 0 | 0 | 62270.7586 | 65197.4842
CA4900640 | SONOMA COUNTY MUTUAL WATER COMPANY | SONOMA | 40 | 18 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0.3 | 9999.2625 | 44996.6813 | 47111.5253
CA1500378 | MAHER MUTUAL WATER COMPANY | KERN | 150 | 50 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA4000654 | RESTHAVEN MOBILE HOME PARK | SAN LUIS OBISPO | 75 | 47 | None | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0.3 | 10838.4422 | 48772.9898 | 51065.3204
CA5400556 | RIVER RETREAT MUTUAL | TULARE | 53 | 25 | None | 7950 | 12.4219 | 34369.8594 | 36088.3523 | 0 | 0 | 36088.3523 | 37784.5049
CA4910011 | SEBASTOPOL, CITY OF | SONOMA | 7786 | 2953 | Some | 1167900 | 1824.8438 | 652405.7188 | 685026.0047 | 0.3 | 195721.7156 | 880747.7203 | 922142.8632
CA3310004 | BOX SPRINGS MUTUAL WC | RIVERSIDE | 3542 | 649 | None | 531300 | 830.1562 | 313217.2812 | 328878.1453 | 0.32 | 100229.53 | 429107.6753 | 449275.7361
CA3301717 | VALLEY VIEW TRAILER PARK | RIVERSIDE | 135 | 37 | None | 20250 | 31.6406 | 40923.4531 | 42969.6258 | 0.32 | 13095.505 | 56065.1308 | 58700.1919
CA3600139 | JUBILEE MWC | SAN BERNARDINO | 710 | 215 | None | 106500 | 166.4062 | 86878.5312 | 91222.4578 | 0.3 | 26063.5594 | 117286.0172 | 122798.46
CA3900649 | GLENWOOD MOBILE HOME PARK | SAN JOAQUIN | 100 | 50 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA3400217 | HOMETOWN COLONIAL ESTATES LLC | SACRAMENTO | 438 | 146 | None | 65700 | 102.6562 | 65139.7812 | 68396.7703 | 0.32 | 20844.73 | 89241.5003 | 93435.8508
CA3500549 | ROSA MORADA MUTUAL WATER COMPANY | SAN BENITO | 129 | 21 | None | 19350 | 30.2344 | 40443.9219 | 42466.118 | 0.3 | 12133.1766 | 54599.2945 | 57165.4614
CA4910025 | KENWOOD VILLAGE WATER COMPANY (PUC) | SONOMA | 1000 | 309 | None | 150000 | 234.375 | 110055.875 | 115558.6687 | 0.3 | 33016.7625 | 148575.4312 | 155558.4765
CA1500406 | TRADEWIND WATER ASSOC. | KERN | 632 | 234 | NULL | 94800 | 148.125 | 80644.625 | 84676.8562 | 0 | 0 | 84676.8562 | 88656.6685
CA1510004 | CASA LOMA WATER CO, INC. | KERN | 900 | 248 | None | 135000 | 210.9375 | 102063.6875 | 107166.8719 | 0 | 0 | 107166.8719 | 112203.7149
CA4900788 | EL CRYSTAL MOBILE HOME PARK | SONOMA | 130 | 57 | None | 19500 | 30.4688 | 40523.8438 | 42550.0359 | 0.3 | 12157.1531 | 54707.1891 | 57278.4269
CA3610105 | GOLDEN STATE WATER CO - APPLE VLY NORTH | SAN BERNARDINO | 2106 | 731 | Some | 315900 | 493.5938 | 198449.4688 | 208371.9422 | 0.3 | 59534.8406 | 267906.7828 | 280498.4016
CA3600279 | GOLDEN STATE WATER DESERT VIEW | SAN BERNARDINO | 125 | 60 | Some | 18750 | 29.2969 | 40124.2344 | 42130.4461 | 0.3 | 12037.2703 | 54167.7164 | 56713.5991
CA5810005 | NEVADA ID - SMARTSVILLE | YUBA | 122 | 43 | None | 18300 | 28.5938 | 39884.4688 | 41878.6922 | 0 | 0 | 41878.6922 | 43846.9907
CA5710007 | ESPARTO C.S.D. | YOLO | 3108 | 1007 | Some | 466200 | 728.4375 | 278531.1875 | 292457.7469 | 0 | 0 | 292457.7469 | 306203.261
CA2410010 | WINTON WATER & SANITARY DIST | MERCED | 9500 | 2672 | Some | 1425000 | 2226.5625 | 789391.8125 | 828861.4031 | 0 | 0 | 828861.4031 | 867817.8891
CA1910086 | MAYWOOD MUTUAL WATER CO. #3 | LOS ANGELES | 9500 | 2014 | Some | 1425000 | 2226.5625 | 789391.8125 | 828861.4031 | 0.32 | 252605.38 | 1081466.7831 | 1132295.7219
CA4400526 | BIG REDWOOD PARK WATER | SANTA CRUZ | 130 | 65 | Some | 19500 | 30.4688 | 40523.8438 | 42550.0359 | 0.3 | 12157.1531 | 54707.1891 | 57278.4269
CA1910081 | LYNWOOD PARK MUTUAL WATER CO. | LOS ANGELES | 2300 | 470 | Some | 345000 | 539.0625 | 213954.3125 | 224652.0281 | 0.32 | 68465.38 | 293117.4081 | 306893.9263
CA5403110 | SIERRA MUTUAL WATER CO | TULARE | 43 | 16 | None | 6450 | 10.0781 | 33570.6406 | 35249.1727 | 0 | 0 | 35249.1727 | 36905.8838
CA3700859 | RANCHO DEL CAMPO WATER SYSTEM | SAN DIEGO | 290 | 110 | Some | 43500 | 67.9688 | 53311.3438 | 55976.9109 | 0.32 | 17059.63 | 73036.5409 | 76469.2584
CA2701498 | HARBOR VIEW WA | MONTEREY | 75 | 29 | None | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0.3 | 10838.4422 | 48772.9898 | 51065.3204
CA1500461 | FOUNTAIN TRAILER PARK WATER | KERN | 68 | 33 | None | 10200 | 15.9375 | 35568.6875 | 37347.1219 | 0 | 0 | 37347.1219 | 39102.4366
CA1700610 | BELLA LAGO MOBILE HOME PARK | LAKE | 152 | 46 |  | 22800 | 35.625 | 42282.125 | 44396.2312 | 0 | 0 | 44396.2312 | 46482.8541
CA1000259 | NEW HORIZONS MOBILE/RV PARK | FRESNO | 82 | 77 | None | 12300 | 19.2188 | 36687.5938 | 38521.9734 | 0 | 0 | 38521.9734 | 40332.5062
CA1210020 | FIELDBROOK GLENDALE C.S.D. | HUMBOLDT | 1848 | 551 |  | 277200 | 433.125 | 177829.625 | 186721.1063 | 0 | 0 | 186721.1063 | 195496.9982
CA5601117 | SENIOR CANYON MUTUAL WATER CO | VENTURA | 800 | 218 | None | 120000 | 187.5 | 94071.5 | 98775.075 | 0.32 | 30102.88 | 128877.955 | 134935.2189
CA2310006 | MILLVIEW COUNTY WATER DISTRICT | MENDOCINO | 5500 | 1609 | Some | 825000 | 1289.0625 | 469704.3125 | 493189.5281 | 0 | 0 | 493189.5281 | 516369.4359
CA2210903 | FISHCAMP MUTUAL WATER COMPANY | MARIPOSA | 275 | 75 | Some | 41250 | 64.4531 | 52112.5156 | 54718.1414 | 0 | 0 | 54718.1414 | 57289.8941
CA5200512 | BEND MOBILEHOME & RV PARK | TEHAMA | 99 | 42 |  | 14850 | 23.2031 | 38046.2656 | 39948.5789 | 0 | 0 | 39948.5789 | 41826.1621
CA3600155 | RIVER RANCH MHP | SAN BERNARDINO | 700 | 138 |  | 105000 | 164.0625 | 86079.3125 | 90383.2781 | 0.3 | 25823.7938 | 116207.0719 | 121668.8043
CA5610701 | NAVAL BASE VENTURA COUNTY, PORT HUENEME | VENTURA | 3500 | 609 |  | 525000 | 820.3125 | 309860.5625 | 325353.5906 | 0.32 | 99155.38 | 424508.9706 | 444460.8922
CA1900649 | GOLDEN SANDS MOBILE HOME PARK | LOS ANGELES | 450 | 152 |  | 67500 | 105.4688 | 66098.8438 | 69403.7859 | 0.32 | 21151.63 | 90555.4159 | 94811.5205
CA1600023 | AZCAL MANAGEMENT CO | KINGS | 73 | 21 | None | 10950 | 17.1094 | 35968.2969 | 37766.7117 | 0 | 0 | 37766.7117 | 39541.7472
CA3410005 | RANCHO MURIETA COMMUNITY SERVI | SACRAMENTO | 5744 | 2726 | None | 861600 | 1346.25 | 489205.25 | 513665.5125 | 0.32 | 156545.68 | 670211.1925 | 701711.1185
CA3900805 | MOREHEAD PARK | SAN JOAQUIN | 300 | 113 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 59486.4469
CA5800832 | CASTLEWOOD MOBILE HOME PARK | YUBA | 200 | 88 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA0800605 | WEST PARK PROPERTIES | DEL NORTE | 112 | 42 | None | 16800 | 26.25 | 39085.25 | 41039.5125 | 0 | 0 | 41039.5125 | 42968.3696
CA2300610 | CASPAR SOUTH SERVICE COMPANY | MENDOCINO | 188 | 95 |  | 28200 | 44.0625 | 45159.3125 | 47417.2781 | 0 | 0 | 47417.2781 | 49645.8902
CA4010018 | GOLDEN STATE WATER COMPANY - NIPOMO | SAN LUIS OBISPO | 4409 | 1505 | Some | 661350 | 1033.3594 | 382509.5469 | 401635.0242 | 0.3 | 114752.8641 | 516387.8883 | 540658.119
CA5310001 | WEAVERVILLE C.S.D. | TRINITY | 3400 | 1654 | Some | 510000 | 796.875 | 301868.375 | 316961.7938 | 0 | 0 | 316961.7938 | 331858.9981
CA1910189 | SAN GABRIEL VALLEY WATER CO.-MONTEBELLO | LOS ANGELES | 8630 | 1579 |  | 1294500 | 2022.6562 | 719859.7812 | 755852.7703 | 0.32 | 230355.13 | 986207.9003 | 1032559.6716
CA2300735 | HOLLY RANCH VILLAGE | MENDOCINO | 50 | 19 |  | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA1310008 | WESTMORLAND, CITY OF | IMPERIAL | 2444 | 501 | None | 366600 | 572.8125 | 225463.0625 | 236736.2156 | 0 | 0 | 236736.2156 | 247862.8178
CA1502620 | POND MUTUAL WATER COMPANY | KERN | 48 | 18 |  | 7200 | 11.25 | 33970.25 | 35668.7625 | 0 | 0 | 35668.7625 | 37345.1943
CA2000593 | OAKHURST MOBILE HOME ESTATES | MADERA | 164 | 116 | None | 24600 | 38.4375 | 43241.1875 | 45403.2469 | 0 | 0 | 45403.2469 | 47537.1995
CA5000237 | NORTH OAKS MUTUAL WATER CO | STANISLAUS | 234 | 78 | Some | 35100 | 54.8438 | 48835.7188 | 51277.5047 | 0 | 0 | 51277.5047 | 53687.5474
CA3600262 | SNOWCREST HEIGHTS IMP ASSOC | SAN BERNARDINO | 600 | 125 | None | 90000 | 140.625 | 78087.125 | 81991.4812 | 0.3 | 23426.1375 | 105417.6187 | 110372.2468
CA5000016 | OID #41 - MOUNTAIN VIEW | STANISLAUS | 147 | 42 | Some | 22050 | 34.4531 | 41882.5156 | 43976.6414 | 0 | 0 | 43976.6414 | 46043.5436
CA5200014 | WILSON ACRES MUTUAL WATER | TEHAMA | 75 | 28 |  | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0 | 0 | 37934.5477 | 39717.4714
CA5000017 | PARK HEIGHTS MUTUAL WATER CO | STANISLAUS | 250 | 95 | NULL | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 55093.3412
CA3900705 | FINNLEES TRAILER PARK | SAN JOAQUIN | 55 | 26 | None | 8250 | 12.8906 | 34529.7031 | 36256.1883 | 0 | 0 | 36256.1883 | 37960.2291
CA1900038 | LANCASTER PARK MOBILE HOME PARK | LOS ANGELES | 61 | 21 |  | 9150 | 14.2969 | 35009.2344 | 36759.6961 | 0.32 | 11202.955 | 47962.6511 | 50216.8957
CA1500593 | UPLANDS OF THE KERN MUTUAL WATER COMPANY | KERN | 80 | 20 |  | 12000 | 18.75 | 36527.75 | 38354.1375 | 0 | 0 | 38354.1375 | 40156.782
CA3700073 | H & J WATER COMPANY | SAN DIEGO | 50 | 39 | Some | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0.32 | 10921.63 | 46758.2284 | 48955.8652
CA3310040 | FERN VALLEY WD | RIVERSIDE | 900 | 1175 | Some | 135000 | 210.9375 | 102063.6875 | 107166.8719 | 0.32 | 32660.38 | 139827.2519 | 146399.1327
CA1510701 | EDWARDS AFB - MAIN BASE | KERN | 12403 | 1058 | Some | 1860450 | 2906.9531 | 1021405.0156 | 1072475.2664 | 0 | 0 | 1072475.2664 | 1122881.6039
CA3610016 | GLEN MARTIN MWC | SAN BERNARDINO | 450 | 338 | Some | 67500 | 105.4688 | 66098.8438 | 69403.7859 | 0.3 | 19829.6531 | 89233.4391 | 93427.4107
CA5000049 | LONE PINE MHP | STANISLAUS | 64 | 32 | NULL | 9600 | 15 | 35249 | 37011.45 | 0 | 0 | 37011.45 | 38750.9881
CA1000345 | PANOCHE WATER DISTRICT | FRESNO | 146 | 46 | None | 21900 | 34.2188 | 41802.5938 | 43892.7234 | 0 | 0 | 43892.7234 | 45955.6814
CA3601036 | CALICO LAKE HOMEOWNERS | SAN BERNARDINO | 150 | 56 |  | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0.3 | 12636.6844 | 56865.0797 | 59537.7384
CA0300016 | VOLCANO COMMUNITY SERVICE DIST | AMADOR | 160 | 80 | Some | 24000 | 37.5 | 42921.5 | 45067.575 | 0 | 0 | 45067.575 | 47185.751
CA3700938 | YUIMA MUNICIPAL WATER DISTRICT IDA | SAN DIEGO | 759 | 232 |  | 113850 | 177.8906 | 90794.7031 | 95334.4383 | 0.32 | 29054.305 | 124388.7433 | 130235.0142
CA5800850 | REBEL RIDGE VILLAGE | YUBA | 60 | 41 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 38399.5397
CA3510002 | SAN JUAN BAUTISTA, CITY OF | SAN BENITO | 2335 | 834 | None | 350250 | 547.2656 | 216751.5781 | 227589.157 | 0.3 | 65025.4734 | 292614.6305 | 306367.5181
CA2702374 | COUNTRYSIDE ESTATES MWC | MONTEREY | 223 | 23 |  | 33450 | 52.2656 | 47956.5781 | 50354.407 | 0.3 | 14386.9734 | 64741.3805 | 67784.2254
CA2701822 | ROBLEY PROPERTY MWS | MONTEREY | 92 | 33 | None | 13800 | 21.5625 | 37486.8125 | 39361.1531 | 0.3 | 11246.0438 | 50607.1969 | 52985.7351
CA3400335 | HOLIDAY MOBILE VILLAGE | SACRAMENTO | 200 | 115 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.32 | 14757.88 | 63182.1738 | 66151.7359
CA3110017 | SIERRA LAKES COUNTY WATER DIST | PLACER | 185 | 1223 | Some | 27750 | 43.3594 | 44919.5469 | 47165.5242 | 0 | 0 | 47165.5242 | 49382.3039
CA2702588 | CANADA WOODS WC | MONTEREY | 610 | 174 | Some | 91500 | 142.9688 | 78886.3438 | 82830.6609 | 0.3 | 23665.9031 | 106496.5641 | 111501.9026
CA5403084 | FAIRWAY MUTUAL WATER CO | TULARE | 126 | 45 | None | 18900 | 29.5312 | 40204.1562 | 42214.3641 | 0 | 0 | 42214.3641 | 44198.4392
CA4300999 | UVAS PINES RV PARK | SANTA CLARA | 86 | 43 | None | 12900 | 20.1562 | 37007.2812 | 38857.6453 | 0.32 | 11842.33 | 50699.9753 | 53082.8742
CA2700547 | DESMOND RD WS #03 | MONTEREY | 56 | 19 | None | 8400 | 13.125 | 34609.625 | 36340.1062 | 0.3 | 10382.8875 | 46722.9938 | 48918.9745
CA4210009 | CUYAMA COMMUNITY SERVICES DISTRICT | SANTA BARBARA | 763 | 254 | None | 114450 | 178.8281 | 91114.3906 | 95670.1102 | 0.3 | 27334.3172 | 123004.4273 | 128785.6354
CA2810004 | ST. HELENA, CITY OF | NAPA | 6152 | 2681 | None | 922800 | 1441.875 | 521813.375 | 547904.0437 | 0.3 | 156544.0125 | 704448.0563 | 737557.1149
CA1400110 | PARK WEST MUTUAL WATER COMPANY | INYO | 200 | 67 |  | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA4000775 | MUSTANG SPRINGS MUTUAL WATER | SAN LUIS OBISPO | 30 | 16 | None | 4500 | 7.0312 | 32531.6562 | 34158.2391 | 0.3 | 9759.4969 | 43917.7359 | 45981.8695
CA1300588 | IID VILLAGE | IMPERIAL | 30 | 18 | None | 4500 | 7.0312 | 32531.6562 | 34158.2391 | 0 | 0 | 34158.2391 | 35763.6763
CA3710012 | RANCHO PAUMA MUTUAL WC | SAN DIEGO | 899 | 379 | Some | 134850 | 210.7031 | 101983.7656 | 107082.9539 | 0.32 | 32634.805 | 139717.7589 | 146284.4936
CA4500081 | LAZY LANDING MOBILE HOME PARK | SHASTA | 250 | 110 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 55093.3412
CA4000660 | BEAR VALLEY WATER COMPANY | SAN LUIS OBISPO | 45 | 17 |  | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0.3 | 10119.1453 | 45536.1539 | 47676.3531
CA4010901 | SLOCSA #10A - CAYUCOS | SAN LUIS OBISPO | 1200 | 771 | None | 180000 | 281.25 | 126040.25 | 132342.2625 | 0.3 | 37812.075 | 170154.3375 | 178151.5914
CA4000808 | MONTE SERENO MUTUAL BENEFIT WATER | SAN LUIS OBISPO | 60 | 26 |  | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA1910185 | LOS ANGELES CWWD 36-VAL VERDE | LOS ANGELES | 5289 | 1384 | None | 793350 | 1239.6094 | 452840.7969 | 475482.8367 | 0.32 | 144909.055 | 620391.8917 | 649550.3106
CA2701789 | HOLLY HILLS MWC | MONTEREY | 108 | 27 | None | 16200 | 25.3125 | 38765.5625 | 40703.8406 | 0.3 | 11629.6688 | 52333.5094 | 54793.1843
CA3610117 | DEVORE WC | SAN BERNARDINO | 1633 | 467 | Some | 244950 | 382.7344 | 160646.4219 | 168678.743 | 0.3 | 48193.9266 | 216872.6695 | 227065.685
CA4010016 | LOS OSOS COMMUNITY SERVICES DISTRICT | SAN LUIS OBISPO | 7086 | 2772 | Some | 1062900 | 1660.7812 | 596460.4062 | 626283.4266 | 0.3 | 178938.1219 | 805221.5484 | 843066.9612
CA4300760 | SANTA TERESA MEADOWS WATER COMPANY | SANTA CLARA | 68 | 23 |  | 10200 | 15.9375 | 35568.6875 | 37347.1219 | 0.32 | 11381.98 | 48729.1019 | 51019.3697
CA1400034 | KEOUGH'S HOT SPRINGS | INYO | 175 | 36 | None | 26250 | 41.0156 | 44120.3281 | 46326.3445 | 0 | 0 | 46326.3445 | 48503.6827
CA3900517 | ALMOND PARK WATER SYSTEM | SAN JOAQUIN | 60 | 20 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 38399.5397
CA4400652 | CATHEDRAL HILLS MWC, INC | SANTA CRUZ | 60 | 25 |  | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA5400940 | SIERRA KING HOMEOWNERS ASSN | TULARE | 200 | 49 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA1400026 | RAWSON CREEK MUTUAL WATER COMPANY | INYO | 90 | 40 | NULL | 13500 | 21.0938 | 37326.9688 | 39193.3172 | 0 | 0 | 39193.3172 | 41035.4031
CA4400604 | BRACKEN BRAE COUNTRY CLUB | SANTA CRUZ | 54 | 24 | None | 8100 | 12.6562 | 34449.7812 | 36172.2703 | 0.3 | 10334.9344 | 46507.2047 | 48693.0433
CA5700700 | CACHEVILLE SERVICE DIST | YOLO | 400 | 157 | Some | 60000 | 93.75 | 62102.75 | 65207.8875 | 0 | 0 | 65207.8875 | 68272.6582
CA1900303 | LLANO MUTUAL WATER COMPANY | LOS ANGELES | 264 | 78 | None | 39600 | 61.875 | 51233.375 | 53795.0437 | 0.32 | 16394.68 | 70189.7238 | 73488.6408
CA1900808 | LANCASTER WATER COMPANY | LOS ANGELES | 80 | 22 | None | 12000 | 18.75 | 36527.75 | 38354.1375 | 0.32 | 11688.88 | 50043.0175 | 52395.0393
CA4200870 | CASMALIA COMMUNITY SERVICES DISTRICT | SANTA BARBARA | 234 | 53 |  | 35100 | 54.8438 | 48835.7188 | 51277.5047 | 0.3 | 14650.7156 | 65928.2203 | 69026.8467
CA1500452 | RIVERDALE VILLAGE | KERN | 750 | 290 |  | 112500 | 175.7812 | 90075.4062 | 94579.1766 | 0 | 0 | 94579.1766 | 99024.3979
CA4700638 | OAK VALLEY ACRES P.O.A. | SISKIYOU | 80 | 27 | None | 12000 | 18.75 | 36527.75 | 38354.1375 | 0 | 0 | 38354.1375 | 40156.782
CA1910160 | TRACT 349 MUTUAL WATER CO. | LOS ANGELES | 7500 | 922 | Some | 1125000 | 1757.8125 | 629548.0625 | 661025.4656 | 0.32 | 201455.38 | 862480.8456 | 903017.4454
CA2000595 | MADERA MH & RV PARK | MADERA | 450 | 99 | None | 67500 | 105.4688 | 66098.8438 | 69403.7859 | 0 | 0 | 69403.7859 | 72665.7639
CA3900653 | ISLANDER MARINA | SAN JOAQUIN | 150 | 73 |  | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA5800827 | WHISPERING PINES MOBILE HOME PARK | YUBA | 25 | 19 | None | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0 | 0 | 33738.6492 | 35324.3657
CA3702754 | RANCHO CORRIDO RV RESORT | SAN DIEGO | 350 | 120 | None | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0.32 | 18594.13 | 79606.1191 | 83347.6067
CA3610023 | GREEN VALLEY MWC | SAN BERNARDINO | 1350 | 1169 | None | 202500 | 316.4062 | 138028.5312 | 144929.9578 | 0.3 | 41408.5594 | 186338.5172 | 195096.4275
CA1500588 | SON SHINE PROPERTIES | KERN | 438 | 106 |  | 65700 | 102.6562 | 65139.7812 | 68396.7703 | 0 | 0 | 68396.7703 | 71611.4185
CA3301209 | DESERT VIEW TRAILER PARK | RIVERSIDE | 60 | 22 |  | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.32 | 11177.38 | 47853.1581 | 50102.2566
CA1400135 | WILSON CIRCLE MUTUAL WATER COMPANY | INYO | 129 | 48 | Some | 19350 | 30.2344 | 40443.9219 | 42466.118 | 0 | 0 | 42466.118 | 44462.0255
CA3900842 | DOUBLE L MOBILE ESTATES | SAN JOAQUIN | 320 | 150 | Some | 48000 | 75 | 55709 | 58494.45 | 0 | 0 | 58494.45 | 61243.6891
CA3700933 | PALOMAR MOUNTAIN MUTUAL WATER CO. | SAN DIEGO | 70 | 197 | Some | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0.32 | 11433.13 | 48948.0878 | 51248.6479
CA2000553 | MD 28 RIPPERDAN SELF HELP | MADERA | 48 | 17 |  | 7200 | 11.25 | 33970.25 | 35668.7625 | 0 | 0 | 35668.7625 | 37345.1943
CA4500194 | VILLAGE GREEN | SHASTA | 90 | 32 | None | 13500 | 21.0938 | 37326.9688 | 39193.3172 | 0 | 0 | 39193.3172 | 41035.4031
CA1710007 | KELSEYVILLE CO WATERWORKS DISTRICT 3 | LAKE | 4280 | 1280 | Some | 642000 | 1003.125 | 372199.625 | 390809.6063 | 0 | 0 | 390809.6063 | 409177.6577
CA5403023 | DELFT COLONY WATER | TULARE | 454 | 99 | Some | 68100 | 106.4062 | 66418.5312 | 69739.4578 | 0 | 0 | 69739.4578 | 73017.2123
CA0810002 | SMITH RIVER C.S.D. | DEL NORTE | 2568 | 600 | None | 385200 | 601.875 | 235373.375 | 247142.0438 | 0 | 0 | 247142.0438 | 258757.7198
CA2310007 | NORTH GUALALA WATER COMPANY | MENDOCINO | 2593 | 1059 | Some | 388950 | 607.7344 | 237371.4219 | 249239.993 | 0 | 0 | 249239.993 | 260954.2726
CA4700884 | SHASTINA MOBILE ESTATES | SISKIYOU | 32 | 32 | None | 4800 | 7.5 | 32691.5 | 34326.075 | 0 | 0 | 34326.075 | 35939.4005
CA1503536 | GLENNVILLE MUTUAL WATER COMPANY | KERN | 100 | 25 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA1503475 | WESTERN ACRES MUTUAL WATER COMPANY | KERN | 310 | 90 | None | 46500 | 72.6562 | 54909.7812 | 57655.2703 | 0 | 0 | 57655.2703 | 60365.068
CA0800800 | PINE GROVE TRAILER PARK | DEL NORTE | 100 | 51 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA4500094 | RIVERLAND MOBILEHOME PARK | SHASTA | 274 | 93 |  | 41100 | 64.2188 | 52032.5938 | 54634.2234 | 0 | 0 | 54634.2234 | 57202.0319
CA5000019 | RIVERDALE PARK TRACT CSD | STANISLAUS | 610 | 182 | None | 91500 | 142.9688 | 78886.3438 | 82830.6609 | 0 | 0 | 82830.6609 | 86723.702
CA2701904 | SAN JERARDO COOP WS | MONTEREY | 249 | 67 | None | 37350 | 58.3594 | 50034.5469 | 52536.2742 | 0.3 | 15010.3641 | 67546.6383 | 70721.3303
CA4900612 | HEIGHTS MUTUAL WATER COMPANY | SONOMA | 363 | 110 | None | 54450 | 85.0781 | 59145.6406 | 62102.9227 | 0.3 | 17743.6922 | 79846.6148 | 83599.4057
CA1009028 | HARRIS FARMS SOUTH #101-144 | FRESNO | 160 | 40 | None | 24000 | 37.5 | 42921.5 | 45067.575 | 0 | 0 | 45067.575 | 47185.751
CA1400066 | ASPENDELL MUTUAL WATER COMPANY | INYO | 60 | 94 | Some | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 38399.5397
CA3100061 | SIERRA MEADOWS APARTMENT | PLACER | 52 | 28 | None | 7800 | 12.1875 | 34289.9375 | 36004.4344 | 0 | 0 | 36004.4344 | 37696.6428
CA3100011 | AUBURN VALLEY COMMUNITY SERVICE DIS | PLACER | 290 | 143 | Some | 43500 | 67.9688 | 53311.3438 | 55976.9109 | 0 | 0 | 55976.9109 | 58607.8258
CA1510703 | CHINA LAKE NAVAL AIR WEAPONS STATION | KERN | 5000 | 1380 | Some | 750000 | 1171.875 | 429743.375 | 451230.5438 | 0 | 0 | 451230.5438 | 472438.3793
CA4400617 | SUMMIT WEST MUTUAL WATER CO. | SANTA CRUZ | 468 | 142 |  | 70200 | 109.6875 | 67537.4375 | 70914.3094 | 0.3 | 20261.2313 | 91175.5406 | 95460.791
CA3610107 | GOLDEN STATE WATER CO - APPLE VLY SOUTH | SAN BERNARDINO | 6340 | 1935 | Some | 951000 | 1485.9375 | 536838.6875 | 563680.6219 | 0.3 | 161051.6063 | 724732.2281 | 758794.6428
CA4700521 | SISKIYOU CO.SERVICE AREA #5/CARRICK | SISKIYOU | 142 | 58 |  | 21300 | 33.2812 | 41482.9062 | 43557.0516 | 0 | 0 | 43557.0516 | 45604.233
CA3301107 | CARVER TRACT MUTUAL WATER COMP | RIVERSIDE | 300 | 188 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0.32 | 17315.38 | 74131.4706 | 77615.6497
CA0901217 | BEAR STATE WATER WORKS | EL DORADO | 100 | 56 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.3 | 11437.8563 | 51470.3531 | 53889.4597
CA3110051 | NORTHSTAR CSD - MARTIS VALLEY | PLACER | 1218 | 1107 | Some | 182700 | 285.4688 | 127478.8438 | 133852.7859 | 0 | 0 | 133852.7859 | 140143.8669
CA3610854 | SEARLES VALLEY MINERALS OPERATIONS INC | SAN BERNARDINO | 1818 | 779 | None | 272700 | 426.0938 | 175431.9688 | 184203.5672 | 0.3 | 52629.5906 | 236833.1578 | 247964.3162
CA3600027 | BAR "H" MWC | SAN BERNARDINO | 260 | 45 |  | 39000 | 60.9375 | 50913.6875 | 53459.3719 | 0.3 | 15274.1063 | 68733.4781 | 71963.9516
CA1910153 | SOUTH MONTEBELLO IRRIGATION DIST. | LOS ANGELES | 8205 | 2374 | Some | 1230750 | 1923.0469 | 685892.9844 | 720187.6336 | 0.32 | 219485.755 | 939673.3886 | 983838.0379
CA1009147 | FARMING D | FRESNO | 110 | 29 |  | 16500 | 25.7812 | 38925.4062 | 40871.6766 | 0 | 0 | 40871.6766 | 42792.6454
CA1900717 | CASA DULCE ESTATES | LOS ANGELES | 28 | 17 | None | 4200 | 6.5625 | 32371.8125 | 33990.4031 | 0.32 | 10358.98 | 44349.3831 | 46433.8041
CA1510051 | LEBEC COUNTY WATER DISTRICT | KERN | 1379 | 303 | Some | 206850 | 323.2031 | 140346.2656 | 147363.5789 | 0 | 0 | 147363.5789 | 154289.6671
CA4500062 | LONE TREE MOBILE HOME PARK | SHASTA | 85 | 26 | None | 12750 | 19.9219 | 36927.3594 | 38773.7273 | 0 | 0 | 38773.7273 | 40596.0925
CA1510023 | LAKE OF THE WOODS MWC | KERN | 1103 | 390 | None | 165450 | 258.5156 | 118287.8281 | 124202.2195 | 0 | 0 | 124202.2195 | 130039.7238
CA3901474 | HESKETT, JOE WATER SYSTEM | SAN JOAQUIN | 39 | 15 | Some | 5850 | 9.1406 | 33250.9531 | 34913.5008 | 0 | 0 | 34913.5008 | 36554.4353
CA3900624 | IL VINETO | SAN JOAQUIN | 160 | 83 | None | 24000 | 37.5 | 42921.5 | 45067.575 | 0 | 0 | 45067.575 | 47185.751
CA1700549 | CORINTHIAN BAY MUTUAL WATER COMPANY | LAKE | 150 | 74 |  | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA1900555 | LOS ANGELES, CITY OF - POWER PLANT #1 | LOS ANGELES | 20 | 19 | None | 3000 | 4.6875 | 31732.4375 | 33319.0594 | 0.32 | 10154.38 | 43473.4394 | 45516.691
CA1700519 | CRESCENT BAY IMPROVEMENT COMPANY | LAKE | 30 | 24 | None | 4500 | 7.0312 | 32531.6562 | 34158.2391 | 0 | 0 | 34158.2391 | 35763.6763
CA3410003 | GOLDEN STATE WATER CO - ARDEN WATER SERV | SACRAMENTO | 5154 | 1716 | Some | 773100 | 1207.9688 | 442051.3438 | 464153.9109 | 0.32 | 141456.43 | 605610.3409 | 634074.027
CA0707547 | KNIGHTSEN COMMUNITY WATER SYSTEM | CONTRA COSTA | 250 | 18 |  | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0.3 | 15034.3406 | 67654.5328 | 70834.2959
CA0707501 | ANGLER S RANCH #3 | CONTRA COSTA | 60 | 32 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA5410017 | LONDON COMMUNITY SERV DIST | TULARE | 2138 | 320 | None | 320700 | 501.0938 | 201006.9688 | 211057.3172 | 0 | 0 | 211057.3172 | 220977.0111
CA4900559 | FIRCREST MUTUAL WATER COMPANY | SONOMA | 126 | 47 | None | 18900 | 29.5312 | 40204.1562 | 42214.3641 | 0.3 | 12061.2469 | 54275.6109 | 56826.5647
CA4200580 | SAN MARCOS MUTUAL WATER COMPANY | SANTA BARBARA | 120 | 33 | None | 18000 | 28.125 | 39724.625 | 41710.8562 | 0.3 | 11917.3875 | 53628.2438 | 56148.7712
CA4300578 | ANGELO LANE WATER COMPANY | SANTA CLARA | 52 | 15 |  | 7800 | 12.1875 | 34289.9375 | 36004.4344 | 0.32 | 10972.78 | 46977.2144 | 49185.1435
CA3301482 | ORTEGA OAKS RV PARK&CAMPGROUND | RIVERSIDE | 180 | 77 |  | 27000 | 42.1875 | 44519.9375 | 46745.9344 | 0.32 | 14246.38 | 60992.3144 | 63858.9532
CA3210004 | AMERICAN VALLEY CSD | PLUMAS | 4300 | 1607 | Some | 645000 | 1007.8125 | 373798.0625 | 392487.9656 | 0 | 0 | 392487.9656 | 410934.9
CA1510028 | MIL POTRERO MWC | KERN | 1600 | 2354 | Some | 240000 | 375 | 158009 | 165909.45 | 0 | 0 | 165909.45 | 173707.1941
CA4110010 | MONTARA WATER AND SANITARY DISTRICT | SAN MATEO | 5289 | 1673 | Some | 793350 | 1239.6094 | 452840.7969 | 475482.8367 | 0.32 | 144909.055 | 620391.8917 | 649550.3106
CA0400003 | HARTLEY MUTUAL WATER SYSTEM | BUTTE | 31 | 15 | None | 4650 | 7.2656 | 32611.5781 | 34242.157 | 0 | 0 | 34242.157 | 35851.5384
CA3910022 | LITTLE POTATO SLOUGH MUTUAL | SAN JOAQUIN | 950 | 202 | None | 142500 | 222.6562 | 106059.7812 | 111362.7703 | 0 | 0 | 111362.7703 | 116596.8205
CA1900145 | REESEDALE MUTUAL | LOS ANGELES | 76 | 23 |  | 11400 | 17.8125 | 36208.0625 | 38018.4656 | 0.32 | 11586.58 | 49605.0456 | 51936.4828
CA1500404 | PINEBROOK COMMUNITY WATER WELL | KERN | 68 | 42 | None | 10200 | 15.9375 | 35568.6875 | 37347.1219 | 0 | 0 | 37347.1219 | 39102.4366
CA0707569 | ANGLERS SUBDIVISION 4 | CONTRA COSTA | 210 | 89 | Some | 31500 | 49.2188 | 46917.5938 | 49263.4734 | 0.3 | 14075.2781 | 63338.7516 | 66315.6729
CA4910008 | RUSSIAN RIVER COUNTY WATER DISTRICT | SONOMA | 4150 | 1253 | None | 622500 | 972.6562 | 361809.7812 | 379900.2703 | 0.3 | 108542.9344 | 488443.2047 | 511400.0353
CA2910001 | CITY OF GRASS VALLEY | NEVADA | 4947 | 2486 |  | 742050 | 1159.4531 | 425507.5156 | 446782.8914 | 0 | 0 | 446782.8914 | 467781.6873
CA3600200 | RANCHERITOS MWC | SAN BERNARDINO | 655 | 286 | None | 98250 | 153.5156 | 82482.8281 | 86606.9695 | 0.3 | 24744.8484 | 111351.818 | 116585.3534
CA5700788 | NORTH DAVIS MEADOWS | YOLO | 314 | 96 |  | 47100 | 73.5938 | 55229.4688 | 57990.9422 | 0 | 0 | 57990.9422 | 60716.5165
CA1900976 | THE OAKS | LOS ANGELES | 67 | 26 | None | 10050 | 15.7031 | 35488.7656 | 37263.2039 | 0.32 | 11356.405 | 48619.6089 | 50904.7305
CA1900158 | LITTLE BALDY WATER | LOS ANGELES | 55 | 36 |  | 8250 | 12.8906 | 34529.7031 | 36256.1883 | 0.32 | 11049.505 | 47305.6933 | 49529.0609
CA2800528 | LINDA VISTA MUTUAL WATER CO | NAPA | 50 | 36 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0.3 | 10239.0281 | 46075.6266 | 48241.181
CA4900797 | NORTH STAR MOBILE HOME PARK | SONOMA | 75 | 79 | None | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0.3 | 10838.4422 | 48772.9898 | 51065.3204
CA4300615 | THOUSAND TRAILS - MORGAN HILL | SANTA CLARA | 508 | 320 |  | 76200 | 119.0625 | 70734.3125 | 74271.0281 | 0.32 | 22634.98 | 96906.0081 | 101460.5905
CA2900511 | SHADY LAKE WATER ASSOCIATION | NEVADA | 90 | 28 | None | 13500 | 21.0938 | 37326.9688 | 39193.3172 | 0 | 0 | 39193.3172 | 41035.4031
CA4700686 | SUN MOUNTAIN M.W.C. | SISKIYOU | 55 | 31 | None | 8250 | 12.8906 | 34529.7031 | 36256.1883 | 0 | 0 | 36256.1883 | 37960.2291
CA3900596 | VILLA CEREZOS | SAN JOAQUIN | 200 | 82 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA5400935 | CWS - MULLEN WATER COMPANY | TULARE | 138 | 42 | Some | 20700 | 32.3438 | 41163.2188 | 43221.3797 | 0 | 0 | 43221.3797 | 45252.7845
CA2010017 | TESORO VIEJO MASTER MWC, INC. | MADERA | 2640 | 301 |  | 396000 | 618.75 | 241127.75 | 253184.1375 | 0 | 0 | 253184.1375 | 265083.792
CA3600008 | APPLE VALLEY FOOTHILL CWD | SAN BERNARDINO | 729 | 218 |  | 109350 | 170.8594 | 88397.0469 | 92816.8992 | 0.3 | 26519.1141 | 119336.0133 | 124944.8059
CA1410503 | NPS - DEATH VALLEY, COW CREEK/NEVARES | INYO | 88 | 61 |  | 13200 | 20.625 | 37167.125 | 39025.4812 | 0 | 0 | 39025.4812 | 40859.6789
CA3103835 | LAKEVIEW HILLS COMMUNITY ASSOC | PLACER | 499 | 152 | None | 74850 | 116.9531 | 70015.0156 | 73515.7664 | 0 | 0 | 73515.7664 | 76971.0074
CA5410503 | NPS-WOLVERTON | TULARE | 2940 | 125 | None | 441000 | 689.0625 | 265104.3125 | 278359.5281 | 0 | 0 | 278359.5281 | 291442.4259
CA1010501 | NPS-GRANT GROVE | FRESNO | 2950 | 100 | Some | 442500 | 691.4062 | 265903.5312 | 279198.7078 | 0 | 0 | 279198.7078 | 292321.0471
CA1500371 | UNION PACIFIC RAILROAD CO.-KEENE WATER | KERN | 208 | 26 |  | 31200 | 48.75 | 46757.75 | 49095.6375 | 0 | 0 | 49095.6375 | 51403.1325
CA2600622 | SIERRA EAST HOA | MONO | 84 | 30 | None | 12600 | 19.6875 | 36847.4375 | 38689.8094 | 0 | 0 | 38689.8094 | 40508.2304
CA3500579 | VINEYARD ESTATES MWC | SAN BENITO | 90 | 26 | None | 13500 | 21.0938 | 37326.9688 | 39193.3172 | 0.3 | 11198.0906 | 50391.4078 | 52759.804
CA4900665 | RUSSIAN RIVER MUTUAL WATER CO. | SONOMA | 84 | 30 | None | 12600 | 19.6875 | 36847.4375 | 38689.8094 | 0.3 | 11054.2313 | 49744.0406 | 52082.0105
CA1200541 | PHILLIPSVILLE C.S.D. | HUMBOLDT | 300 | 66 |  | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 59486.4469
CA4000744 | AFUERA DE CHORRO WATER COMPANY | SAN LUIS OBISPO | 79 | 24 |  | 11850 | 18.5156 | 36447.8281 | 38270.2195 | 0.3 | 10934.3484 | 49204.568 | 51517.1827
CA4010017 | GOLDEN STATE WATER COMPANY - LOS OSOS | SAN LUIS OBISPO | 5518 | 2684 | Some | 827700 | 1293.2812 | 471142.9062 | 494700.0516 | 0.3 | 141342.8719 | 636042.9234 | 665936.9408
CA2000692 | MD 95 RANCHOS WEST | MADERA | 150 | 27 |  | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA5000095 | SUNRISE VILLAGE MHP | STANISLAUS | 339 | 103 |  | 50850 | 79.4531 | 57227.5156 | 60088.8914 | 0 | 0 | 60088.8914 | 62913.0693
CA2300668 | POINT CABRILLO HIGHLANDS | MENDOCINO | 42 | 21 |  | 6300 | 9.8438 | 33490.7188 | 35165.2547 | 0 | 0 | 35165.2547 | 36818.0217
CA3400125 | FREEPORT MARINA | SACRAMENTO | 42 | 27 | None | 6300 | 9.8438 | 33490.7188 | 35165.2547 | 0.32 | 10717.03 | 45882.2847 | 48038.7521
CA3610053 | WESTERN HEIGHTS WATER COMPANY | SAN BERNARDINO | 7521 | 2340 | Some | 1128150 | 1762.7344 | 631226.4219 | 662787.743 | 0.3 | 189367.9266 | 852155.6695 | 892206.986
CA1900537 | OAK GROVE FAMILY PARK | LOS ANGELES | 109 | 40 |  | 16350 | 25.5469 | 38845.4844 | 40787.7586 | 0.32 | 12430.555 | 53218.3136 | 55719.5743
CA1900961 | WINTERHAVEN MOBILE ESTATES | LOS ANGELES | 56 | 20 |  | 8400 | 13.125 | 34609.625 | 36340.1062 | 0.32 | 11075.08 | 47415.1862 | 49643.7
CA4200616 | SKYLINE PARK | SANTA BARBARA | 300 | 95 |  | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0.3 | 16233.1688 | 73049.2594 | 76482.5746
CA4400684 | APTOS RIDGE MUTUAL WATER CO | SANTA CRUZ | 52 | 16 | None | 7800 | 12.1875 | 34289.9375 | 36004.4344 | 0.3 | 10286.9813 | 46291.4156 | 48467.1122
CA3600031 | BIG PINE TRACT | SAN BERNARDINO | 300 | 136 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0.3 | 16233.1688 | 73049.2594 | 76482.5746
CA3600156 | LUCERNE VALLEY MWC | SAN BERNARDINO | 275 | 69 |  | 41250 | 64.4531 | 52112.5156 | 54718.1414 | 0.3 | 15633.7547 | 70351.8961 | 73658.4352
CA2300609 | SEAFAIR ROAD AND WATER COMPANY | MENDOCINO | 50 | 31 |  | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA4500093 | RED HILL MOBILEHOME PARK | SHASTA | 35 | 24 |  | 5250 | 8.2031 | 32931.2656 | 34577.8289 | 0 | 0 | 34577.8289 | 36202.9869
CA3701408 | YUIMA MUNICIPAL WATER DISTRICT | SAN DIEGO | 350 | 106 | Some | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0.32 | 18594.13 | 79606.1191 | 83347.6067
CA2700771 | SPRINGFIELD WATER COMPANY | MONTEREY | 200 | 34 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.3 | 13835.5125 | 62259.8063 | 65186.0171
CA4000765 | VARIAN RANCH MUTUAL WATER | SAN LUIS OBISPO | 111 | 49 | None | 16650 | 26.0156 | 39005.3281 | 40955.5945 | 0.3 | 11701.5984 | 52657.193 | 55132.081
CA5410019 | IVANHOE PUBLIC UTILITY DIST | TULARE | 4495 | 1118 | None | 674250 | 1053.5156 | 389382.8281 | 408851.9695 | 0 | 0 | 408851.9695 | 428068.0121
CA3310052 | LAKE HEMET-GARNER VALLEY | RIVERSIDE | 709 | 307 | Some | 106350 | 166.1719 | 86798.6094 | 91138.5398 | 0.32 | 27775.555 | 118914.0948 | 124503.0573
CA4300516 | ALDERCROFT HEIGHTS COUNTY WATER DISTRICT | SANTA CLARA | 338 | 116 | None | 50700 | 79.2188 | 57147.5938 | 60004.9734 | 0.32 | 18287.23 | 78292.2034 | 81971.937
CA2100508 | MUIR BEACH COMMUNITY | MARIN | 336 | 161 | None | 50400 | 78.75 | 56987.75 | 59837.1375 | 0.3 | 17096.325 | 76933.4625 | 80549.3352
CA1210007 | DEL ORO WATER CO-FERNDALE | HUMBOLDT | 1998 | 785 | None | 299700 | 468.2812 | 189817.9062 | 199308.8016 | 0 | 0 | 199308.8016 | 208676.3152
CA4510015 | DEL ORO WATER CO.-JOHNSON PARK | SHASTA | 917 | 278 | None | 137550 | 214.9219 | 103422.3594 | 108593.4773 | 0 | 0 | 108593.4773 | 113697.3708
CA1400031 | RANCH ROAD ESTATES MUTUAL WATER COMPANY | INYO | 65 | 27 | Some | 9750 | 15.2344 | 35328.9219 | 37095.368 | 0 | 0 | 37095.368 | 38838.8503
CA4900799 | EL PORTAL MOBILE ESTATES | SONOMA | 200 | 122 |  | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.3 | 13835.5125 | 62259.8063 | 65186.0171
CA3400150 | DELTA CROSSING MHP | SACRAMENTO | 30 | 22 | None | 4500 | 7.0312 | 32531.6562 | 34158.2391 | 0.32 | 10410.13 | 44568.3691 | 46663.0824
CA3500550 | SAN JUSTO MUTUAL WATER COMPANY | SAN BENITO | 160 | 60 | None | 24000 | 37.5 | 42921.5 | 45067.575 | 0.3 | 12876.45 | 57944.025 | 60667.3942
CA4000749 | TERRA DE ORO WATER COMPANY | SAN LUIS OBISPO | 38 | 17 | None | 5700 | 8.9062 | 33171.0312 | 34829.5828 | 0.3 | 9951.3094 | 44780.8922 | 46885.5941
CA5400710 | BADGER HILL ESTATES | TULARE | 272 | 98 | None | 40800 | 63.75 | 51872.75 | 54466.3875 | 0 | 0 | 54466.3875 | 57026.3077
CA3301267 | FISHERMAN'S RETREAT | RIVERSIDE | 402 | 172 | None | 60300 | 94.2188 | 62262.5938 | 65375.7234 | 0.32 | 19924.03 | 85299.7534 | 89308.8418
CA0800556 | HRC C.S.D. | DEL NORTE | 150 | 54 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA4110012 | CUESTA LA HONDA GUILD INC | SAN MATEO | 832 | 297 | None | 124800 | 195 | 96629 | 101460.45 | 0.32 | 30921.28 | 132381.73 | 138603.6713
CA1200715 | GREEN DIAMOND RESOURCE COMPANY - KORBEL | HUMBOLDT | 250 | 18 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 55093.3412
CA2701364 | PEDRAZZI MWC | MONTEREY | 273 | 96 | None | 40950 | 63.9844 | 51952.6719 | 54550.3055 | 0.3 | 15585.8016 | 70136.107 | 73432.5041
CA5000061 | MARTIN'S MOBILE HOME COURT | STANISLAUS | 60 | 20 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 38399.5397
CA1200547 | MILL CREEK M.W.C. | HUMBOLDT | 65 | 36 | None | 9750 | 15.2344 | 35328.9219 | 37095.368 | 0 | 0 | 37095.368 | 38838.8503
CA5000060 | CASA DE AMIGOS MOBILE HOME PARK | STANISLAUS | 220 | 73 | Some | 33000 | 51.5625 | 47716.8125 | 50102.6531 | 0 | 0 | 50102.6531 | 52457.4778
CA4400618 | RIDGE MUTUAL WATER COMPANY | SANTA CRUZ | 240 | 76 |  | 36000 | 56.25 | 49315.25 | 51781.0125 | 0.3 | 14794.575 | 66575.5875 | 69704.6401
CA1110003 | CAL-WATER SERVICE CO.-WILLOWS | GLENN | 7153 | 2387 | Some | 1072950 | 1676.4844 | 601815.1719 | 631905.9305 | 0 | 0 | 631905.9305 | 661605.5092
CA1010017 | FCWWD #41/SHAVER LAKE | FRESNO | 2037 | 960 |  | 305550 | 477.4219 | 192934.8594 | 202581.6023 | 0 | 0 | 202581.6023 | 212102.9377
CA3301045 | BLYTHE MOBILE HOME ESTATES | RIVERSIDE | 35 | 25 |  | 5250 | 8.2031 | 32931.2656 | 34577.8289 | 0.32 | 10538.005 | 45115.8339 | 47236.2781
CA4900603 | RIEBLI MUTUAL WATER COMPANY | SONOMA | 150 | 47 | Some | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0.3 | 12636.6844 | 56865.0797 | 59537.7384
CA3301330 | INDIAN OAKS TRAILER PARK | RIVERSIDE | 90 | 63 | None | 13500 | 21.0938 | 37326.9688 | 39193.3172 | 0.32 | 11944.63 | 51137.9472 | 53541.4307
CA2010009 | BAKMAN WATER-ROLLING HILLS | MADERA | 1106 | 339 | Some | 165900 | 259.2188 | 118527.5938 | 124453.9734 | 0 | 0 | 124453.9734 | 130303.3102
CA3701961 | PINE VALLEY TRAILER PARK | SAN DIEGO | 200 | 92 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.32 | 14757.88 | 63182.1738 | 66151.7359
CA4900646 | ALEXANDER VALLEY ACRES WATER COMPANY | SONOMA | 37 | 16 | None | 5550 | 8.6719 | 33091.1094 | 34745.6648 | 0.3 | 9927.3328 | 44672.9977 | 46772.6285
CA5410007 | LSID - TONYVILLE | TULARE | 500 | 50 | None | 75000 | 117.1875 | 70094.9375 | 73599.6844 | 0 | 0 | 73599.6844 | 77058.8695
CA1600507 | HARDWICK WATER COMPANY | KINGS | 69 | 20 | None | 10350 | 16.1719 | 35648.6094 | 37431.0398 | 0 | 0 | 37431.0398 | 39190.2987
CA2710020 | PAJARO COMMUNITY SERVICES DISTRICT | MONTEREY | 6500 | 461 | Some | 975000 | 1523.4375 | 549626.1875 | 577107.4969 | 0.3 | 164887.8563 | 741995.3531 | 776869.1347
CA3600071 | CHAMISAL MWC | SAN BERNARDINO | 63 | 29 | None | 9450 | 14.7656 | 35169.0781 | 36927.532 | 0.3 | 10550.7234 | 47478.2555 | 49709.7335
CA3610032 | NEEDLES, CITY OF | SAN BERNARDINO | 5183 | 1706 | None | 777450 | 1214.7656 | 444369.0781 | 466587.532 | 0.3 | 133310.7234 | 599898.2555 | 628093.4735
CA3900569 | EL RIO MOBILE HOME PARK | SAN JOAQUIN | 60 | 28 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 38399.5397
CA1010026 | PINEDALE COUNTY WATER DISTRICT | FRESNO | 16735 | 2120 | None | 2510250 | 3922.2656 | 1367626.5781 | 1436007.907 | 0 | 0 | 1436007.907 | 1503500.2787
CA4500104 | SUNRISE MOBILEHOME PARK | SHASTA | 35 | 16 |  | 5250 | 8.2031 | 32931.2656 | 34577.8289 | 0 | 0 | 34577.8289 | 36202.9869
CA3010068 | EAST ORANGE COUNTY WD - RZ | ORANGE | 3247 | 1206 | Some | 487050 | 761.0156 | 289640.3281 | 304122.3445 | 0.3 | 86892.0984 | 391014.443 | 409392.1218
CA0900422 | CRYSTAL CAVES MHP | EL DORADO | 112 | 40 |  | 16800 | 26.25 | 39085.25 | 41039.5125 | 0.3 | 11725.575 | 52765.0875 | 55245.0466
CA2700612 | LAGUNA SECA WC | MONTEREY | 162 | 58 | None | 24300 | 37.9688 | 43081.3438 | 45235.4109 | 0.3 | 12924.4031 | 58159.8141 | 60893.3253
CA2701800 | TULARCITOS MWC | MONTEREY | 129 | 46 | None | 19350 | 30.2344 | 40443.9219 | 42466.118 | 0.3 | 12133.1766 | 54599.2945 | 57165.4614
CA2000509 | CASCADEL MUTUAL WATER SYSTEM | MADERA | 314 | 120 | Some | 47100 | 73.5938 | 55229.4688 | 57990.9422 | 0 | 0 | 57990.9422 | 60716.5165
CA2000647 | JOHN HOVANNISIAN WATER SYSTEM | MADERA | 80 | 18 |  | 12000 | 18.75 | 36527.75 | 38354.1375 | 0 | 0 | 38354.1375 | 40156.782
CA4900608 | SIX ACRES WATER COMPANY | SONOMA | 66 | 22 | None | 9900 | 15.4688 | 35408.8438 | 37179.2859 | 0.3 | 10622.6531 | 47801.9391 | 50048.6302
CA2600546 | CROWLEY LAKE MUTUAL WATER COMPANY | MONO | 175 | 57 | None | 26250 | 41.0156 | 44120.3281 | 46326.3445 | 0 | 0 | 46326.3445 | 48503.6827
CA2700509 | OAK MANOR WS | MONTEREY | 92 | 28 |  | 13800 | 21.5625 | 37486.8125 | 39361.1531 | 0.3 | 11246.0438 | 50607.1969 | 52985.7351
CA0800532 | BIG ROCK C.S.D. | DEL NORTE | 400 | 107 | NULL | 60000 | 93.75 | 62102.75 | 65207.8875 | 0 | 0 | 65207.8875 | 68272.6582
CA3100538 | ROSECREST MUTUAL | PLACER | 31 | 15 | None | 4650 | 7.2656 | 32611.5781 | 34242.157 | 0 | 0 | 34242.157 | 35851.5384
CA1000054 | LAS DELTAS MUTUAL WATER SYSTEM | FRESNO | 375 | 107 |  | 56250 | 87.8906 | 60104.7031 | 63109.9383 | 0 | 0 | 63109.9383 | 66076.1054
CA3900664 | NEW HOPE LANDING GENERAL STORE | SAN JOAQUIN | 125 | 44 | None | 18750 | 29.2969 | 40124.2344 | 42130.4461 | 0 | 0 | 42130.4461 | 44110.5771
CA1810003 | LASSEN COUNTY WATER DISTRICT #1 | LASSEN | 450 | 147 | Some | 67500 | 105.4688 | 66098.8438 | 69403.7859 | 0 | 0 | 69403.7859 | 72665.7639
CA4200837 | RANCHO YNECITA | SANTA BARBARA | 129 | 39 | Some | 19350 | 30.2344 | 40443.9219 | 42466.118 | 0.3 | 12133.1766 | 54599.2945 | 57165.4614
CA2000557 | MD 43 MIAMI CREEK KNOLLS | MADERA | 100 | 26 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA3610703 | USMC - 29 PALMS | SAN BERNARDINO | 18811 | 2480 | Some | 2821650 | 4408.8281 | 1533544.3906 | 1610221.6102 | 0.3 | 460063.3172 | 2070284.9273 | 2167588.3189
CA1500585 | OASIS PROPERTY OWNERS ASSOCIATION | KERN | 100 | 39 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA3301169 | MURRIETA PALMS MOBILE HOME PARK | RIVERSIDE | 237 | 71 | None | 35550 | 55.5469 | 49075.4844 | 51529.2586 | 0.32 | 15704.155 | 67233.4136 | 70393.384
CA3400433 | EDGEWATER MOBILE HOME PARK | SACRAMENTO | 40 | 22 |  | 6000 | 9.375 | 33330.875 | 34997.4187 | 0.32 | 10665.88 | 45663.2988 | 47809.4738
CA3301040 | RIVERDALE ESTATES | RIVERSIDE | 300 | 186 |  | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0.32 | 17315.38 | 74131.4706 | 77615.6497
CA2000849 | MD 60 DILLON ESTATES | MADERA | 150 | 38 |  | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA1010049 | BIOLA COMMUNITY SERVICES DIST | FRESNO | 1623 | 1200 |  | 243450 | 380.3906 | 159847.2031 | 167839.5633 | 0 | 0 | 167839.5633 | 175728.0228
CA3410007 | DEL PASO MANOR COUNTY WATER DI | SACRAMENTO | 4520 | 1796 | Some | 678000 | 1059.375 | 391380.875 | 410949.9188 | 0.32 | 125241.88 | 536191.7987 | 561392.8133
CA1503329 | HART CREEK ESTATES MUTUAL WATER CO. | KERN | 148 | 73 | None | 22200 | 34.6875 | 41962.4375 | 44060.5594 | 0 | 0 | 44060.5594 | 46131.4057
CA1100237 | WILLOWS MOBILE HOME COMMUNITY & RV PARK | GLENN | 190 | 87 | None | 28500 | 44.5312 | 45319.1562 | 47585.1141 | 0 | 0 | 47585.1141 | 49821.6144
CA0400036 | MOUNTAIN VIEW MHC LLC | BUTTE | 230 | 129 | None | 34500 | 53.9062 | 48516.0312 | 50941.8328 | 0 | 0 | 50941.8328 | 53336.099
CA3700909 | JULIAN COMMUNITY SERVICES DISTRICT | SAN DIEGO | 1517 | 185 | Some | 227550 | 355.5469 | 151375.4844 | 158944.2586 | 0.32 | 48440.155 | 207384.4136 | 217131.481
CA5301002 | LEWISTON COMMUNITY SERVICES DISTRICT | TRINITY | 701 | 231 | Some | 105150 | 164.2969 | 86159.2344 | 90467.1961 | 0 | 0 | 90467.1961 | 94719.1543
CA2300506 | MEADOW ESTATES MUTUAL | MENDOCINO | 100 | 35 |  | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA0500075 | LAKESIDE MOBILE ESTATES | CALAVERAS | 54 | 24 | None | 8100 | 12.6562 | 34449.7812 | 36172.2703 | 0 | 0 | 36172.2703 | 37872.367
CA3510004 | AROMAS WATER DISTRICT | SAN BENITO | 2988 | 968 | Some | 448200 | 700.3125 | 268940.5625 | 282387.5906 | 0.3 | 80682.1687 | 363069.7594 | 380134.0381
CA0410003 | DURHAM IRRIGATION DISTRICT | BUTTE | 1561 | 479 | Some | 234150 | 365.8594 | 154892.0469 | 162636.6492 | 0 | 0 | 162636.6492 | 170280.5717
CA1500409 | BROCK MUTUAL WATER COMPANY | KERN | 462 | 155 |  | 69300 | 108.2812 | 67057.9062 | 70410.8016 | 0 | 0 | 70410.8016 | 73720.1092
CA4901346 | DELORES LANE WATER SYSTEM | SONOMA | 56 | 17 | None | 8400 | 13.125 | 34609.625 | 36340.1062 | 0.3 | 10382.8875 | 46722.9938 | 48918.9745
CA1000004 | BELMONT WATER CORPORATION | FRESNO | 264 | 40 | None | 39600 | 61.875 | 51233.375 | 53795.0437 | 0 | 0 | 53795.0437 | 56323.4108
CA4300560 | GREEN MOUNTAIN WATER COMPANY | SANTA CLARA | 80 | 38 | None | 12000 | 18.75 | 36527.75 | 38354.1375 | 0.32 | 11688.88 | 50043.0175 | 52395.0393
CA5410038 | TERRA BELLA IRRIGATION DISTRICT - TBT | TULARE | 4957 | 803 | None | 743550 | 1161.7969 | 426306.7344 | 447622.0711 | 0 | 0 | 447622.0711 | 468660.3084
CA1910117 | MONTEBELLO-CITY, WATER DEPT. | LOS ANGELES | 8157 | 1503 | None | 1223550 | 1911.7969 | 682056.7344 | 716159.5711 | 0.32 | 218258.155 | 934417.7261 | 978335.3592
CA5400754 | SOUTH KAWEAH MUTUAL WATER COMPANY | TULARE | 384 | 138 | None | 57600 | 90 | 60824 | 63865.2 | 0 | 0 | 63865.2 | 66866.8644
CA5401003 | EAST OROSI CSD | TULARE | 932 | 103 |  | 139800 | 218.4375 | 104621.1875 | 109852.2469 | 0 | 0 | 109852.2469 | 115015.3025
CA4900647 | SERENO DEL MAR WATER COMPANY (PUC) | SONOMA | 435 | 136 | None | 65250 | 101.9531 | 64900.0156 | 68145.0164 | 0.3 | 19470.0047 | 87615.0211 | 91732.9271
CA4510002 | MOUNTAIN GATE C.S.D. | SHASTA | 2227 | 669 | Some | 334050 | 521.9531 | 208120.0156 | 218526.0164 | 0 | 0 | 218526.0164 | 228796.7392
CA2900548 | SIERRA ESTATES MUTUAL WATER COMPANY | NEVADA | 100 | 32 |  | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA5400665 | DEL ORO RIVER ISLAND SERV TERR #1 | TULARE | 1296 | 397 | None | 194400 | 303.75 | 133712.75 | 140398.3875 | 0 | 0 | 140398.3875 | 146997.1117
CA3400107 | RIVER'S EDGE MARINA & RESORT | SACRAMENTO | 150 | 83 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0.32 | 13479.13 | 57707.5253 | 60419.779
CA3600187 | OLIVE DELL RANCH | SAN BERNARDINO | 350 | 100 | Some | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0.3 | 17431.9969 | 78443.9859 | 82130.8533
CA5210003 | LOS MOLINOS COMM. SERVICES DIST. | TEHAMA | 1450 | 376 | Some | 217500 | 339.8438 | 146020.7188 | 153321.7547 | 0 | 0 | 153321.7547 | 160527.8772
CA5800572 | FAIRWAY DOWNS MUTUAL WATER CO | YUBA | 100 | 27 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA1800511 | LAKE FOREST MUTUAL W.C. | LASSEN | 565 | 220 | None | 84750 | 132.4219 | 75289.8594 | 79054.3523 | 0 | 0 | 79054.3523 | 82769.9069
CA4010015 | MORRO ROCK MUTUAL WATER CO | SAN LUIS OBISPO | 1881 | 649 | None | 282150 | 440.8594 | 180467.0469 | 189490.3992 | 0.3 | 54140.1141 | 243630.5133 | 255081.1474
CA1000369 | ZONNEVELD DAIRY - CEDAR | FRESNO | 70 | 15 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0 | 0 | 37514.9578 | 39278.1608
CA1400005 | OWENS VALLEY WATER COMPANY | INYO | 300 | 111 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 59486.4469
CA5500074 | SIERRA VILLAGE MUTUAL WATER CO | TUOLUMNE | 272 | 129 | None | 40800 | 63.75 | 51872.75 | 54466.3875 | 0 | 0 | 54466.3875 | 57026.3077
CA2701423 | ECHO VALLEY RD WS #05 | MONTEREY | 45 | 16 | None | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0.3 | 10119.1453 | 45536.1539 | 47676.3531
CA1900520 | THE VILLAGE MOBILE HOME PARK | LOS ANGELES | 50 | 34 |  | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0.32 | 10921.63 | 46758.2284 | 48955.8652
CA2701515 | MOSS LANDING HARBOR WS | MONTEREY | 402 | 143 | None | 60300 | 94.2188 | 62262.5938 | 65375.7234 | 0.3 | 18678.7781 | 84054.5016 | 88005.0631
CA4901381 | LICHAU HYLANDS MUTUAL WATER COMPANY | SONOMA | 56 | 20 | None | 8400 | 13.125 | 34609.625 | 36340.1062 | 0.3 | 10382.8875 | 46722.9938 | 48918.9745
CA4200862 | MESA HILLS MUTUAL WATER COMPANY | SANTA BARBARA | 54 | 18 |  | 8100 | 12.6562 | 34449.7812 | 36172.2703 | 0.3 | 10334.9344 | 46507.2047 | 48693.0433
CA5500353 | SIERRA VILLAGE MOBILE HOME PARK | TUOLUMNE | 30 | 30 | None | 4500 | 7.0312 | 32531.6562 | 34158.2391 | 0 | 0 | 34158.2391 | 35763.6763
CA2800516 | TUCKER ACRES MUTUAL WATER CO. | NAPA | 200 | 23 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.3 | 13835.5125 | 62259.8063 | 65186.0171
CA5000433 | OID-OAKDALE RURAL WATER SYSTEM #1 | STANISLAUS | 1570 | 476 | Some | 235500 | 367.9688 | 155611.3438 | 163391.9109 | 0 | 0 | 163391.9109 | 171071.3308
CA5400536 | KINGS RIVER ESTATES MUTUAL WATER COMPANY | TULARE | 106 | 38 | None | 15900 | 24.8438 | 38605.7188 | 40536.0047 | 0 | 0 | 40536.0047 | 42441.1969
CA2700579 | ELKHORN RD WS #04 | MONTEREY | 60 | 20 |  | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA3900543 | MAURLAND MANOR WATER SYSTEM | SAN JOAQUIN | 110 | 28 |  | 16500 | 25.7812 | 38925.4062 | 40871.6766 | 0 | 0 | 40871.6766 | 42792.6454
CA3210001 | IVCSD-GREENVILLE | PLUMAS | 1129 | 576 | Some | 169350 | 264.6094 | 120365.7969 | 126384.0867 | 0 | 0 | 126384.0867 | 132324.1388
CA3400137 | LINCOLN CHAN-HOME RANCH | SACRAMENTO | 33 | 19 | None | 4950 | 7.7344 | 32771.4219 | 34409.993 | 0.32 | 10486.855 | 44896.848 | 47006.9998
CA0400020 | PLEASANT GROVE MHP | BUTTE | 327 | 88 | None | 49050 | 76.6406 | 56268.4531 | 59081.8758 | 0 | 0 | 59081.8758 | 61858.7239
CA3500904 | HOLLISTER RANCH ESTATES | SAN BENITO | 150 | 37 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0.3 | 12636.6844 | 56865.0797 | 59537.7384
CA1200706 | TRINIDAD EXTENDED STAY RV | HUMBOLDT | 130 | 72 | None | 19500 | 30.4688 | 40523.8438 | 42550.0359 | 0 | 0 | 42550.0359 | 44549.8876
CA1400004 | CHARLES BROWN WATER COMPANY | INYO | 242 | 31 | None | 36300 | 56.7188 | 49475.0938 | 51948.8484 | 0 | 0 | 51948.8484 | 54390.4443
CA1000378 | SUNSET WEST COMMUNITY LLC | FRESNO | 350 | 159 | None | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0 | 0 | 61011.9891 | 63879.5525
CA4900871 | DE ANZA MOON VALLEY WATER COMPANY | SONOMA | 691 | 247 |  | 103650 | 161.9531 | 85360.0156 | 89628.0164 | 0.3 | 25608.0047 | 115236.0211 | 120652.1141
CA1000244 | SHADY LAKES MOBILE HOME PARK | FRESNO | 160 | 65 | None | 24000 | 37.5 | 42921.5 | 45067.575 | 0 | 0 | 45067.575 | 47185.751
CA3900721 | WOODBRIDGE MOBILE ESTATES | SAN JOAQUIN | 110 | 37 |  | 16500 | 25.7812 | 38925.4062 | 40871.6766 | 0 | 0 | 40871.6766 | 42792.6454
CA5601116 | SAN CAYETANO MUTUAL WATER CO | VENTURA | 46 | 50 | Some | 6900 | 10.7812 | 33810.4062 | 35500.9266 | 0.32 | 10819.33 | 46320.2566 | 48497.3086
CA2210901 | MPWD-COULTERVILLE CSA 1 | MARIPOSA | 193 | 98 | None | 28950 | 45.2344 | 45558.9219 | 47836.868 | 0 | 0 | 47836.868 | 50085.2008
CA1400144 | SUNLAND VILLAGE MOBILE HOME PARK | INYO | 42 | 26 | None | 6300 | 9.8438 | 33490.7188 | 35165.2547 | 0 | 0 | 35165.2547 | 36818.0217
CA1610001 | ARMONA COMMUNITY SERVICES DIST | KINGS | 4143 | 1246 | Some | 621450 | 971.0156 | 361250.3281 | 379312.8445 | 0 | 0 | 379312.8445 | 397140.5482
CA3100043 | GOLD HILL MOBILEHOME PARK | PLACER | 75 | 32 |  | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0 | 0 | 37934.5477 | 39717.4714
CA1009023 | BRITZ/COLUSA | FRESNO | 85 | 15 | None | 12750 | 19.9219 | 36927.3594 | 38773.7273 | 0 | 0 | 38773.7273 | 40596.0925
CA2910011 | PLAVADA COMMUNITY ASSOCIATION | NEVADA | 359 | 255 | Some | 53850 | 84.1406 | 58825.9531 | 61767.2508 | 0 | 0 | 61767.2508 | 64670.3116
CA5000082 | 4N MOBILEHOME PARK | STANISLAUS | 65 | 31 |  | 9750 | 15.2344 | 35328.9219 | 37095.368 | 0 | 0 | 37095.368 | 38838.8503
CA1000056 | MEADOW LAKES CLUB | FRESNO | 240 | 120 | None | 36000 | 56.25 | 49315.25 | 51781.0125 | 0 | 0 | 51781.0125 | 54214.7201
CA1910147 | SATIVA WATER SYSTEM | LOS ANGELES | 6837 | 1643 | None | 1025550 | 1602.4219 | 576559.8594 | 605387.8523 | 0.32 | 184499.155 | 789887.0073 | 827011.6967
CA1310700 | NAF EL CENTRO | IMPERIAL | 972 | 386 |  | 145800 | 227.8125 | 107818.0625 | 113208.9656 | 0 | 0 | 113208.9656 | 118529.787
CA5000010 | TID/ LA GRANGE WATER SYSTEM | STANISLAUS | 195 | 59 | Some | 29250 | 45.7031 | 45718.7656 | 48004.7039 | 0 | 0 | 48004.7039 | 50260.925
CA1900075 | BLEICH FLATS MUTUAL | LOS ANGELES | 93 | 34 |  | 13950 | 21.7969 | 37566.7344 | 39445.0711 | 0.32 | 12021.355 | 51466.4261 | 53885.3481
CA3400103 | B & W RESORT MARINA | SACRAMENTO | 100 | 37 | Some | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.32 | 12200.38 | 52232.8769 | 54687.8221
CA2701906 | LAKE SAN ANTONIO PARK WS | MONTEREY | 54 | 30 | None | 8100 | 12.6562 | 34449.7812 | 36172.2703 | 0.3 | 10334.9344 | 46507.2047 | 48693.0433
CA4900521 | GILL CREEK MUTUAL WATER COMPANY | SONOMA | 232 | 92 | None | 34800 | 54.375 | 48675.875 | 51109.6687 | 0.3 | 14602.7625 | 65712.4312 | 68800.9155
CA4500255 | SACRAMENTO RIVER RV PARK | SHASTA | 382 | 156 | None | 57300 | 89.5312 | 60664.1562 | 63697.3641 | 0 | 0 | 63697.3641 | 66691.1402
CA5000067 | TULLY MOBILE ESTATES | STANISLAUS | 40 | 15 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0 | 0 | 34997.4187 | 36642.2974
CA3900563 | GAYLA MANOR PWS | SAN JOAQUIN | 146 | 54 | None | 21900 | 34.2188 | 41802.5938 | 43892.7234 | 0 | 0 | 43892.7234 | 45955.6814
CA3910017 | SAN JOAQUIN COUNTY-MOKELUMNE ACRES | SAN JOAQUIN | 3800 | 1151 | Some | 570000 | 890.625 | 333837.125 | 350528.9813 | 0 | 0 | 350528.9813 | 367003.8434
CA3200188 | GREENHORN CREEK CSD | PLUMAS | 280 | 136 | None | 42000 | 65.625 | 52512.125 | 55137.7312 | 0 | 0 | 55137.7312 | 57729.2046
CA3900722 | MORADA ESTATES PWS | SAN JOAQUIN | 158 | 88 | None | 23700 | 37.0312 | 42761.6562 | 44899.7391 | 0 | 0 | 44899.7391 | 47010.0268
CA5200510 | RIVER RANCH MOBILE HOME PARK | TEHAMA | 305 | 109 |  | 45750 | 71.4844 | 54510.1719 | 57235.6805 | 0 | 0 | 57235.6805 | 59925.7575
CA4900687 | BROOKWOOD MOBILE HOME PARK | SONOMA | 400 | 202 | None | 60000 | 93.75 | 62102.75 | 65207.8875 | 0.3 | 18630.825 | 83838.7125 | 87779.132
CA4910023 | CALIFORNIA-AMERICAN LARKFIELD (PUC) | SONOMA | 7524 | 2284 | None | 1128600 | 1763.4375 | 631466.1875 | 663039.4969 | 0.3 | 189439.8563 | 852479.3531 | 892545.8827
CA1500556 | HART FLAT BEAR MUTUAL WATER | KERN | 56 | 28 | Some | 8400 | 13.125 | 34609.625 | 36340.1062 | 0 | 0 | 36340.1062 | 38048.0912
CA1900721 | TERRA NOVA MOBILE HOME PARK | LOS ANGELES | 140 | 75 | None | 21000 | 32.8125 | 41323.0625 | 43389.2156 | 0.32 | 13223.38 | 56612.5956 | 59273.3876
CA1300572 | VALLEY MOBILE HOME PARK | IMPERIAL | 70 | 22 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0 | 0 | 37514.9578 | 39278.1608
CA4200827 | SANTA YNEZ ROBLAR MOBILE HOME PARK | SANTA BARBARA | 25 | 19 | None | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0.3 | 9639.6141 | 43378.2633 | 45417.0417
CA5500149 | COLUMBIA MOBILE HOME PARK | TUOLUMNE | 88 | 63 | None | 13200 | 20.625 | 37167.125 | 39025.4812 | 0 | 0 | 39025.4812 | 40859.6789
CA4300994 | COYOTE VALLEY RV RESORT | SANTA CLARA | 500 | 129 | None | 75000 | 117.1875 | 70094.9375 | 73599.6844 | 0.32 | 22430.38 | 96030.0644 | 100543.4774
CA3301018 | ANZA PINES MOBILE HOME PARK | RIVERSIDE | 150 | 47 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0.32 | 13479.13 | 57707.5253 | 60419.779
CA3610085 | SAN ANTONIO WATER COMPANY | SAN BERNARDINO | 3371 | 1214 | None | 505650 | 790.0781 | 299550.6406 | 314528.1727 | 0.3 | 89865.1922 | 404393.3648 | 423399.853
CA2000549 | MD 05 MOUNTAIN RANCHES | MADERA | 239 | 27 |  | 35850 | 56.0156 | 49235.3281 | 51697.0945 | 0 | 0 | 51697.0945 | 54126.858
CA5601105 | FILLMORE IRRIGATION CO | VENTURA | 353 | 236 | Some | 52950 | 82.7344 | 58346.4219 | 61263.743 | 0.32 | 18670.855 | 79934.598 | 83691.5241
CA4900675 | ROSELAND MOBILE HOME PARK | SONOMA | 130 | 70 | None | 19500 | 30.4688 | 40523.8438 | 42550.0359 | 0.3 | 12157.1531 | 54707.1891 | 57278.4269
CA5100112 | TIERRA BUENA MHP #1 | SUTTER | 50 | 17 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA1310801 | CENTINELA STATE PRISON | IMPERIAL | 4600 | 2001 | Some | 690000 | 1078.125 | 397774.625 | 417663.3563 | 0 | 0 | 417663.3563 | 437293.534
CA1500341 | SIERRA BELLA MUTUAL WATER COMPANY | KERN | 60 | 180 |  | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 38399.5397
CA3600222 | JUNIPER RIVIERA CWD | SAN BERNARDINO | 441 | 250 | None | 66150 | 103.3594 | 65379.5469 | 68648.5242 | 0.3 | 19613.8641 | 88262.3883 | 92410.7205
CA2700842 | BAUMANN RD WS #01 | MONTEREY | 40 | 17 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0.3 | 9999.2625 | 44996.6813 | 47111.5253
CA3610118 | APPLE VALLEY RANCHOS WATER CO - YERMO | SAN BERNARDINO | 1033 | 316 | Some | 154950 | 242.1094 | 112693.2969 | 118327.9617 | 0.3 | 33807.9891 | 152135.9508 | 159286.3405
CA1000019 | FCSA #30/EL PORVENIR | FRESNO | 241 | 56 | None | 36150 | 56.4844 | 49395.1719 | 51864.9305 | 0 | 0 | 51864.9305 | 54302.5822
CA3210007 | WEST ALMANOR M.W.C. | PLUMAS | 1394 | 500 | Some | 209100 | 326.7188 | 141545.0938 | 148622.3484 | 0 | 0 | 148622.3484 | 155607.5988
CA3710039 | PINE VALLEY MUTUAL WC | SAN DIEGO | 2500 | 719 | Some | 375000 | 585.9375 | 229938.6875 | 241435.6219 | 0.32 | 73580.38 | 315016.0019 | 329821.754
CA5201147 | GOLDEN MEADOWS CSD | TEHAMA | 102 | 49 |  | 15300 | 23.9062 | 38286.0312 | 40200.3328 | 0 | 0 | 40200.3328 | 42089.7485
CA4010081 | WOODLANDS DEVELOPMENT | SAN LUIS OBISPO | 2918 | 1276 | None | 437700 | 683.9062 | 263346.0312 | 276513.3328 | 0.3 | 79003.8094 | 355517.1422 | 372226.4479
CA1000260 | SANDY CREEK VILLAGE MHP | FRESNO | 88 | 45 | Some | 13200 | 20.625 | 37167.125 | 39025.4812 | 0 | 0 | 39025.4812 | 40859.6789
CA5400567 | TOOLEVILLE MUTUAL NON PROFIT WATER ASSOC | TULARE | 340 | 77 | None | 51000 | 79.6875 | 57307.4375 | 60172.8094 | 0 | 0 | 60172.8094 | 63000.9314
CA3301528 | OAK HAVEN ASSOCIATION | RIVERSIDE | 92 | 36 | None | 13800 | 21.5625 | 37486.8125 | 39361.1531 | 0.32 | 11995.78 | 51356.9331 | 53770.709
CA0707615 | DOUBLETREE RANCH WATER SYSTEM | CONTRA COSTA | 49 | 20 |  | 7350 | 11.4844 | 34050.1719 | 35752.6805 | 0.3 | 10215.0516 | 45967.732 | 48128.2154
CA2701036 | APPLE AVE WS #03 | MONTEREY | 60 | 20 |  | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA5800820 | RIVER HIGHLANDS CSD | YUBA | 200 | 84 |  | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA3900682 | LOCKEFORD MOBILE HOME PARK WTR SYS | SAN JOAQUIN | 100 | 43 |  | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA1100405 | BLACK BUTTE MOBILE H.P. | GLENN | 148 | 49 |  | 22200 | 34.6875 | 41962.4375 | 44060.5594 | 0 | 0 | 44060.5594 | 46131.4057
CA1900542 | LOS ANGELES, CITY OF - POWER PLANT #2 | LOS ANGELES | 41 | 16 | None | 6150 | 9.6094 | 33410.7969 | 35081.3367 | 0.32 | 10691.455 | 45772.7917 | 47924.1129
CA5700615 | YOLO CO HOUSING AUTHORITY-EL RIO VILLA | YOLO | 432 | 113 | Some | 64800 | 101.25 | 64660.25 | 67893.2625 | 0 | 0 | 67893.2625 | 71084.2458
CA1500494 | WILSON ROAD WATER COMMUNITY | KERN | 66 | 20 | None | 9900 | 15.4688 | 35408.8438 | 37179.2859 | 0 | 0 | 37179.2859 | 38926.7124
CA1500535 | MANON MANOR MUTUAL WATER COMPANY | KERN | 200 | 55 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA3600306 | THUNDERBIRD CWD | SAN BERNARDINO | 997 | 302 | None | 149550 | 233.6719 | 109816.1094 | 115306.9148 | 0.3 | 32944.8328 | 148251.7477 | 155219.5798
CA2702405 | JENSEN MHP WS | MONTEREY | 56 | 26 | None | 8400 | 13.125 | 34609.625 | 36340.1062 | 0.3 | 10382.8875 | 46722.9938 | 48918.9745
CA4000506 | WOODLAND PARK MUTUAL WATER CO | SAN LUIS OBISPO | 534 | 162 | None | 80100 | 125.1562 | 72812.2812 | 76452.8953 | 0.3 | 21843.6844 | 98296.5797 | 102916.5189
CA3010082 | SERRANO WATER DISTRICT | ORANGE | 5895 | 2254 | Some | 884250 | 1381.6406 | 501273.4531 | 526337.1258 | 0.3 | 150382.0359 | 676719.1617 | 708524.9623
CA2010011 | MADERA CO SA1-INDIAN LAKES | MADERA | 1562 | 473 |  | 234300 | 366.0938 | 154971.9688 | 162720.5672 | 0 | 0 | 162720.5672 | 170368.4338
CA3600260 | SMILEY PARK COUNTRY CLUB | SAN BERNARDINO | 530 | 102 | None | 79500 | 124.2188 | 72492.5938 | 76117.2234 | 0.3 | 21747.7781 | 97865.0016 | 102464.6566
CA4010010 | SAN MIGUEL COMMUNITY SERVICES DISTRICT | SAN LUIS OBISPO | 2600 | 923 | Some | 390000 | 609.375 | 237930.875 | 249827.4188 | 0.3 | 71379.2625 | 321206.6813 | 336303.3953
CA4500022 | DEL ORO WATER CO. - HAT CREEK DISTRICT | SHASTA | 205 | 62 | None | 30750 | 48.0469 | 46517.9844 | 48843.8836 | 0 | 0 | 48843.8836 | 51139.5461
CA3600785 | LAKE JODIE WATER SYSTEM | SAN BERNARDINO | 250 | 50 |  | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0.3 | 15034.3406 | 67654.5328 | 70834.2959
CA2100565 | GREEN GULCH FARM | MARIN | 75 | 17 | Some | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0.3 | 10838.4422 | 48772.9898 | 51065.3204
CA5610700 | NAVAL BASE VENTURA COUNTY, POINT MUGU | VENTURA | 1700 | 928 |  | 255000 | 398.4375 | 166001.1875 | 174301.2469 | 0.32 | 53120.38 | 227421.6269 | 238110.4433
CA1610009 | KETTLEMAN CITY CSD | KINGS | 1450 | 354 | Some | 217500 | 339.8438 | 146020.7188 | 153321.7547 | 0 | 0 | 153321.7547 | 160527.8772
CA1900942 | ALPINE SPRINGS MOBILE HOME PARK | LOS ANGELES | 175 | 53 | None | 26250 | 41.0156 | 44120.3281 | 46326.3445 | 0.32 | 14118.505 | 60444.8495 | 63285.7575
CA1910085 | MAYWOOD MUTUAL WATER CO. #2 | LOS ANGELES | 7118 | 1924 | Some | 1067700 | 1668.2812 | 599017.9062 | 628968.8016 | 0.32 | 191685.73 | 820654.5316 | 859225.2945
CA5410513 | NPS-ASH MOUNTAIN | TULARE | 2930 | 45 | None | 439500 | 686.7188 | 264305.0938 | 277520.3484 | 0 | 0 | 277520.3484 | 290563.8048
CA1907014 | NORTH TRAILS MUTUAL WATER COMPANY | LOS ANGELES | 100 | 49 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.32 | 12200.38 | 52232.8769 | 54687.8221
CA3910014 | SAN JOAQUIN COUNTY-RAYMUS VILLAGE | SAN JOAQUIN | 1082 | 329 | Some | 162300 | 253.5938 | 116609.4688 | 122439.9422 | 0 | 0 | 122439.9422 | 128194.6195
CA3900927 | SPRING CREEK ESTATES PWS | SAN JOAQUIN | 90 | 36 | None | 13500 | 21.0938 | 37326.9688 | 39193.3172 | 0 | 0 | 39193.3172 | 41035.4031
CA2702140 | WOODSIDE WA | MONTEREY | 73 | 26 | None | 10950 | 17.1094 | 35968.2969 | 37766.7117 | 0.3 | 10790.4891 | 48557.2008 | 50839.3892
CA5000066 | MODESTO MOBILE HOME PARK | STANISLAUS | 300 | 150 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 59486.4469
CA1500478 | VALLEY ESTATES POA, INC. | KERN | 386 | 117 | Some | 57900 | 90.4688 | 60983.8438 | 64033.0359 | 0 | 0 | 64033.0359 | 67042.5886
CA4400559 | SUMMIT MUTUAL WATER COMPANY | SANTA CRUZ | 152 | 54 |  | 22800 | 35.625 | 42282.125 | 44396.2312 | 0.3 | 12684.6375 | 57080.8688 | 59763.6696
CA5510016 | SIERRA PARK WATER COMPANY, INC. | TUOLUMNE | 300 | 347 | Some | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 59486.4469
CA2702073 | SAN MIGUEL WS #22 | MONTEREY | 93 | 31 | None | 13950 | 21.7969 | 37566.7344 | 39445.0711 | 0.3 | 11270.0203 | 50715.0914 | 53098.7007
CA1000257 | MT ARARAT MOBILE HOME PARK | FRESNO | 43 | 36 | Some | 6450 | 10.0781 | 33570.6406 | 35249.1727 | 0 | 0 | 35249.1727 | 36905.8838
CA4901221 | GRATON MUTUAL (GREEN VALLEY HOA) | SONOMA | 50 | 16 |  | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0.3 | 10239.0281 | 46075.6266 | 48241.181
CA4400572 | FERN GROVE WATER CLUB | SANTA CRUZ | 182 | 67 | Some | 27300 | 42.6562 | 44679.7812 | 46913.7703 | 0.3 | 13403.9344 | 60317.7047 | 63152.6368
CA3301283 | GLEN EDEN SUN CLUB | RIVERSIDE | 495 | 407 | Some | 74250 | 116.0156 | 69695.3281 | 73180.0945 | 0.32 | 22302.505 | 95482.5995 | 99970.2817
CA3910800 | DEUEL VOCATIONAL INSTITUTION | SAN JOAQUIN | 3271 | 1688 | Some | 490650 | 766.6406 | 291558.4531 | 306136.3758 | 0 | 0 | 306136.3758 | 320524.7854
CA4210022 | GOLDEN STATE WATER COMPANY - LAKE MARIE | SANTA BARBARA | 527 | 206 |  | 79050 | 123.5156 | 72252.8281 | 75865.4695 | 0.3 | 21675.8484 | 97541.318 | 102125.7599
CA2300606 | LAKE VIEW MUTUAL WATER CO. | MENDOCINO | 90 | 29 |  | 13500 | 21.0938 | 37326.9688 | 39193.3172 | 0 | 0 | 39193.3172 | 41035.4031
CA0800552 | NORTHCREST TRAILER CITY | DEL NORTE | 250 | 89 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 55093.3412
CA2700534 | COLONIAL OAK WC INC | MONTEREY | 198 | 66 |  | 29700 | 46.4062 | 45958.5312 | 48256.4578 | 0.3 | 13787.5594 | 62044.0172 | 64960.086
CA3400397 | LAGUNA VILLAGE RV PARK | SACRAMENTO | 32 | 28 | None | 4800 | 7.5 | 32691.5 | 34326.075 | 0.32 | 10461.28 | 44787.355 | 46892.3607
CA4510013 | SHASTA C.S.D. | SHASTA | 1584 | 480 |  | 237600 | 371.25 | 156730.25 | 164566.7625 | 0 | 0 | 164566.7625 | 172301.4003
CA4900634 | HUCKLEBERRY MUTUAL WATER COMPANY | SONOMA | 45 | 29 | None | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0.3 | 10119.1453 | 45536.1539 | 47676.3531
CA5400523 | EL MONTE VILLAGE MHP | TULARE | 100 | 47 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA0707556 | SANDMOUND MUTUAL | CONTRA COSTA | 160 | 103 | None | 24000 | 37.5 | 42921.5 | 45067.575 | 0.3 | 12876.45 | 57944.025 | 60667.3942
CA2701898 | CLEAR RIDGE WA | MONTEREY | 123 | 41 | None | 18450 | 28.8281 | 39964.3906 | 41962.6102 | 0.3 | 11989.3172 | 53951.9273 | 56487.6679
CA2610002 | JUNE LAKE PUD VILLAGE | MONO | 2740 | 293 | Some | 411000 | 642.1875 | 249119.9375 | 261575.9344 | 0 | 0 | 261575.9344 | 273870.0033
CA3701341 | QUIET OAKS MOBILE HOME PARK | SAN DIEGO | 120 | 45 |  | 18000 | 28.125 | 39724.625 | 41710.8562 | 0.32 | 12711.88 | 54422.7363 | 56980.6049
CA3700918 | RANCHO SANTA TERESA MW CO. | SAN DIEGO | 95 | 37 |  | 14250 | 22.2656 | 37726.5781 | 39612.907 | 0.32 | 12072.505 | 51685.412 | 54114.6264
CA3600258 | SKY FOREST MWC | SAN BERNARDINO | 605 | 159 | None | 90750 | 141.7969 | 78486.7344 | 82411.0711 | 0.3 | 23546.0203 | 105957.0914 | 110937.0747
CA4300573 | GREEN ACRES MUTUAL WATER | SANTA CLARA | 53 | 19 | None | 7950 | 12.4219 | 34369.8594 | 36088.3523 | 0.32 | 10998.355 | 47086.7073 | 49299.7826
CA2701888 | CACHAGUA MUTUAL WS (#4) | MONTEREY | 55 | 24 | None | 8250 | 12.8906 | 34529.7031 | 36256.1883 | 0.3 | 10358.9109 | 46615.0992 | 48806.0089
CA5200555 | RIO RANCH COMMUNITY SVCS DIST | TEHAMA | 44 | 30 |  | 6600 | 10.3125 | 33650.5625 | 35333.0906 | 0 | 0 | 35333.0906 | 36993.7459
CA2500911 | I'SOT WELL #3 & #15 | MODOC | 215 | 53 | Some | 32250 | 50.3906 | 47317.2031 | 49683.0633 | 0 | 0 | 49683.0633 | 52018.1673
CA4500012 | CASCADE RACQUET CLUB MUTUAL WATER | SHASTA | 89 | 27 | None | 13350 | 20.8594 | 37247.0469 | 39109.3992 | 0 | 0 | 39109.3992 | 40947.541
CA5500019 | JENNESS PARK CHRISTIAN CAMP | TUOLUMNE | 505 | 43 | Some | 75750 | 118.3594 | 70494.5469 | 74019.2742 | 0 | 0 | 74019.2742 | 77498.1801
CA2700773 | SUNNY MESA WATER SYSTEM | MONTEREY | 880 | 267 | None | 132000 | 206.25 | 100465.25 | 105488.5125 | 0.3 | 30139.575 | 135628.0875 | 142002.6076
CA5200527 | HUNTER'S FISHING RESORT | TEHAMA | 50 | 47 |  | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA4300637 | LOS RANCHOS DE UVAS WATER COMPANY | SANTA CLARA | 58 | 21 | None | 8700 | 13.5938 | 34769.4688 | 36507.9422 | 0.32 | 11126.23 | 47634.1722 | 49872.9783
CA3901276 | HANOT FOUNDATION INC | SAN JOAQUIN | 38 | 15 | Some | 5700 | 8.9062 | 33171.0312 | 34829.5828 | 0 | 0 | 34829.5828 | 36466.5732
CA2710012 | CWSC SALINAS HILLS | MONTEREY | 8213 | 1632 | Some | 1231950 | 1924.9219 | 686532.3594 | 720858.9773 | 0.3 | 205959.7078 | 926818.6852 | 970379.1634
CA1900523 | WHITE FENCE FARMS MWC NO.3 | LOS ANGELES | 749 | 253 | None | 112350 | 175.5469 | 89995.4844 | 94495.2586 | 0.32 | 28798.555 | 123293.8136 | 129088.6228
CA5101009 | WILDWOOD EAST MUTUAL | SUTTER | 350 | 48 | None | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0 | 0 | 61011.9891 | 63879.5525
CA4410016 | FOREST LAKES MWC | SANTA CRUZ | 1067 | 326 | Some | 160050 | 250.0781 | 115410.6406 | 121181.1727 | 0.3 | 34623.1922 | 155804.3648 | 163127.17
CA5400880 | THE LAKES ASSOCIATION | TULARE | 495 | 161 | Some | 74250 | 116.0156 | 69695.3281 | 73180.0945 | 0 | 0 | 73180.0945 | 76619.559
CA2700634 | CHETMOORE ACRES WA | MONTEREY | 70 | 25 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0.3 | 10718.5594 | 48233.5172 | 50500.4925
CA5400506 | NORTH KAWEAH MWC | TULARE | 560 | 71 |  | 84000 | 131.25 | 74890.25 | 78634.7625 | 0 | 0 | 78634.7625 | 82330.5963
CA3500556 | MISSION FARM R.V. PARK | SAN BENITO | 110 | 173 | None | 16500 | 25.7812 | 38925.4062 | 40871.6766 | 0.3 | 11677.6219 | 52549.2984 | 55019.1155
CA4400645 | HIDDEN MEADOW MUTUAL WATER CO | SANTA CRUZ | 45 | 18 | None | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0.3 | 10119.1453 | 45536.1539 | 47676.3531
CA3900835 | WAYSIDE MOTEL APARTMENTS WTR SYS | SAN JOAQUIN | 70 | 25 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0 | 0 | 37514.9578 | 39278.1608
CA2910010 | TRUCKEE-DONNER PUD - HIRSCHDALE | NEVADA | 85 | 26 | None | 12750 | 19.9219 | 36927.3594 | 38773.7273 | 0 | 0 | 38773.7273 | 40596.0925
CA5000317 | OID #51 - SUNSET OAKS #10 | STANISLAUS | 287 | 82 | None | 43050 | 67.2656 | 53071.5781 | 55725.157 | 0 | 0 | 55725.157 | 58344.2394
CA3600012 | APPLE VALLEY VIEW MWC | SAN BERNARDINO | 275 | 81 | None | 41250 | 64.4531 | 52112.5156 | 54718.1414 | 0.3 | 15633.7547 | 70351.8961 | 73658.4352
CA1400045 | PRIMROSE LANE APARTMENTS | INYO | 73 | 26 | None | 10950 | 17.1094 | 35968.2969 | 37766.7117 | 0 | 0 | 37766.7117 | 39541.7472
CA1500560 | KRANENBURG WATER SYSTEM | KERN | 42 | 15 | None | 6300 | 9.8438 | 33490.7188 | 35165.2547 | 0 | 0 | 35165.2547 | 36818.0217
CA5510025 | TUD - PHOENIX LAKE PARK | TUOLUMNE | 119 | 57 | NULL | 17850 | 27.8906 | 39644.7031 | 41626.9383 | 0 | 0 | 41626.9383 | 43583.4044
CA1000021 | FCSA #05/WILDWOOD ISLAND | FRESNO | 417 | 149 | None | 62550 | 97.7344 | 63461.4219 | 66634.493 | 0 | 0 | 66634.493 | 69766.3141
CA1400007 | SIERRA HIGHLAND CSD | INYO | 600 | 215 | Some | 90000 | 140.625 | 78087.125 | 81991.4812 | 0 | 0 | 81991.4812 | 85845.0809
CA3901304 | ENCLAVE AT THE DELTA | SAN JOAQUIN | 39 | 15 | Some | 5850 | 9.1406 | 33250.9531 | 34913.5008 | 0 | 0 | 34913.5008 | 36554.4353
CA3310047 | CABAZON WATER DISTRICT | RIVERSIDE | 2588 | 969 | Some | 388200 | 606.5625 | 236971.8125 | 248820.4031 | 0.32 | 75830.98 | 324651.3831 | 339909.9981
CA1510013 | MCFARLAND, CITY OF | KERN | 15506 | 2849 | Some | 2325900 | 3634.2188 | 1269402.5938 | 1332872.7234 | 0 | 0 | 1332872.7234 | 1395517.7414
CA2000608 | WILDWOOD MOBILE HOME PK INC | MADERA | 100 | 68 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA0300053 | RANCHO DEL ORO | AMADOR | 44 | 24 |  | 6600 | 10.3125 | 33650.5625 | 35333.0906 | 0 | 0 | 35333.0906 | 36993.7459
CA4500314 | SHASTA CO CSA # 13 ALPINE MEADOWS | SHASTA | 31 | 31 | None | 4650 | 7.2656 | 32611.5781 | 34242.157 | 0 | 0 | 34242.157 | 35851.5384
CA3205003 | GOLD MOUNTAIN CSD | PLUMAS | 100 | 100 | Some | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA1900913 | LILY OF THE VALLEY MOBILE VILLAGE | LOS ANGELES | 495 | 182 | None | 74250 | 116.0156 | 69695.3281 | 73180.0945 | 0.32 | 22302.505 | 95482.5995 | 99970.2817
CA2410018 | SANTA NELLA COUNTY WATER DISTRICT | MERCED | 1308 | 667 | Some | 196200 | 306.5625 | 134671.8125 | 141405.4031 | 0 | 0 | 141405.4031 | 148051.4571
CA4900669 | WENDELL LANE MUTUAL WATER COMPANY | SONOMA | 82 | 25 | None | 12300 | 19.2188 | 36687.5938 | 38521.9734 | 0.3 | 11006.2781 | 49528.2516 | 51856.0794
CA0400123 | HUMBOLDT HIGHLANDS MUTUAL | BUTTE | 50 | 28 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA0707577 | RIVERVIEW WATER ASSOCIATION | CONTRA COSTA | 230 | 89 | Some | 34500 | 53.9062 | 48516.0312 | 50941.8328 | 0.3 | 14554.8094 | 65496.6422 | 68574.9844
CA3301877 | BLOCK 77 WATER COMPANY | RIVERSIDE | 50 | 18 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0.32 | 10921.63 | 46758.2284 | 48955.8652
CA1009027 | HARRIS FARMS HEADQUARTERS | FRESNO | 300 | 69 | NULL | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 59486.4469
CA2000526 | PIKE RANCH MUTUAL WATER CO | MADERA | 74 | 20 | None | 11100 | 17.3438 | 36048.2188 | 37850.6297 | 0 | 0 | 37850.6297 | 39629.6093
CA2410002 | CITY OF DOS PALOS | MERCED | 7452 | 2521 | None | 1117800 | 1746.5625 | 625711.8125 | 656997.4031 | 0 | 0 | 656997.4031 | 687876.2811
CA1010044 | HURON, CITY OF | FRESNO | 9306 | 871 | None | 1395900 | 2181.0938 | 773886.9688 | 812581.3172 | 0 | 0 | 812581.3172 | 850772.6391
CA2300604 | POINT OF VIEW MUTUAL WATER CO | MENDOCINO | 56 | 30 | None | 8400 | 13.125 | 34609.625 | 36340.1062 | 0 | 0 | 36340.1062 | 38048.0912
CA2000775 | OAK CREEK MOBILE HOME PARK | MADERA | 370 | 198 |  | 55500 | 86.7188 | 59705.0938 | 62690.3484 | 0 | 0 | 62690.3484 | 65636.7948
CA4200731 | ALEGRIA DOMESTIC MUTUAL WATER COMPANY | SANTA BARBARA | 54 | 17 | Some | 8100 | 12.6562 | 34449.7812 | 36172.2703 | 0.3 | 10334.9344 | 46507.2047 | 48693.0433
CA1500290 | NORTH MUROC MUTUAL WATER COMPANY | KERN | 270 | 198 |  | 40500 | 63.2812 | 51712.9062 | 54298.5516 | 0 | 0 | 54298.5516 | 56850.5835
CA2310008 | REDWOOD VALLEY COUNTY WATER DISTRICT | MENDOCINO | 5200 | 1317 | None | 780000 | 1218.75 | 445727.75 | 468014.1375 | 0 | 0 | 468014.1375 | 490010.802
CA5800821 | HERITAGE PARK | YUBA | 26 | 20 |  | 3900 | 6.0938 | 32211.9688 | 33822.5672 | 0 | 0 | 33822.5672 | 35412.2278
CA2000530 | CRASS MUTUAL WATER COMPANY | MADERA | 80 | 26 | None | 12000 | 18.75 | 36527.75 | 38354.1375 | 0 | 0 | 38354.1375 | 40156.782
CA3400191 | ELEVEN OAKS MOBILE HOME COMMUNITY | SACRAMENTO | 262 | 136 |  | 39300 | 61.4062 | 51073.5312 | 53627.2078 | 0.32 | 16343.53 | 69970.7378 | 73259.3625
CA4200891 | BOBCAT SPRINGS MUTUAL WATER COMPANY | SANTA BARBARA | 120 | 47 | None | 18000 | 28.125 | 39724.625 | 41710.8562 | 0.3 | 11917.3875 | 53628.2438 | 56148.7712
CA2600547 | CROWLEY LAKE TRAILER PARK | MONO | 230 | 108 |  | 34500 | 53.9062 | 48516.0312 | 50941.8328 | 0 | 0 | 50941.8328 | 53336.099
CA1400027 | CARTAGO MUTUAL WATER COMPANY | INYO | 132 | 40 | None | 19800 | 30.9375 | 40683.6875 | 42717.8719 | 0 | 0 | 42717.8719 | 44725.6119
CA4300562 | ROSEVIEW HEIGHTS MUTUAL WATER COMPANY | SANTA CLARA | 143 | 51 | None | 21450 | 33.5156 | 41562.8281 | 43640.9695 | 0.32 | 13300.105 | 56941.0745 | 59617.305
CA5400816 | BEDEL MUTUAL WATER CO | TULARE | 155 | 66 | None | 23250 | 36.3281 | 42521.8906 | 44647.9852 | 0 | 0 | 44647.9852 | 46746.4405
CA4500082 | MIDWAY MOBILEHOME PARK | SHASTA | 50 | 29 |  | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA5200012 | VISTA GRANDE WATER SYSTEM | TEHAMA | 400 | 141 | NULL | 60000 | 93.75 | 62102.75 | 65207.8875 | 0 | 0 | 65207.8875 | 68272.6582
CA5200013 | WOMACK SUBDIVISION M.W.C. | TEHAMA | 40 | 16 |  | 6000 | 9.375 | 33330.875 | 34997.4187 | 0 | 0 | 34997.4187 | 36642.2974
CA3400401 | PLANTATION MOBILE HOME PARK | SACRAMENTO | 44 | 44 | None | 6600 | 10.3125 | 33650.5625 | 35333.0906 | 0.32 | 10768.18 | 46101.2706 | 48268.0303
CA1500443 | CANYON MEADOWS MUTUAL WATER | KERN | 394 | 141 | NULL | 59100 | 92.3438 | 61623.2188 | 64704.3797 | 0 | 0 | 64704.3797 | 67745.4855
CA5500041 | ALPINE ACRES MUTUAL WATER CO | TUOLUMNE | 59 | 55 | NULL | 8850 | 13.8281 | 34849.3906 | 36591.8602 | 0 | 0 | 36591.8602 | 38311.6776
CA3100019 | NORTH EDEN VALLEY | PLACER | 52 | 21 |  | 7800 | 12.1875 | 34289.9375 | 36004.4344 | 0 | 0 | 36004.4344 | 37696.6428
CA3901215 | SAN JUAN VISTA | SAN JOAQUIN | 100 | 72 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA5200547 | GATEWAY MOBILE HOME PARK | TEHAMA | 75 | 32 | None | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0 | 0 | 37934.5477 | 39717.4714
CA3900586 | B&G MOBILE HOME PARK LLC WS | SAN JOAQUIN | 50 | 22 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA2700766 | STRAWBERRY RD WS #06 | MONTEREY | 78 | 27 | None | 11700 | 18.2812 | 36367.9062 | 38186.3016 | 0.3 | 10910.3719 | 49096.6734 | 51404.2171
CA3900724 | ELKHORN ESTATES WATER SYSTEM | SAN JOAQUIN | 200 | 71 | Some | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA2700589 | GLENN AVE WS #01 | MONTEREY | 73 | 26 |  | 10950 | 17.1094 | 35968.2969 | 37766.7117 | 0.3 | 10790.4891 | 48557.2008 | 50839.3892
CA2900562 | ANANDA VILLAGE | NEVADA | 290 | 83 | Some | 43500 | 67.9688 | 53311.3438 | 55976.9109 | 0 | 0 | 55976.9109 | 58607.8258
CA0707594 | CASA MEDANOS WATER SYSTEM | CONTRA COSTA | 45 | 16 | None | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0.3 | 10119.1453 | 45536.1539 | 47676.3531
CA1502600 | WEGIS MUTUAL WATER COMPANY | KERN | 64 | 23 | None | 9600 | 15 | 35249 | 37011.45 | 0 | 0 | 37011.45 | 38750.9881
CA4300831 | MT. EDEN MUTUAL WATER COMPANY | SANTA CLARA | 165 | 65 | None | 24750 | 38.6719 | 43321.1094 | 45487.1648 | 0.32 | 13862.755 | 59349.9198 | 62139.3661
CA1010020 | LATON COMMUNITY SERVICES DISTRICT | FRESNO | 1824 | 472 | Some | 273600 | 427.5 | 175911.5 | 184707.075 | 0 | 0 | 184707.075 | 193388.3075
CA0300062 | HOPE FOUNDATION/MORIAH HEIGHTS | AMADOR | 299 | 21 | Some | 44850 | 70.0781 | 54030.6406 | 56732.1727 | 0 | 0 | 56732.1727 | 59398.5848
CA2710013 | CWSC LAS LOMAS | MONTEREY | 3387 | 621 | Some | 508050 | 793.8281 | 300829.3906 | 315870.8602 | 0.3 | 90248.8172 | 406119.6773 | 425207.3022
CA4710002 | DUNSMUIR, CITY OF | SISKIYOU | 1923 | 1187 | Some | 288450 | 450.7031 | 183823.7656 | 193014.9539 | 0 | 0 | 193014.9539 | 202086.6567
CA5410034 | DEL ORO CALIFORNIA PINES DISTRICT | TULARE | 930 | 284 |  | 139500 | 217.9688 | 104461.3438 | 109684.4109 | 0 | 0 | 109684.4109 | 114839.5783
CA4000803 | RANCHO SALINAS MBWC | SAN LUIS OBISPO | 50 | 20 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0.3 | 10239.0281 | 46075.6266 | 48241.181
CA4500313 | SHASTA CO CSA # 8 PALO CEDRO | SHASTA | 261 | 79 | None | 39150 | 61.1719 | 50993.6094 | 53543.2898 | 0 | 0 | 53543.2898 | 56059.8245
CA3901348 | FAIROAKS PWS #44 | SAN JOAQUIN | 1172 | 355 | Some | 175800 | 274.6875 | 123802.4375 | 129992.5594 | 0 | 0 | 129992.5594 | 136102.2097
CA2702148 | ASOLEADO MWC | MONTEREY | 101 | 36 | None | 15150 | 23.6719 | 38206.1094 | 40116.4148 | 0.3 | 11461.8328 | 51578.2477 | 54002.4253
CA3600107 | FOREST PARK MWC | SAN BERNARDINO | 415 | 93 |  | 62250 | 97.2656 | 63301.5781 | 66466.657 | 0.3 | 18990.4734 | 85457.1305 | 89473.6156
CA2000529 | BONADELLE RANCHOS MUTUAL WATER | MADERA | 50 | 23 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA3301031 | BANNING HTS. MUTUAL WATER CO. | RIVERSIDE | 552 | 178 | None | 82800 | 129.375 | 74250.875 | 77963.4187 | 0.32 | 23760.28 | 101723.6987 | 106504.7126
CA5400641 | TEVISTON CSD | TULARE | 343 | 140 | None | 51450 | 80.3906 | 57547.2031 | 60424.5633 | 0 | 0 | 60424.5633 | 63264.5178
CA1300664 | RIVERFRONT MUTUAL WATER COMPANY | IMPERIAL | 15 | 42 |  | 2250 | 3.5156 | 31332.8281 | 32899.4695 | 0 | 0 | 32899.4695 | 34445.7446
CA1510007 | FRAZIER PARK PUD | KERN | 2691 | 1318 | Some | 403650 | 630.7031 | 245203.7656 | 257463.9539 | 0 | 0 | 257463.9539 | 269564.7597
CA2000533 | SUGAR PINE HOMEOWNERS ASSOC | MADERA | 120 | 58 | None | 18000 | 28.125 | 39724.625 | 41710.8562 | 0 | 0 | 41710.8562 | 43671.2665
CA4200572 | LAS POSITAS MUTUAL WATER COMPANY | SANTA BARBARA | 200 | 62 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.3 | 13835.5125 | 62259.8063 | 65186.0171
CA1600002 | SUNSET VISTA ESTATES MHP | KINGS | 400 | 108 | None | 60000 | 93.75 | 62102.75 | 65207.8875 | 0 | 0 | 65207.8875 | 68272.6582
CA3301943 | PLANTATION ON THE LAKE PARK | RIVERSIDE | 891 | 554 | Some | 133650 | 208.8281 | 101344.3906 | 106411.6102 | 0.32 | 32430.205 | 138841.8152 | 145367.3805
CA3701988 | ALPINE OAKS ESTATES LLC | SAN DIEGO | 125 | 68 | NULL | 18750 | 29.2969 | 40124.2344 | 42130.4461 | 0.32 | 12839.755 | 54970.2011 | 57553.8005
CA5800805 | LAKE FRANCIS MUTUAL WATER COMPANY | YUBA | 60 | 19 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 38399.5397
CA3700958 | LOS TULES MUTUAL WATER COMPANY | SAN DIEGO | 140 | 100 | Some | 21000 | 32.8125 | 41323.0625 | 43389.2156 | 0.32 | 13223.38 | 56612.5956 | 59273.3876
CA4400605 | CRESTWOOD HEIGHTS WATER ASSN | SANTA CRUZ | 126 | 45 |  | 18900 | 29.5312 | 40204.1562 | 42214.3641 | 0.3 | 12061.2469 | 54275.6109 | 56826.5647
CA2000573 | THE VILLAGE | MADERA | 40 | 21 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0 | 0 | 34997.4187 | 36642.2974
CA4010006 | CAYUCOS BEACH MUTUAL WATER COMPANY | SAN LUIS OBISPO | 2373 | 783 | None | 355950 | 556.1719 | 219788.6094 | 230778.0398 | 0.3 | 65936.5828 | 296714.6227 | 310660.2099
CA3901081 | MOBILE VILLAS TRAILER PARK | SAN JOAQUIN | 130 | 36 | None | 19500 | 30.4688 | 40523.8438 | 42550.0359 | 0 | 0 | 42550.0359 | 44549.8876
CA1100711 | BUTTE CITY COMMUNITY S.D. | GLENN | 75 | 48 | None | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0 | 0 | 37934.5477 | 39717.4714
CA4000771 | RANCHO NIPOMO WATER COMPANY | SAN LUIS OBISPO | 65 | 44 |  | 9750 | 15.2344 | 35328.9219 | 37095.368 | 0.3 | 10598.6766 | 47694.0445 | 49935.6646
CA5610001 | DEMPSEY ROAD MUTUAL WATER CO | VENTURA | 990 | 301 |  | 148500 | 232.0312 | 109256.6562 | 114719.4891 | 0.32 | 34962.13 | 149681.6191 | 156716.6552
CA3301428 | BLYTHE - MESA RANCH | RIVERSIDE | 561 | 189 | Some | 84150 | 131.4844 | 74970.1719 | 78718.6805 | 0.32 | 23990.455 | 102709.1355 | 107536.4648
CA3810700 | PRESIDIO OF SAN FRANCISCO | SAN FRANCISCO | 3500 | 1219 | None | 525000 | 820.3125 | 309860.5625 | 325353.5906 | 0.32 | 99155.38 | 424508.9706 | 444460.8922
CA1900301 | SHADOW ACRES MUTUAL WATER COMPANY | LOS ANGELES | 431 | 162 | None | 64650 | 101.0156 | 64580.3281 | 67809.3445 | 0.32 | 20665.705 | 88475.0495 | 92633.3769
CA3301171 | BRADFORD RUN RV | RIVERSIDE | 100 | 59 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.32 | 12200.38 | 52232.8769 | 54687.8221
CA3301381 | CSA 51 | RIVERSIDE | 350 | 77 | None | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0.32 | 18594.13 | 79606.1191 | 83347.6067
CA2701959 | TIERRA VISTA MWC | MONTEREY | 54 | 18 |  | 8100 | 12.6562 | 34449.7812 | 36172.2703 | 0.3 | 10334.9344 | 46507.2047 | 48693.0433
CA2701918 | LOMAS DEL SOL MWS | MONTEREY | 93 | 32 | None | 13950 | 21.7969 | 37566.7344 | 39445.0711 | 0.3 | 11270.0203 | 50715.0914 | 53098.7007
CA1900903 | SLEEPY VALLEY WATER COMPANY | LOS ANGELES | 130 | 58 | None | 19500 | 30.4688 | 40523.8438 | 42550.0359 | 0.32 | 12967.63 | 55517.6659 | 58126.9962
CA5410001 | CUTLER PUD | TULARE | 6200 | 1218 | None | 930000 | 1453.125 | 525649.625 | 551932.1062 | 0 | 0 | 551932.1062 | 577872.9152
CA3000618 | LIBERTY PARK WATER ASSOCIATION | ORANGE | 89 | 27 | None | 13350 | 20.8594 | 37247.0469 | 39109.3992 | 0.3 | 11174.1141 | 50283.5133 | 52646.8384
CA5402038 | PATTERSON TRACT CSD | TULARE | 550 | 153 | None | 82500 | 128.9062 | 74091.0312 | 77795.5828 | 0 | 0 | 77795.5828 | 81451.9752
CA3900964 | SAHARA MOBILE COURT | SAN JOAQUIN | 300 | 162 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 59486.4469
CA4900510 | SOUTH CLOVERDALE WATER COMPANY | SONOMA | 90 | 39 | None | 13500 | 21.0938 | 37326.9688 | 39193.3172 | 0.3 | 11198.0906 | 50391.4078 | 52759.804
CA2000757 | MD 63 MEADOW SPRINGS RANCH | MADERA | 300 | 85 |  | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 59486.4469
CA4210021 | GOLDEN STATE WATER COMPANY - TANGLEWOOD | SANTA BARBARA | 1962 | 455 |  | 294300 | 459.8438 | 186940.7188 | 196287.7547 | 0.3 | 56082.2156 | 252369.9703 | 264231.3589
CA3301535 | RANCHO CARRILLO MWC | RIVERSIDE | 210 | 74 | Some | 31500 | 49.2188 | 46917.5938 | 49263.4734 | 0.32 | 15013.63 | 64277.1034 | 67298.1273
CA3901303 | ACAMPO WATER SYSTEM | SAN JOAQUIN | 150 | 70 | Some | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA1900843 | CALIFORNIAN MOBILE HOME PARK | LOS ANGELES | 372 | 133 | None | 55800 | 87.1875 | 59864.9375 | 62858.1844 | 0.32 | 19156.78 | 82014.9644 | 85869.6677
CA2300832 | HILLS RANCH MUTUAL WATER COMPANY | MENDOCINO | 77 | 48 |  | 11550 | 18.0469 | 36287.9844 | 38102.3836 | 0 | 0 | 38102.3836 | 39893.1956
CA5410050 | ALPAUGH COMMUNITY SERVICES DISTRICT | TULARE | 1026 | 394 |  | 153900 | 240.4688 | 112133.8438 | 117740.5359 | 0 | 0 | 117740.5359 | 123274.3411
CA5000218 | COUNTRY VILLA APTS | STANISLAUS | 60 | 23 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 38399.5397
CA2701278 | RANCHO CHAPARRAL MWC | MONTEREY | 58 | 20 | None | 8700 | 13.5938 | 34769.4688 | 36507.9422 | 0.3 | 10430.8406 | 46938.7828 | 49144.9056
CA3400122 | EL DORADO WEST MHP | SACRAMENTO | 172 | 128 | None | 25800 | 40.3125 | 43880.5625 | 46074.5906 | 0.32 | 14041.78 | 60116.3706 | 62941.84
CA2701034 | APPLE AVE WS #02 | MONTEREY | 75 | 18 |  | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0.3 | 10838.4422 | 48772.9898 | 51065.3204
CA3410026 | CALIFORNIA STATE FAIR | SACRAMENTO | 650 | 269 | None | 97500 | 152.3438 | 82083.2188 | 86187.3797 | 0.32 | 26266.63 | 112454.0097 | 117739.3481
CA1400037 | FOOTHILL MOBILE HOME PARK | INYO | 60 | 48 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 38399.5397
CA4300551 | HAPPY ACRES MWC | SANTA CLARA | 220 | 79 | None | 33000 | 51.5625 | 47716.8125 | 50102.6531 | 0.32 | 15269.38 | 65372.0331 | 68444.5187
CA1000298 | WOODWARD BLUFFS MHP | FRESNO | 300 | 172 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 59486.4469
CA5610006 | YERBA BUENA WATER COMPANY | VENTURA | 690 | 245 | Some | 103500 | 161.7188 | 85280.0938 | 89544.0984 | 0.32 | 27289.63 | 116833.7284 | 122324.9137
CA4200802 | OAK TRAIL RANCH | SANTA BARBARA | 105 | 31 |  | 15750 | 24.6094 | 38525.7969 | 40452.0867 | 0.3 | 11557.7391 | 52009.8258 | 54454.2876
CA2910016 | DONNER SUMMIT PUBLIC UTILITY DISTRICT | NEVADA | 310 | 352 | Some | 46500 | 72.6562 | 54909.7812 | 57655.2703 | 0 | 0 | 57655.2703 | 60365.068
CA3400181 | LAGUNA DEL SOL INC | SACRAMENTO | 470 | 112 | None | 70500 | 110.1562 | 67697.2812 | 71082.1453 | 0.32 | 21663.13 | 92745.2753 | 97104.3033
CA1900803 | EL DORADO MUTUAL WATER CO. | LOS ANGELES | 660 | 237 | None | 99000 | 154.6875 | 82882.4375 | 87026.5594 | 0.32 | 26522.38 | 113548.9394 | 118885.7395
CA0400081 | FEATHER RIDGE ESTATES WATER CO | BUTTE | 37 | 32 | None | 5550 | 8.6719 | 33091.1094 | 34745.6648 | 0 | 0 | 34745.6648 | 36378.7111
CA3000825 | SOUTH MIDWAY CITY MUTUAL WATER CO. | ORANGE | 825 | 56 | None | 123750 | 193.3594 | 96069.5469 | 100873.0242 | 0.3 | 28820.8641 | 129693.8883 | 135789.501
CA2410003 | CITY OF GUSTINE | MERCED | 5855 | 1913 | Some | 878250 | 1372.2656 | 498076.5781 | 522980.407 | 0 | 0 | 522980.407 | 547560.4862
CA3110048 | PLACER CSA - SHERIDAN | PLACER | 726 | 196 | Some | 108900 | 170.1562 | 88157.2812 | 92565.1453 | 0 | 0 | 92565.1453 | 96915.7071
CA5601119 | SIETE ROBLES MUTUAL WATER CO | VENTURA | 323 | 95 | None | 48450 | 75.7031 | 55948.7656 | 58746.2039 | 0.32 | 17903.605 | 76649.8089 | 80252.3499
CA5200526 | HIDDEN HARBOR MARINA & RVP | TEHAMA | 70 | 70 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0 | 0 | 37514.9578 | 39278.1608
CA2700535 | JOST POST WA | MONTEREY | 60 | 20 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA1500542 | WILLOW SPRINGS MOBILE HOME PARK | KERN | 275 | 104 | None | 41250 | 64.4531 | 52112.5156 | 54718.1414 | 0 | 0 | 54718.1414 | 57289.8941
CA2700656 | MORO COJO MWA | MONTEREY | 67 | 19 |  | 10050 | 15.7031 | 35488.7656 | 37263.2039 | 0.3 | 10646.6297 | 47909.8336 | 50161.5958
CA5400544 | ALLENSWORTH CSD | TULARE | 521 | 164 | None | 78150 | 122.1094 | 71773.2969 | 75361.9617 | 0 | 0 | 75361.9617 | 78903.9739
CA2700503 | ASSISI MWC | MONTEREY | 126 | 42 | None | 18900 | 29.5312 | 40204.1562 | 42214.3641 | 0.3 | 12061.2469 | 54275.6109 | 56826.5647
CA2000561 | MD 08 NORTH FORK WATER SYSTEM | MADERA | 264 | 75 |  | 39600 | 61.875 | 51233.375 | 53795.0437 | 0 | 0 | 53795.0437 | 56323.4108
CA2010010 | MADERA VALLEY WATER COMPANY | MADERA | 6372 | 1944 | Some | 955800 | 1493.4375 | 539396.1875 | 566365.9969 | 0 | 0 | 566365.9969 | 592985.1987
CA1310003 | GSWC-CALIPATRIA | IMPERIAL | 4335 | 1164 | Some | 650250 | 1016.0156 | 376595.3281 | 395425.0945 | 0 | 0 | 395425.0945 | 414010.074
CA5510006 | MI WUK VILLAGE MUT WTR CO | TUOLUMNE | 1737 | 770 | None | 260550 | 407.1094 | 168958.2969 | 177406.2117 | 0 | 0 | 177406.2117 | 185744.3037
CA1910060 | LA PUENTE VALLEY CWD | LOS ANGELES | 8108 | 2457 | None | 1216200 | 1900.3125 | 678140.5625 | 712047.5906 | 0.32 | 217004.98 | 929052.5706 | 972718.0414
CA5010031 | CITY OF MODESTO - WALNUT MANOR | STANISLAUS | 175 | 53 | None | 26250 | 41.0156 | 44120.3281 | 46326.3445 | 0 | 0 | 46326.3445 | 48503.6827
CA0600012 | COLUSA CO. SERVICE AREA #1-CENTURY RANCH | COLUSA | 246 | 88 |  | 36900 | 57.6562 | 49794.7812 | 52284.5203 | 0 | 0 | 52284.5203 | 54741.8928
CA1800516 | LITTLE VALLEY CSD | LASSEN | 70 | 44 | NULL | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0 | 0 | 37514.9578 | 39278.1608
CA4100539 | KINGS MOUNTAIN PARK MUTUAL | SAN MATEO | 66 | 23 | None | 9900 | 15.4688 | 35408.8438 | 37179.2859 | 0.32 | 11330.83 | 48510.1159 | 50790.0914
CA4200560 | SISQUOC | SANTA BARBARA | 133 | 76 |  | 19950 | 31.1719 | 40763.6094 | 42801.7898 | 0.3 | 12229.0828 | 55030.8727 | 57617.3237
CA5400542 | DUCOR CSD | TULARE | 535 | 166 | None | 80250 | 125.3906 | 72892.2031 | 76536.8133 | 0 | 0 | 76536.8133 | 80134.0435
CA1700674 | WALNUT COVE MOBILE ESTATES | LAKE | 200 | 60 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA4700626 | COVE MOBILE VILLA | SISKIYOU | 105 | 47 | None | 15750 | 24.6094 | 38525.7969 | 40452.0867 | 0 | 0 | 40452.0867 | 42353.3348
CA4600017 | R.R. LEWIS SMALL WC | SIERRA | 324 | 120 |  | 48600 | 75.9375 | 56028.6875 | 58830.1219 | 0 | 0 | 58830.1219 | 61595.1376
CA4600019 | SIERRA CO. W.W.D #1 CALPINE | SIERRA | 225 | 135 |  | 33750 | 52.7344 | 48116.4219 | 50522.243 | 0 | 0 | 50522.243 | 52896.7884
CA5410026 | POPLAR COMM SERVICE DIST | TULARE | 2200 | 597 |  | 330000 | 515.625 | 205962.125 | 216260.2313 | 0 | 0 | 216260.2313 | 226424.4621
CA1502056 | CLARK STREET COMMUNITY WELL | KERN | 90 | 20 | None | 13500 | 21.0938 | 37326.9688 | 39193.3172 | 0 | 0 | 39193.3172 | 41035.4031
CA1000359 | FCSA #32/CANTUA CREEK | FRESNO | 476 | 79 | None | 71400 | 111.5625 | 68176.8125 | 71585.6531 | 0 | 0 | 71585.6531 | 74950.1788
CA1910218 | LA HABRA HEIGHTS CWD | LOS ANGELES | 5459 | 2006 | Some | 818850 | 1279.4531 | 466427.5156 | 489748.8914 | 0.32 | 149256.805 | 639005.6964 | 669038.9641
CA4700872 | MONTE SHASTA M.W.C. | SISKIYOU | 150 | 46 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA4500028 | SHASTA CSA - CRAGVIEW, #23 | SHASTA | 218 | 66 | None | 32700 | 51.0938 | 47556.9688 | 49934.8172 | 0 | 0 | 49934.8172 | 52281.7536
CA5200521 | ANTELOPE CREEK MHP | TEHAMA | 175 | 60 |  | 26250 | 41.0156 | 44120.3281 | 46326.3445 | 0 | 0 | 46326.3445 | 48503.6827
CA1909006 | WEST VALLEY COUNTY WATER DISTRICT | LOS ANGELES | 766 | 237 | None | 114900 | 179.5312 | 91354.1562 | 95921.8641 | 0.32 | 29233.33 | 125155.1941 | 131037.4882
CA2700738 | SAN MIGUEL WS #01 | MONTEREY | 100 | 34 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.3 | 11437.8563 | 51470.3531 | 53889.4597
CA5400553 | DEL ORO TRAVER DISTRICT | TULARE | 660 | 199 | None | 99000 | 154.6875 | 82882.4375 | 87026.5594 | 0 | 0 | 87026.5594 | 91116.8077
CA4900552 | MICHELE MUTUAL WATER COMPANY | SONOMA | 170 | 62 | None | 25500 | 39.8438 | 43720.7188 | 45906.7547 | 0.3 | 13116.2156 | 59022.9703 | 61797.0499
CA3610017 | HAVASU WC | SAN BERNARDINO | 361 | 224 | None | 54150 | 84.6094 | 58985.7969 | 61935.0867 | 0.3 | 17695.7391 | 79630.8258 | 83373.4746
CA2000506 | SIERRA LINDA MUTUAL WATER CO | MADERA | 200 | 89 | Some | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 50700.2356
CA3610009 | BIGHORN - DESERT VIEW WATER AGENCY | SAN BERNARDINO | 3689 | 1708 | Some | 553350 | 864.6094 | 324965.7969 | 341214.0867 | 0.3 | 97489.7391 | 438703.8258 | 459322.9056
CA5403217 | OKIEVILLE HIGHLAND ACRES MWC | TULARE | 300 | 72 |  | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 59486.4469
CA1210024 | WESTHAVEN C.S.D. | HUMBOLDT | 490 | 226 | Some | 73500 | 114.8438 | 69295.7188 | 72760.5047 | 0 | 0 | 72760.5047 | 76180.2484
CA2702007 | VIERRA ESTATES WS | MONTEREY | 164 | 48 | None | 24600 | 38.4375 | 43241.1875 | 45403.2469 | 0.3 | 12972.3563 | 58375.6031 | 61119.2565
CA2410011 | LE GRAND COMM SERVICES DIST | MERCED | 1700 | 474 | None | 255000 | 398.4375 | 166001.1875 | 174301.2469 | 0 | 0 | 174301.2469 | 182493.4055
CA1010021 | MENDOTA, CITY OF | FRESNO | 11104 | 2300 | Some | 1665600 | 2602.5 | 917586.5 | 963465.825 | 0 | 0 | 963465.825 | 1008748.7188
CA4900795 | STONEGATE MOBILE HOME PARK | SONOMA | 100 | 75 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.3 | 11437.8563 | 51470.3531 | 53889.4597
CA3500823 | BEST ROAD MWC | SAN BENITO | 133 | 48 | None | 19950 | 31.1719 | 40763.6094 | 42801.7898 | 0.3 | 12229.0828 | 55030.8727 | 57617.3237
CA3900661 | MAPACHE TRAILER PARK | SAN JOAQUIN | 275 | 99 | None | 41250 | 64.4531 | 52112.5156 | 54718.1414 | 0 | 0 | 54718.1414 | 57289.8941
CA0900300 | KYBURZ MUTUAL WATER COMPANY | EL DORADO | 150 | 118 |  | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0.3 | 12636.6844 | 56865.0797 | 59537.7384
CA3601045 | BEAR VALLEY MHP | SAN BERNARDINO | 150 | 98 |  | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0.3 | 12636.6844 | 56865.0797 | 59537.7384
CA4400582 | PINE TREE LANE MUTUAL WATER CO | SANTA CRUZ | 80 | 36 | None | 12000 | 18.75 | 36527.75 | 38354.1375 | 0.3 | 10958.325 | 49312.4625 | 51630.1482
CA3600308 | FREEDOM ACRES THE RESORT | SAN BERNARDINO | 500 | 100 |  | 75000 | 117.1875 | 70094.9375 | 73599.6844 | 0.3 | 21028.4813 | 94628.1656 | 99075.6894
CA3610060 | BDVWA - GOAT MOUNTAIN ID | SAN BERNARDINO | 1300 | 602 |  | 195000 | 304.6875 | 134032.4375 | 140734.0594 | 0.3 | 40209.7312 | 180943.7906 | 189448.1488
CA3610028 | MARYGOLD MWC | SAN BERNARDINO | 3055 | 926 | Some | 458250 | 716.0156 | 274295.3281 | 288010.0945 | 0.3 | 82288.5984 | 370298.693 | 387702.7315
CA5810004 | CITY OF WHEATLAND | YUBA | 3456 | 1219 | Some | 518400 | 810 | 306344 | 321661.2 | 0 | 0 | 321661.2 | 336779.2764
CA2600532 | LUNDY MUTUAL WATER COMPANY | MONO | 70 | 32 |  | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0 | 0 | 37514.9578 | 39278.1608
CA1400072 | NORTH LONE PINE MUTUAL WATER COMPANY | INYO | 70 | 33 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0 | 0 | 37514.9578 | 39278.1608
CA4400665 | MEADOWRIDGE MUTUAL WATER CO | SANTA CRUZ | 42 | 18 |  | 6300 | 9.8438 | 33490.7188 | 35165.2547 | 0.3 | 10047.2156 | 45212.4703 | 47337.4564
CA0707519 | DUTCH SLOUGH WATER WORKS | CONTRA COSTA | 49 | 58 |  | 7350 | 11.4844 | 34050.1719 | 35752.6805 | 0.3 | 10215.0516 | 45967.732 | 48128.2154
CA2410012 | HILMAR COUNTY WATER DISTRICT | MERCED | 5416 | 1649 | Some | 812400 | 1269.375 | 462990.875 | 486140.4188 | 0 | 0 | 486140.4188 | 508989.0184
CA5200562 | SKY VIEW COUNTY WATER | TEHAMA | 412 | 85 |  | 61800 | 96.5625 | 63061.8125 | 66214.9031 | 0 | 0 | 66214.9031 | 69327.0036
CA3901172 | PAR COUNTRY ESTATES CSA-16 | SAN JOAQUIN | 120 | 54 | Some | 18000 | 28.125 | 39724.625 | 41710.8562 | 0 | 0 | 41710.8562 | 43671.2665
CA4300581 | VELLADAO MOBILE HOME PARK | SANTA CLARA | 75 | 27 |  | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0.32 | 11561.005 | 49495.5527 | 51821.8436
CA5400631 | LINNELL FARM LABOR CENTER | TULARE | 694 | 195 | None | 104100 | 162.6562 | 85599.7812 | 89879.7703 | 0 | 0 | 89879.7703 | 94104.1195
CA2010005 | YOSEMITE SPRING PARK UTIL CO | MADERA | 6224 | 1902 |  | 933600 | 1458.75 | 527567.75 | 553946.1375 | 0 | 0 | 553946.1375 | 579981.606
CA5400792 | WOODVILLE FARM LABOR CENTER | TULARE | 650 | 177 | None | 97500 | 152.3438 | 82083.2188 | 86187.3797 | 0 | 0 | 86187.3797 | 90238.1865
CA2702055 | VIERRA KNOLLS MWC | MONTEREY | 66 | 22 |  | 9900 | 15.4688 | 35408.8438 | 37179.2859 | 0.3 | 10622.6531 | 47801.9391 | 50048.6302
CA5401038 | AKIN WATER CO | TULARE | 86 | 26 |  | 12900 | 20.1562 | 37007.2812 | 38857.6453 | 0 | 0 | 38857.6453 | 40683.9546
CA1500599 | CHOCTAW VALLEY MUTUAL WATER CO. | KERN | 44 | 18 | None | 6600 | 10.3125 | 33650.5625 | 35333.0906 | 0 | 0 | 35333.0906 | 36993.7459
CA1500553 | RANCHOS DEL RIO | KERN | 62 | 24 | None | 9300 | 14.5312 | 35089.1562 | 36843.6141 | 0 | 0 | 36843.6141 | 38575.2639
CA1502622 | GOSFORD ROAD WATER COMPANY | KERN | 50 | 15 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA3110049 | TAHOE PARK WATER CO - SKYLAND/NIELSEN | PLACER | 50 | 92 | Some | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA3110047 | TALMONT RESORT IMPROVEMENT DISTRICT | PLACER | 300 | 346 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 59486.4469
CA1000018 | EASTON ESTATES WATER COMPANY | FRESNO | 302 | 108 | None | 45300 | 70.7812 | 54270.4062 | 56983.9266 | 0 | 0 | 56983.9266 | 59662.1711
CA1700536 | SUNRISE SHORE MUTUAL WATER COMPANY | LAKE | 83 | 42 | None | 12450 | 19.4531 | 36767.5156 | 38605.8914 | 0 | 0 | 38605.8914 | 40420.3683
CA1400518 | VAN LOON WATER ASSOCIATION | INYO | 25 | 15 |  | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0 | 0 | 33738.6492 | 35324.3657
CA1000063 | NEW AUBERRY WATER ASSOCIATION | FRESNO | 120 | 35 | None | 18000 | 28.125 | 39724.625 | 41710.8562 | 0 | 0 | 41710.8562 | 43671.2665
CA4710007 | MONTAGUE, CITY OF | SISKIYOU | 1495 | 536 | Some | 224250 | 350.3906 | 149617.2031 | 157098.0633 | 0 | 0 | 157098.0633 | 164481.6723
CA1900767 | GOLDEN VALLEY MUNICIPAL WATER DISTRICT | LOS ANGELES | 70 | 18 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0.32 | 11433.13 | 48948.0878 | 51248.6479
CA1510046 | LOST HILLS UTILITY DISTRICT | KERN | 2412 | 443 | Some | 361800 | 565.3125 | 222905.5625 | 234050.8406 | 0 | 0 | 234050.8406 | 245051.2301
CA3400179 | MC CLELLAN MHP | SACRAMENTO | 700 | 199 |  | 105000 | 164.0625 | 86079.3125 | 90383.2781 | 0.32 | 27545.38 | 117928.6581 | 123471.3051
CA0500068 | DUNROVIN MOBILE HOME VILLAGE | CALAVERAS | 99 | 42 |  | 14850 | 23.2031 | 38046.2656 | 39948.5789 | 0 | 0 | 39948.5789 | 41826.1621
CA1000405 | PIEDRA PARK ASSOCIATION | FRESNO | 25 | 15 | None | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0 | 0 | 33738.6492 | 35324.3657
CA3301247 | ELMS MOBILE PARK | RIVERSIDE | 100 | 47 |  | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.32 | 12200.38 | 52232.8769 | 54687.8221
CA3900720 | SHADED TERRACE PWS | SAN JOAQUIN | 161 | 72 | None | 24150 | 37.7344 | 43001.4219 | 45151.493 | 0 | 0 | 45151.493 | 47273.6131
CA5500092 | PONDEROSA MOBILE HOME PARK | TUOLUMNE | 52 | 58 | Some | 7800 | 12.1875 | 34289.9375 | 36004.4344 | 0 | 0 | 36004.4344 | 37696.6428
CA3600157 | LUCERNE VISTA MWC | SAN BERNARDINO | 160 | 57 | None | 24000 | 37.5 | 42921.5 | 45067.575 | 0.3 | 12876.45 | 57944.025 | 60667.3942
CA5400682 | PLAINVIEW MWC - CENTRAL WATER | TULARE | 138 | 42 | Some | 20700 | 32.3438 | 41163.2188 | 43221.3797 | 0 | 0 | 43221.3797 | 45252.7845
CA1502645 | MEADOWS OF THE KERN MUTUAL WATER COMPANY | KERN | 32 | 16 | None | 4800 | 7.5 | 32691.5 | 34326.075 | 0 | 0 | 34326.075 | 35939.4005
CA5500116 | PEPPERMINT CREEK MHP | TUOLUMNE | 280 | 101 |  | 42000 | 65.625 | 52512.125 | 55137.7312 | 0 | 0 | 55137.7312 | 57729.2046
CA3900561 | LODI LAKE MOBILE HOME PARK | SAN JOAQUIN | 104 | 52 | None | 15600 | 24.375 | 38445.875 | 40368.1687 | 0 | 0 | 40368.1687 | 42265.4727
CA3400192 | TUNNEL TRAILER PARK | SACRAMENTO | 44 | 21 | None | 6600 | 10.3125 | 33650.5625 | 35333.0906 | 0.32 | 10768.18 | 46101.2706 | 48268.0303
CA4900785 | NOEL HEIGHTS-CAL WATER SERVICE (PUC) | SONOMA | 137 | 50 | Some | 20550 | 32.1094 | 41083.2969 | 43137.4617 | 0.3 | 12324.9891 | 55462.4508 | 58069.186
CA4700803 | SHADOW MOUNTAIN MHP | SISKIYOU | 100 | 73 |  | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA2300514 | ELK COUNTY WATER DISTRICT | MENDOCINO | 380 | 99 | Some | 57000 | 89.0625 | 60504.3125 | 63529.5281 | 0 | 0 | 63529.5281 | 66515.4159
CA3610047 | GOLDEN STATE WATER CO - WRIGHTWOOD | SAN BERNARDINO | 4440 | 2777 | Some | 666000 | 1040.625 | 384987.125 | 404236.4813 | 0.3 | 115496.1375 | 519732.6188 | 544160.0518
CA4500023 | HAT CREEK HIGHLANDS MUTUAL WATER CO | SHASTA | 88 | 44 |  | 13200 | 20.625 | 37167.125 | 39025.4812 | 0 | 0 | 39025.4812 | 40859.6789
CA2010008 | MADERA CO MD10A-MADERA RANCHOS | MADERA | 3172 | 944 |  | 475800 | 743.4375 | 283646.1875 | 297828.4969 | 0 | 0 | 297828.4969 | 311826.4362
CA2000605 | WHISPERING PINES MHP | MADERA | 36 | 30 | Some | 5400 | 8.4375 | 33011.1875 | 34661.7469 | 0 | 0 | 34661.7469 | 36290.849
CA5410008 | OROSI PUBLIC UTILITY DISTRICT | TULARE | 8770 | 1579 | Some | 1315500 | 2055.4688 | 731048.8438 | 767601.2859 | 0 | 0 | 767601.2859 | 803678.5464
CA3700923 | LAKE MORENA OAK SHORES MWC | SAN DIEGO | 670 | 197 | Some | 100500 | 157.0312 | 83681.6562 | 87865.7391 | 0.32 | 26778.13 | 114643.8691 | 120032.1309
CA4400624 | RANCHO CORRALITOS | SANTA CRUZ | 60 | 31 |  | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA5500053 | LEISURE PINES MUTUAL WATER CO | TUOLUMNE | 340 | 103 | Some | 51000 | 79.6875 | 57307.4375 | 60172.8094 | 0 | 0 | 60172.8094 | 63000.9314
CA4910029 | CAMP MEEKER WATER SYSTEM | SONOMA | 1171 | 356 | None | 175650 | 274.4531 | 123722.5156 | 129908.6414 | 0.3 | 37116.7547 | 167025.3961 | 174875.5897
CA1907028 | SPV WATER COMPANY | LOS ANGELES | 211 | 73 | Some | 31650 | 49.4531 | 46997.5156 | 49347.3914 | 0.32 | 15039.205 | 64386.5964 | 67412.7664
CA1010001 | BAKMAN WATER COMPANY | FRESNO | 16756 | 2608 | Some | 2513400 | 3927.1875 | 1369304.9375 | 1437770.1844 | 0 | 0 | 1437770.1844 | 1505345.383
CA3301511 | PINYON CREST HOA | RIVERSIDE | 104 | 90 | None | 15600 | 24.375 | 38445.875 | 40368.1687 | 0.32 | 12302.68 | 52670.8487 | 55146.3786
CA0310019 | AWA LA MEL HEIGHTS #3 | AMADOR | 188 | 55 | Some | 28200 | 44.0625 | 45159.3125 | 47417.2781 | 0 | 0 | 47417.2781 | 49645.8902
CA5400529 | SHADY GROVE MHP, LLC | TULARE | 95 | 42 | None | 14250 | 22.2656 | 37726.5781 | 39612.907 | 0 | 0 | 39612.907 | 41474.7137
CA5601104 | CASITAS MUTUAL WATER COMPANY | VENTURA | 238 | 85 |  | 35700 | 55.7812 | 49155.4062 | 51613.1766 | 0.32 | 15729.73 | 67342.9066 | 70508.0232
CA1009078 | HARRIS FEEDING COMPANY | FRESNO | 225 | 30 | None | 33750 | 52.7344 | 48116.4219 | 50522.243 | 0 | 0 | 50522.243 | 52896.7884
CA3901031 | 132 INVESTMENTS WATER SYSTEM | SAN JOAQUIN | 100 | 93 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 41914.0242
CA4300924 | PARKWAY LAKES RV PARK | SANTA CLARA | 250 | 121 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0.32 | 16036.63 | 68656.8222 | 71883.6928
CA2702520 | ARROYO SECO ESTATES MWS | MONTEREY | 70 | 27 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0.3 | 10718.5594 | 48233.5172 | 50500.4925
CA5400819 | MOUNTAIN VIEW MHP | TULARE | 44 | 24 | None | 6600 | 10.3125 | 33650.5625 | 35333.0906 | 0 | 0 | 35333.0906 | 36993.7459
CA3100038 | HEATHER GLEN COMMUNITY SERVICE DIST | PLACER | 250 | 101 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 55093.3412
CA2702094 | BLACKIE RD WS #18 | MONTEREY | 60 | 21 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA4200881 | OAK TRAIL ESTATES | SANTA BARBARA | 210 | 63 |  | 31500 | 49.2188 | 46917.5938 | 49263.4734 | 0.3 | 14075.2781 | 63338.7516 | 66315.6729
CA5800924 | CAMPTONVILLE COMMUNITY SERV DIST | YUBA | 180 | 85 | None | 27000 | 42.1875 | 44519.9375 | 46745.9344 | 0 | 0 | 46745.9344 | 48942.9933
CA5200556 | MAYWOOD MOBILE HOME PARK | TEHAMA | 140 | 50 |  | 21000 | 32.8125 | 41323.0625 | 43389.2156 | 0 | 0 | 43389.2156 | 45428.5088
CA0706004 | OAKLEY MUTUAL WATER COMPANY | CONTRA COSTA | 170 | 50 | None | 25500 | 39.8438 | 43720.7188 | 45906.7547 | 0.3 | 13116.2156 | 59022.9703 | 61797.0499
CA3110015 | FULTON WATER COMPANY | PLACER | 500 | 923 | Some | 75000 | 117.1875 | 70094.9375 | 73599.6844 | 0 | 0 | 73599.6844 | 77058.8695
CA3700934 | PAUMA VALLEY WATER COMPANY | SAN DIEGO | 193 | 101 | None | 28950 | 45.2344 | 45558.9219 | 47836.868 | 0.32 | 14578.855 | 62415.723 | 65349.2619
CA4200618 | MIDLAND SCHOOL | SANTA BARBARA | 300 | 48 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0.3 | 16233.1688 | 73049.2594 | 76482.5746
CA5410004 | FARMERSVILLE, CITY OF | TULARE | 11327 | 2736 | Some | 1699050 | 2654.7656 | 935409.0781 | 982179.532 | 0 | 0 | 982179.532 | 1028341.97
CA2701254 | CARMEL RIVIERA MWC | MONTEREY | 584 | 177 | Some | 87600 | 136.875 | 76808.375 | 80648.7937 | 0.3 | 23042.5125 | 103691.3062 | 108564.7976
CA2100519 | ESTERO MUTUAL | MARIN | 186 | 145 | None | 27900 | 43.5938 | 44999.4688 | 47249.4422 | 0.3 | 13499.8406 | 60749.2828 | 63604.4991
CA4300546 | SIERRA ROAD IMPROVEMENT ASSOCIATION INC | SANTA CLARA | 280 | 50 | None | 42000 | 65.625 | 52512.125 | 55137.7312 | 0.32 | 16803.88 | 71941.6113 | 75322.867
CA3700422 | LAGUNA MOUNTIAN MUTUAL WATER CO. | SAN DIEGO | 100 | 28 |  | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.32 | 12200.38 | 52232.8769 | 54687.8221
CA2700691 | PESANTE RD WS #06 | MONTEREY | 48 | 16 | None | 7200 | 11.25 | 33970.25 | 35668.7625 | 0.3 | 10191.075 | 45859.8375 | 48015.2499
CA5410011 | SPRINGVILLE PUD | TULARE | 1500 | 390 | None | 225000 | 351.5625 | 150016.8125 | 157517.6531 | 0 | 0 | 157517.6531 | 164920.9828
CA3400296 | SAC CITY MOBILE HOME COMMUNITY LP | SACRAMENTO | 350 | 164 | None | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0.32 | 18594.13 | 79606.1191 | 83347.6067
CA5304109 | BURNT RANCH ESTATES | TRINITY | 115 | 35 | None | 17250 | 26.9531 | 39325.0156 | 41291.2664 | 0 | 0 | 41291.2664 | 43231.9559
CA5500115 | SUGAR PINE RV RESORT | TUOLUMNE | 244 | 87 | None | 36600 | 57.1875 | 49634.9375 | 52116.6844 | 0 | 0 | 52116.6844 | 54566.1685
CA5400732 | PIERPOINT SPRINGS WATER CO. | TULARE | 35 | 84 | Some | 5250 | 8.2031 | 32931.2656 | 34577.8289 | 0 | 0 | 34577.8289 | 36202.9869
CA5500060 | MI WUK HEIGHTS MWC | TUOLUMNE | 352 | 158 | None | 52800 | 82.5 | 58266.5 | 61179.825 | 0 | 0 | 61179.825 | 64055.2768
CA1900155 | WILSONA GARDENS MUTUAL | LOS ANGELES | 74 | 39 | None | 11100 | 17.3438 | 36048.2188 | 37850.6297 | 0.32 | 11535.43 | 49386.0597 | 51707.2045
CA3700041 | BARRETT LAKE MH AND RV LLC | SAN DIEGO | 150 | 58 | Some | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0.32 | 13479.13 | 57707.5253 | 60419.779
CA4400723 | MISSION SPRINGS CONFERENCE CENTER | SANTA CRUZ | 1310 | 141 |  | 196500 | 307.0312 | 134831.6562 | 141573.2391 | 0.3 | 40449.4969 | 182022.7359 | 190577.8045
CA3301775 | HIGH VALLEYS WATER DISTRICT | RIVERSIDE | 762 | 231 | None | 114300 | 178.5938 | 91034.4688 | 95586.1922 | 0.32 | 29131.03 | 124717.2222 | 130578.9316
CA3600372 | PALMS RIVER RESORT | SAN BERNARDINO | 127 | 205 |  | 19050 | 29.7656 | 40284.0781 | 42298.282 | 0.3 | 12085.2234 | 54383.5055 | 56939.5302
CA1000267 | KINGS CANYON MOBILE HOME PARK | FRESNO | 120 | 26 | None | 18000 | 28.125 | 39724.625 | 41710.8562 | 0 | 0 | 41710.8562 | 43671.2665
CA2000828 | SHADY OAKS MOBILE HOME PARK LLC | MADERA | 27 | 21 | None | 4050 | 6.3281 | 32291.8906 | 33906.4852 | 0 | 0 | 33906.4852 | 35500.09
CA3301800 | STONEWOOD CANYON ESTATES | RIVERSIDE | 40 | 26 |  | 6000 | 9.375 | 33330.875 | 34997.4187 | 0.32 | 10665.88 | 45663.2988 | 47809.4738
CA2702256 | NORTH SHORE ESTATES WS | MONTEREY | 60 | 33 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA5000015 | OID #22 - WILLIAMS TRACT | STANISLAUS | 150 | 53 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA1900100 | METTLER VALLEY MUTUAL | LOS ANGELES | 135 | 98 | None | 20250 | 31.6406 | 40923.4531 | 42969.6258 | 0.32 | 13095.505 | 56065.1308 | 58700.1919
CA2701670 | LANGLEY/VALLE PACIFICO WS | MONTEREY | 81 | 31 | None | 12150 | 18.9844 | 36607.6719 | 38438.0555 | 0.3 | 10982.3016 | 49420.357 | 51743.1138
CA3610110 | ARROWBEAR PARK CWD | SAN BERNARDINO | 1856 | 955 | Some | 278400 | 435 | 178469 | 187392.45 | 0.3 | 53540.7 | 240933.15 | 252257.0081
CA2700799 | VISTA DEL TORO WS | MONTEREY | 92 | 28 | None | 13800 | 21.5625 | 37486.8125 | 39361.1531 | 0.3 | 11246.0438 | 50607.1969 | 52985.7351
CA4200807 | WOODSTOCK RANCH | SANTA BARBARA | 350 | 117 |  | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0.3 | 17431.9969 | 78443.9859 | 82130.8533
CA5200551 | WOODSON BRIDGE MHP | TEHAMA | 158 | 104 |  | 23700 | 37.0312 | 42761.6562 | 44899.7391 | 0 | 0 | 44899.7391 | 47010.0268
CA2000589 | MAMMOTH POOL MOBILE HOME PARK | MADERA | 60 | 32 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 38399.5397
CA2000511 | MD 85 VALETA | MADERA | 45 | 20 |  | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0 | 0 | 35417.0086 | 37081.608
CA3900607 | COUNTRY SQUIRE MOBILE ESTATES & WATER SY | SAN JOAQUIN | 64 | 49 | None | 9600 | 15 | 35249 | 37011.45 | 0 | 0 | 37011.45 | 38750.9881
CA1900936 | AQUA J. MUTUAL WATER COMPANY | LOS ANGELES | 165 | 48 | None | 24750 | 38.6719 | 43321.1094 | 45487.1648 | 0.32 | 13862.755 | 59349.9198 | 62139.3661
CA5400744 | EAST THREE RIVERS MUTUAL WATER CORP | TULARE | 40 | 15 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0 | 0 | 34997.4187 | 36642.2974
CA1100616 | ELK CREEK COMMUNITY S.D. | GLENN | 159 | 90 | None | 23850 | 37.2656 | 42841.5781 | 44983.657 | 0 | 0 | 44983.657 | 47097.8889
CA5400824 | SULTANA CSD | TULARE | 866 | 249 | None | 129900 | 202.9688 | 99346.3438 | 104313.6609 | 0 | 0 | 104313.6609 | 109216.403
CA5402048 | DEL ORO RIVER ISLAND SERV TERR #2 | TULARE | 99 | 27 | None | 14850 | 23.2031 | 38046.2656 | 39948.5789 | 0 | 0 | 39948.5789 | 41826.1621
CA4000815 | LAS VENTANAS RANCH | SAN LUIS OBISPO | 108 | 33 |  | 16200 | 25.3125 | 38765.5625 | 40703.8406 | 0.3 | 11629.6688 | 52333.5094 | 54793.1843
CA1410006 | BIG PINE CSD | INYO | 792 | 304 | Some | 118800 | 185.625 | 93432.125 | 98103.7312 | 0 | 0 | 98103.7312 | 102714.6066
CA3610030 | MARIANA RANCHOS CWD | SAN BERNARDINO | 1459 | 442 | None | 218850 | 341.9531 | 146740.0156 | 154077.0164 | 0.3 | 44022.0047 | 198099.0211 | 207409.6751
CA2700687 | PESANTE RD WS #02 | MONTEREY | 120 | 40 | None | 18000 | 28.125 | 39724.625 | 41710.8562 | 0.3 | 11917.3875 | 53628.2438 | 56148.7712
CA5510023 | SONORA MEADOWS MUTUAL WTR CO | TUOLUMNE | 1123 | 448 | Some | 168450 | 263.2031 | 119886.2656 | 125880.5789 | 0 | 0 | 125880.5789 | 131796.9661
CA2700728 | SAN ARDO WD | MONTEREY | 575 | 161 | None | 86250 | 134.7656 | 76089.0781 | 79893.532 | 0.3 | 22826.7234 | 102720.2555 | 107548.1075
CA1000426 | RIVERBEND MOBILE HOME & RV PARK | FRESNO | 400 | 49 | None | 60000 | 93.75 | 62102.75 | 65207.8875 | 0 | 0 | 65207.8875 | 68272.6582
CA3400155 | SEQUOIA WATER ASSOC | SACRAMENTO | 54 | 18 | None | 8100 | 12.6562 | 34449.7812 | 36172.2703 | 0.32 | 11023.93 | 47196.2003 | 49414.4217
CA3400138 | LOCKE WATER WORKS CO [SWS] | SACRAMENTO | 80 | 44 | None | 12000 | 18.75 | 36527.75 | 38354.1375 | 0.32 | 11688.88 | 50043.0175 | 52395.0393
CA3303087 | SAN JOSE COMMUNITY WATER SYSTEM | RIVERSIDE | 71 | 15 |  | 10650 | 16.6406 | 35808.4531 | 37598.8758 | 0.32 | 11458.705 | 49057.5808 | 51363.2871
CA1410505 | NPS - DEATH VALLEY, FURNACE CREEK | INYO | 150 | 150 |  | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA1910023 | AVERYDALE MWC | LOS ANGELES | 964 | 297 | None | 144600 | 225.9375 | 107178.6875 | 112537.6219 | 0.32 | 34297.18 | 146834.8019 | 153736.0376
CA2701633 | PARADISE RD WS #21 | MONTEREY | 48 | 16 |  | 7200 | 11.25 | 33970.25 | 35668.7625 | 0.3 | 10191.075 | 45859.8375 | 48015.2499
CA5200560 | MIRA MONTE WATER CO. | TEHAMA | 142 | 41 | NULL | 21300 | 33.2812 | 41482.9062 | 43557.0516 | 0 | 0 | 43557.0516 | 45604.233
CA3901092 | SAN JOAQUIN WATER WORKS #2 | SAN JOAQUIN | 293 | 94 | Some | 43950 | 68.6719 | 53551.1094 | 56228.6648 | 0 | 0 | 56228.6648 | 58871.4121
CA3600386 | FOOTHILL ESTATES MHP | SAN BERNARDINO | 135 | 33 |  | 20250 | 31.6406 | 40923.4531 | 42969.6258 | 0.3 | 12277.0359 | 55246.6617 | 57843.2548
CA2310012 | IRISH BEACH WATER DISTRICT | MENDOCINO | 560 | 204 | Some | 84000 | 131.25 | 74890.25 | 78634.7625 | 0 | 0 | 78634.7625 | 82330.5963
CA3510006 | MISSION OAKS MOBILE HOME PARK | SAN BENITO | 550 | 238 | None | 82500 | 128.9062 | 74091.0312 | 77795.5828 | 0.3 | 22227.3094 | 100022.8922 | 104723.9681
CA3500510 | MCMAHON ROAD MUTUAL WATER COMPANY | SAN BENITO | 102 | 32 | None | 15300 | 23.9062 | 38286.0312 | 40200.3328 | 0.3 | 11485.8094 | 51686.1422 | 54115.3909
CA2701068 | IVERSON & JACKS APTS WS | MONTEREY | 150 | 31 | NULL | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0.3 | 12636.6844 | 56865.0797 | 59537.7384
CA5400550 | SEVILLE WATER COMPANY | TULARE | 691 | 90 | None | 103650 | 161.9531 | 85360.0156 | 89628.0164 | 0 | 0 | 89628.0164 | 93840.5332
CA4300771 | NEW AVENUE MUTUAL WATER COMPANY | SANTA CLARA | 302 | 113 | None | 45300 | 70.7812 | 54270.4062 | 56983.9266 | 0.32 | 17366.53 | 74350.4566 | 77844.928
CA4900793 | VINEHILL VISTAS MUTUAL WATER COMPANY | SONOMA | 42 | 29 | Some | 6300 | 9.8438 | 33490.7188 | 35165.2547 | 0.3 | 10047.2156 | 45212.4703 | 47337.4564
CA4200714 | SAN AUGUSTINE MUTUAL WATER COMPANY | SANTA BARBARA | 43 | 23 | None | 6450 | 10.0781 | 33570.6406 | 35249.1727 | 0.3 | 10071.1922 | 45320.3648 | 47450.422
CA3303035 | THERMAL PARK | RIVERSIDE | 73 | 22 |  | 10950 | 17.1094 | 35968.2969 | 37766.7117 | 0.32 | 11509.855 | 49276.5667 | 51592.5654
CA3910024 | SAN JOAQUIN COUNTY - WILKINSON MANOR | SAN JOAQUIN | 903 | 258 | Some | 135450 | 211.6406 | 102303.4531 | 107418.6258 | 0 | 0 | 107418.6258 | 112467.3012
CA5403212 | MONSON WATER SYSTEM | TULARE | 140 | 32 | None | 21000 | 32.8125 | 41323.0625 | 43389.2156 | 0 | 0 | 43389.2156 | 45428.5088
CA1900130 | DEL RIO MUTUAL | LOS ANGELES | 700 | 250 | None | 105000 | 164.0625 | 86079.3125 | 90383.2781 | 0.32 | 27545.38 | 117928.6581 | 123471.3051
CA4500290 | PINE GROVE MOBILEHOME PARK | SHASTA | 53 | 19 | None | 7950 | 12.4219 | 34369.8594 | 36088.3523 | 0 | 0 | 36088.3523 | 37784.5049
CA1502653 | BELLA VISTA MUTUAL WATER COMPANY | KERN | 150 | 46 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA3900512 | MORADA ACRES WATER SYSTEM | SAN JOAQUIN | 105 | 32 | None | 15750 | 24.6094 | 38525.7969 | 40452.0867 | 0 | 0 | 40452.0867 | 42353.3348
CA2700733 | SAN JUAN RD WS #01 | MONTEREY | 49 | 15 | None | 7350 | 11.4844 | 34050.1719 | 35752.6805 | 0.3 | 10215.0516 | 45967.732 | 48128.2154
CA1700584 | WESTWIND MOBILE HOME PARK | LAKE | 104 | 38 |  | 15600 | 24.375 | 38445.875 | 40368.1687 | 0 | 0 | 40368.1687 | 42265.4727
CA1400006 | PINE CREEK VILLAGE | INYO | 350 | 89 | Some | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0 | 0 | 61011.9891 | 63879.5525
CA2701956 | PIONEER PLACE MWS | MONTEREY | 66 | 22 | None | 9900 | 15.4688 | 35408.8438 | 37179.2859 | 0.3 | 10622.6531 | 47801.9391 | 50048.6302
CA1500483 | ALLEN ROAD MUTUAL WATER SYSTEM | KERN | 195 | 59 | None | 29250 | 45.7031 | 45718.7656 | 48004.7039 | 0 | 0 | 48004.7039 | 50260.925
CA5400735 | RODRIGUEZ LABOR CAMP | TULARE | 110 | 35 | None | 16500 | 25.7812 | 38925.4062 | 40871.6766 | 0 | 0 | 40871.6766 | 42792.6454
CA1700702 | INNISFREE WATER COMPANY | LAKE | 56 | 17 |  | 8400 | 13.125 | 34609.625 | 36340.1062 | 0 | 0 | 36340.1062 | 38048.0912
CA4000741 | H2O, INC | SAN LUIS OBISPO | 60 | 25 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA5000014 | OID #46 - SUNSET OAKS | STANISLAUS | 269 | 79 | None | 40350 | 63.0469 | 51632.9844 | 54214.6336 | 0 | 0 | 54214.6336 | 56762.7214
CA5410039 | PLAINVIEW MUTUAL WATER COMPANY | TULARE | 617 | 187 | Some | 92550 | 144.6094 | 79445.7969 | 83418.0867 | 0 | 0 | 83418.0867 | 87338.7368
CA1400109 | SIERRA NORTH COMMUNITY SERVICE DISTRICT | INYO | 45 | 16 | None | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0 | 0 | 35417.0086 | 37081.608
CA1900849 | LLANO DEL RIO WATER COMPANY | LOS ANGELES | 510 | 186 | Some | 76500 | 119.5312 | 70894.1562 | 74438.8641 | 0.32 | 22686.13 | 97124.9941 | 101689.8688
CA0500027 | LILI VALLEY WATER CO. | CALAVERAS | 99 | 70 |  | 14850 | 23.2031 | 38046.2656 | 39948.5789 | 0 | 0 | 39948.5789 | 41826.1621
CA1000627 | ZONNEVELD DAIRY - CERINI | FRESNO | 48 | 17 | None | 7200 | 11.25 | 33970.25 | 35668.7625 | 0 | 0 | 35668.7625 | 37345.1943
CA3900907 | BEL AIR MOBILE ESTATE | SAN JOAQUIN | 150 | 116 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA2610004 | JUNE LAKE PUD - DOWN CANYON | MONO | 2810 | 389 | None | 421500 | 658.5938 | 254714.4688 | 267450.1922 | 0 | 0 | 267450.1922 | 280020.3512
CA0707553 | RIVERVIEW MOBILE HOMES | CONTRA COSTA | 216 | 45 |  | 32400 | 50.625 | 47397.125 | 49766.9812 | 0.3 | 14219.1375 | 63986.1188 | 66993.4663
CA3600086 | DAGGETT COMM SVCS DIST | SAN BERNARDINO | 795 | 196 | None | 119250 | 186.3281 | 93671.8906 | 98355.4852 | 0.3 | 28101.5672 | 126457.0523 | 132400.5338
CA2210925 | YOSEMITE TERRACE ESTATES | MARIPOSA | 130 | 53 | Some | 19500 | 30.4688 | 40523.8438 | 42550.0359 | 0 | 0 | 42550.0359 | 44549.8876
CA2700629 | MANZANITA HILLS WA | MONTEREY | 75 | 31 | NULL | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0.3 | 10838.4422 | 48772.9898 | 51065.3204
CA1900154 | TIERRA BONITA MUTUAL WATER | LOS ANGELES | 75 | 32 | None | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0.32 | 11561.005 | 49495.5527 | 51821.8436
CA3400121 | EL DORADO MOBILE HOME PARK | SACRAMENTO | 256 | 128 | None | 38400 | 60 | 50594 | 53123.7 | 0.32 | 16190.08 | 69313.78 | 72571.5277
CA2700837 | BLACKIE RD WS #05 | MONTEREY | 62 | 16 | None | 9300 | 14.5312 | 35089.1562 | 36843.6141 | 0.3 | 10526.7469 | 47370.3609 | 49596.7679
CA1400025 | VALLEY VISTA MUTUAL WATER COMPANY | INYO | 70 | 25 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0 | 0 | 37514.9578 | 39278.1608
CA4300740 | MOUNTAIN SPRINGS MUTUAL WATER COMPANY | SANTA CLARA | 37 | 18 |  | 5550 | 8.6719 | 33091.1094 | 34745.6648 | 0.32 | 10589.155 | 45334.8198 | 47465.5564
CA1010052 | SIERRA CEDARS CSD | FRESNO | 850 | 229 | None | 127500 | 199.2188 | 98067.5938 | 102970.9734 | 0 | 0 | 102970.9734 | 107810.6092
CA5403113 | SOUTH FORK ESTATES MUTUAL WATER CO | TULARE | 92 | 39 | None | 13800 | 21.5625 | 37486.8125 | 39361.1531 | 0 | 0 | 39361.1531 | 41211.1273
CA5610008 | PLEASANT VALLEY MUTUAL WATER CO | VENTURA | 5000 | 1630 | None | 750000 | 1171.875 | 429743.375 | 451230.5438 | 0.32 | 137517.88 | 588748.4237 | 616419.5997
CA3900558 | RANCHO SAN JOAQUIN WATER SYS | SAN JOAQUIN | 141 | 52 | None | 21150 | 33.0469 | 41402.9844 | 43473.1336 | 0 | 0 | 43473.1336 | 45516.3709
CA1009120 | RAU DAIRY | FRESNO | 105 | 43 | None | 15750 | 24.6094 | 38525.7969 | 40452.0867 | 0 | 0 | 40452.0867 | 42353.3348
CA5410024 | RICHGROVE COMMUNITY SERVICES DISTRICT | TULARE | 1617 | 524 | None | 242550 | 378.9844 | 159367.6719 | 167336.0555 | 0 | 0 | 167336.0555 | 175200.8501
CA0707601 | RUSSOS MOBILE PARK | CONTRA COSTA | 110 | 20 |  | 16500 | 25.7812 | 38925.4062 | 40871.6766 | 0.3 | 11677.6219 | 52549.2984 | 55019.1155
CA1502383 | NORD ROAD WATER ASSOCIATION | KERN | 32 | 16 | None | 4800 | 7.5 | 32691.5 | 34326.075 | 0 | 0 | 34326.075 | 35939.4005
CA1710013 | CALLAYOMI COUNTY WATER DISTRICT | LAKE | 1481 | 449 | Some | 222150 | 347.1094 | 148498.2969 | 155923.2117 | 0 | 0 | 155923.2117 | 163251.6027
CA1400511 | MEADOW LAKE APARTMENTS | INYO | 22 | 16 | None | 3300 | 5.1562 | 31892.2812 | 33486.8953 | 0 | 0 | 33486.8953 | 35060.7794
CA5200502 | LAS FLORES WATER WORKS | TEHAMA | 191 | 63 | None | 28650 | 44.7656 | 45399.0781 | 47669.032 | 0 | 0 | 47669.032 | 49909.4765
CA1500424 | LANDS OF PROMISE MWC | KERN | 174 | 63 | None | 26100 | 40.7812 | 44040.4062 | 46242.4266 | 0 | 0 | 46242.4266 | 48415.8206
CA1009111 | SCE/BIG CREEK POWERHOUSE #1 | FRESNO | 126 | 76 | Some | 18900 | 29.5312 | 40204.1562 | 42214.3641 | 0 | 0 | 42214.3641 | 44198.4392
CA1400036 | KEELER COMMUNITY SERVICE DISTRICT | INYO | 66 | 83 | None | 9900 | 15.4688 | 35408.8438 | 37179.2859 | 0 | 0 | 37179.2859 | 38926.7124
CA4200918 | LOS PRIETOS COMPLEX | SANTA BARBARA | 845 | 39 |  | 126750 | 198.0469 | 97667.9844 | 102551.3836 | 0.3 | 29300.3953 | 131851.7789 | 138048.8125
CA3100014 | BAKER RANCH WATER CORP | PLACER | 150 | 31 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 46307.1299
CA3600397 | MOSS MOBILE MANOR | SAN BERNARDINO | 290 | 43 |  | 43500 | 67.9688 | 53311.3438 | 55976.9109 | 0.3 | 15993.4031 | 71970.3141 | 75352.9188
CA4700630 | SHASTA VIEW HEIGHTS OWNERS ASSOCIATION | SISKIYOU | 50 | 24 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA5310003 | TRINITY CENTER M.W.C. . | TRINITY | 729 | 330 |  | 109350 | 170.8594 | 88397.0469 | 92816.8992 | 0 | 0 | 92816.8992 | 97179.2935
CA2810014 | SPANISH FLAT WATER DISTRICT | NAPA | 230 | 97 | Some | 34500 | 53.9062 | 48516.0312 | 50941.8328 | 0.3 | 14554.8094 | 65496.6422 | 68574.9844
CA2600733 | COLD WATER CANYON MWC | MONO | 90 | 45 | NULL | 13500 | 21.0938 | 37326.9688 | 39193.3172 | 0 | 0 | 39193.3172 | 41035.4031
CA4000507 | GARDEN FARMS C.W.D. | SAN LUIS OBISPO | 240 | 107 | NULL | 36000 | 56.25 | 49315.25 | 51781.0125 | 0.3 | 14794.575 | 66575.5875 | 69704.6401
CA5200548 | LASSEN VIEW WATER DISTRICT | TEHAMA | 85 | 30 | NULL | 12750 | 19.9219 | 36927.3594 | 38773.7273 | 0 | 0 | 38773.7273 | 40596.0925
CA3301937 | MESQUITE MUTUAL WATER CO. | RIVERSIDE | 42 | 16 |  | 6300 | 9.8438 | 33490.7188 | 35165.2547 | 0.32 | 10717.03 | 45882.2847 | 48038.7521
CA4300567 | BURCHELL ROAD WATER ASSOCIATION | SANTA CLARA | 132 | 27 | None | 19800 | 30.9375 | 40683.6875 | 42717.8719 | 0.32 | 13018.78 | 55736.6519 | 58356.2745
CA4900674 | PINE HILL TERRACE MOBILE HOME PARK | SONOMA | 27 | 23 | None | 4050 | 6.3281 | 32291.8906 | 33906.4852 | 0.3 | 9687.5672 | 43594.0523 | 45642.9728
CA3900762 | RIVERSIDE MOBILE HOME PARK | SAN JOAQUIN | 55 | 58 |  | 8250 | 12.8906 | 34529.7031 | 36256.1883 | 0 | 0 | 36256.1883 | 37960.2291
CA3900702 | CORRAL HOLLOW PWS | SAN JOAQUIN | 98 | 44 | Some | 14700 | 22.9688 | 37966.3438 | 39864.6609 | 0 | 0 | 39864.6609 | 41738.3
CA5000080 | COUNTRY WESTERN MOBILE HOME PARK | STANISLAUS | 90 | 55 |  | 13500 | 21.0938 | 37326.9688 | 39193.3172 | 0 | 0 | 39193.3172 | 41035.4031
CA5602132 | WATERS ROAD DOMESTIC USERS GROUP | VENTURA | 25 | 16 | None | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0.32 | 10282.255 | 44020.9042 | 46089.8867
CA3601015 | IRONWOOD CAMP | SAN BERNARDINO | 1000 | 74 | Some | 150000 | 234.375 | 110055.875 | 115558.6687 | 0.3 | 33016.7625 | 148575.4312 | 155558.4765
CA5000013 | OID #45 | STANISLAUS | 144 | 51 | None | 21600 | 33.75 | 41642.75 | 43724.8875 | 0 | 0 | 43724.8875 | 45779.9572
CA1910006 | SO. CAL. EDISON CO.-SANTA CATALINA | LOS ANGELES | 4096 | 1886 | None | 614400 | 960 | 357494 | 375368.7 | 0.32 | 114398.08 | 489766.78 | 512785.8187
CA1610007 | HOME GARDEN CSD | KINGS | 1750 | 467 |  | 262500 | 410.1562 | 169997.2812 | 178497.1453 | 0 | 0 | 178497.1453 | 186886.5111
CA2700686 | GARLEN COURT WS | MONTEREY | 65 | 17 |  | 9750 | 15.2344 | 35328.9219 | 37095.368 | 0.3 | 10598.6766 | 47694.0445 | 49935.6646
CA2701589 | SUNNY ACRES MWS | MONTEREY | 45 | 15 | None | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0.3 | 10119.1453 | 45536.1539 | 47676.3531
CA2000800 | MARQUEZ RENTAL | MADERA | 50 | 20 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 37520.9186
CA5410021 | EARLIMART PUD | TULARE | 8800 | 1545 | None | 1320000 | 2062.5 | 733446.5 | 770118.825 | 0 | 0 | 770118.825 | 806314.4098
CA3600400 | APPLE VALLEY VILLAGE MHE | SAN BERNARDINO | 180 | 93 |  | 27000 | 42.1875 | 44519.9375 | 46745.9344 | 0.3 | 13355.9813 | 60101.9156 | 62926.7057
CA3600297 | GORDON ACRES WATER CO | SAN BERNARDINO | 200 | 66 |  | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.3 | 13835.5125 | 62259.8063 | 65186.0171
CA5602117 | STRICKLAND ACRES | VENTURA | 429 | 128 | None | 64350 | 100.5469 | 64420.4844 | 67641.5086 | 0.32 | 20614.555 | 88256.0636 | 92404.0986
CA1910158 | STERLING MUTUAL WATER COMPANY | LOS ANGELES | 548 | 201 | None | 82200 | 128.4375 | 73931.1875 | 77627.7469 | 0.32 | 23657.98 | 101285.7269 | 106046.156
CA4300542 | SAN MARTIN COUNTY WATER DISTRICT | SANTA CLARA | 618 | 185 | None | 92700 | 144.8438 | 79525.7188 | 83502.0047 | 0.32 | 25448.23 | 108950.2347 | 114070.8957
CA1500296 | FULLER ACRES MUTUAL WATER COMPANY | KERN | 545 | 165 | None | 81750 | 127.7344 | 73691.4219 | 77375.993 | 0 | 0 | 77375.993 | 81012.6646
CA1500344 | SOUTH KERN MUTUAL WATER COMPANY | KERN | 32 | 15 | None | 4800 | 7.5 | 32691.5 | 34326.075 | 0 | 0 | 34326.075 | 35939.4005
CA1000407 | GEORGE COX WATER SYSTEM | FRESNO | 40 | 20 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0 | 0 | 34997.4187 | 36642.2974
CA3901337 | MORADA ESTATES N PWS #46 | SAN JOAQUIN | 180 | 129 | Some | 27000 | 42.1875 | 44519.9375 | 46745.9344 | 0 | 0 | 46745.9344 | 48942.9933
CA1500252 | KERN VALLEY MUTUAL WATER COMPANY | KERN | 47 | 47 | None | 7050 | 11.0156 | 33890.3281 | 35584.8445 | 0 | 0 | 35584.8445 | 37257.3322
CA5301001 | BUCKTAIL MUTUAL WATER COMPANY | TRINITY | 61 | 42 | None | 9150 | 14.2969 | 35009.2344 | 36759.6961 | 0 | 0 | 36759.6961 | 38487.4018
CA1502670 | FAIRVIEW WATER COMPANY, LLC | KERN | 240 | 72 | Some | 36000 | 56.25 | 49315.25 | 51781.0125 | 0 | 0 | 51781.0125 | 54214.7201
CA4710013 | LAKE SHASTINA C.S.D | SISKIYOU | 2400 | 1286 | Some | 360000 | 562.5 | 221946.5 | 233043.825 | 0 | 0 | 233043.825 | 243996.8848
CA2701040 | MCCOY RD WS #05 | MONTEREY | 72 | 24 | None | 10800 | 16.875 | 35888.375 | 37682.7937 | 0.3 | 10766.5125 | 48449.3063 | 50726.4236
CA5400655 | CENTRAL MUTUAL WATER CO | TULARE | 119 | 41 | None | 17850 | 27.8906 | 39644.7031 | 41626.9383 | 0 | 0 | 41626.9383 | 43583.4044
CA1500578 | LONG CANYON WATER COMPANY CORP. | KERN | 122 | 64 | None | 18300 | 28.5938 | 39884.4688 | 41878.6922 | 0 | 0 | 41878.6922 | 43846.9907
CA5403043 | YETTEM WATER SYSTEM | TULARE | 350 | 66 | None | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0 | 0 | 61011.9891 | 63879.5525
CA5500086 | SONORA ESTATES MOBILE HOME PARK | TUOLUMNE | 231 | 87 |  | 34650 | 54.1406 | 48595.9531 | 51025.7508 | 0 | 0 | 51025.7508 | 53423.9611
CA1206002 | PALOMINO ESTATES WATER COMPANY | HUMBOLDT | 64 | 19 | NULL | 9600 | 15 | 35249 | 37011.45 | 0 | 0 | 37011.45 | 38750.9881
CA1500442 | SUNSET APARTMENTS WS | KERN | 37 | 20 | None | 5550 | 8.6719 | 33091.1094 | 34745.6648 | 0 | 0 | 34745.6648 | 36378.7111
CA4200678 | SANTA ANITA MUTUAL WATER COMPANY | SANTA BARBARA | 38 | 19 | Some | 5700 | 8.9062 | 33171.0312 | 34829.5828 | 0.3 | 9951.3094 | 44780.8922 | 46885.5941
CA3900523 | MORADA MANOR WATER SYSTEM | SAN JOAQUIN | 109 | 34 | None | 16350 | 25.5469 | 38845.4844 | 40787.7586 | 0 | 0 | 40787.7586 | 42704.7832
CA4400557 | ST FRANCIS TRACT WATER SYSTEM | SANTA CRUZ | 118 | 29 | None | 17700 | 27.6562 | 39564.7812 | 41543.0203 | 0.3 | 11869.4344 | 53412.4547 | 55922.8401
CA1502164 | LLANAS CAMP FOUR WATER SYSTEM | KERN | 54 | 55 | None | 8100 | 12.6562 | 34449.7812 | 36172.2703 | 0 | 0 | 36172.2703 | 37872.367
CA1200687 | RIVERBEND MOBILE HOME PARK | HUMBOLDT | 60 | 28 | NULL | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 38399.5397
CA2400128 | COUNTRY CLUB COUNTY WD | MERCED | 64 | 23 | Some | 9600 | 15 | 35249 | 37011.45 | 0 | 0 | 37011.45 | 38750.9881
CA3000519 | HYNES ESTATES MUTUAL WATER CO. | ORANGE | 139 | 42 | None | 20850 | 32.5781 | 41243.1406 | 43305.2977 | 0.3 | 12372.9422 | 55678.2398 | 58295.1171
CA3200510 | IVCSD CRESCENT MILLS | PLUMAS | 258 | 78 | None | 38700 | 60.4688 | 50753.8438 | 53291.5359 | 0 | 0 | 53291.5359 | 55796.2381
CA0610001 | ARBUCKLE PUBLIC UTILITY DISTRICT | COLUSA | 2778 | 1024 | Some | 416700 | 651.0938 | 252156.9688 | 264764.8172 | 0 | 0 | 264764.8172 | 277208.7636
CA1500413 | TEJON RANCH MAIN HEADQUARTERS | KERN | 132 | 33 | None | 19800 | 30.9375 | 40683.6875 | 42717.8719 | 0 | 0 | 42717.8719 | 44725.6119
CA3600301 | STRAWBERRY LODGE MWC | SAN BERNARDINO | 640 | 137 |  | 96000 | 150 | 81284 | 85348.2 | 0.3 | 24385.2 | 109733.4 | 114890.8698
CA0707575 | FRANKS MARINA | CONTRA COSTA | 185 | 66 | None | 27750 | 43.3594 | 44919.5469 | 47165.5242 | 0.3 | 13475.8641 | 60641.3883 | 63491.5335
CA3110019 | SQUAW VALLEY MWC | PLACER | 500 | 271 | Some | 75000 | 117.1875 | 70094.9375 | 73599.6844 | 0 | 0 | 73599.6844 | 77058.8695
CA5410036 | LSID-STRATHMORE SYSTEM | TULARE | 500 | 161 | None | 75000 | 117.1875 | 70094.9375 | 73599.6844 | 0 | 0 | 73599.6844 | 77058.8695
CA0800603 | BUTTE COURT MOBILE HOME PARK | DEL NORTE | 67 | 23 | None | 10050 | 15.7031 | 35488.7656 | 37263.2039 | 0 | 0 | 37263.2039 | 39014.5745
CA1910159 | TRACT 180 MUTUAL WATER CO. | LOS ANGELES | 14000 | 1184 | Some | 2100000 | 3281.25 | 1149040.25 | 1206492.2625 | 0.32 | 367692.88 | 1574185.1425 | 1648171.8442
CA3200150 | HAMILTON BRANCH MWC | PLUMAS | 250 | 113 | Some | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 55093.3412
CA0900308 | QUINTETTE SERVICE CORP WATER | EL DORADO | 79 | 52 | Some | 11850 | 18.5156 | 36447.8281 | 38270.2195 | 0.3 | 10934.3484 | 49204.568 | 51517.1827
CA1800529 | SUSAN HILLS ESTATES WC | LASSEN | 316 | 98 | None | 47400 | 74.0625 | 55389.3125 | 58158.7781 | 0 | 0 | 58158.7781 | 60892.2407
CA2300837 | YOKAYO TRIBE OF INDIANS | MENDOCINO | 75 | 23 | NULL | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0 | 0 | 37934.5477 | 39717.4714
CA2800531 | MOORE'S RESORT | NAPA | 70 | 20 |  | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0.3 | 10718.5594 | 48233.5172 | 50500.4925
CA4000501 | HALCYON WATER SYSTEM | SAN LUIS OBISPO | 105 | 46 | None | 15750 | 24.6094 | 38525.7969 | 40452.0867 | 0.3 | 11557.7391 | 52009.8258 | 54454.2876
CA4000523 | S & T MUTUAL WATER COMPANY | SAN LUIS OBISPO | 591 | 179 | None | 88650 | 138.5156 | 77367.8281 | 81236.2195 | 0.3 | 23210.3484 | 104446.568 | 109355.5567
CA4900943 | ALLIANCE REDWOODS CONFERENCE GROUNDS | SONOMA | 418 | 73 | None | 62700 | 97.9688 | 63541.3438 | 66718.4109 | 0.3 | 19062.4031 | 85780.8141 | 89812.5123
CA5400504 | PORTERVILLE MOBILE VILLAGE | TULARE | 154 | 62 | None | 23100 | 36.0938 | 42441.9688 | 44564.0672 | 0 | 0 | 44564.0672 | 46658.5783
CA4610001 | CITY OF LOYALTON | SIERRA | 856 | 360 | Some | 128400 | 200.625 | 98547.125 | 103474.4812 | 0 | 0 | 103474.4812 | 108337.7819
CA2810009 | BERRYESSA PINES WATER SYSTEM | NAPA | 261 | 78 | Some | 39150 | 61.1719 | 50993.6094 | 53543.2898 | 0.3 | 15298.0828 | 68841.3727 | 72076.9172
CA5200546 | ANTELOPE-HOMEWOOD MHP | TEHAMA | 140 | 24 | NULL | 21000 | 32.8125 | 41323.0625 | 43389.2156 | 0 | 0 | 43389.2156 | 45428.5088
CA0707574 | SANTIAGO ISLAND VILLAGE | CONTRA COSTA | 400 | 211 |  | 60000 | 93.75 | 62102.75 | 65207.8875 | 0.3 | 18630.825 | 83838.7125 | 87779.132
CA5400881 | SUNRISE MUTUAL WATER CO. | TULARE | 80 | 39 | None | 12000 | 18.75 | 36527.75 | 38354.1375 | 0 | 0 | 38354.1375 | 40156.782
CA2000729 | MADERA CO SA16 SUMNER HILL-WATER SYSTEM | MADERA | 135 | 41 | None | 20250 | 31.6406 | 40923.4531 | 42969.6258 | 0 | 0 | 42969.6258 | 44989.1982
CA0600013 | COLUSA CO. WWD #2 - PRINCETON | COLUSA | 382 | 120 | Some | 57300 | 89.5312 | 60664.1562 | 63697.3641 | 0 | 0 | 63697.3641 | 66691.1402
CA1000247 | SHERWOOD FOREST MHP | FRESNO | 75 | 48 | NULL | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0 | 0 | 37934.5477 | 39717.4714
CA4010005 | OCEANO COMM SERVICES DIST. | SAN LUIS OBISPO | 7487 | 2203 | None | 1123050 | 1754.7656 | 628509.0781 | 659934.532 | 0.3 | 188552.7234 | 848487.2555 | 888366.1565
CA3200148 | FEATHER RIVER RV & MHP | PLUMAS | 700 | 21 | None | 105000 | 164.0625 | 86079.3125 | 90383.2781 | 0 | 0 | 90383.2781 | 94631.2922
CA3900505 | FARMINGTON WATER COMPANY | SAN JOAQUIN | 270 | 78 |  | 40500 | 63.2812 | 51712.9062 | 54298.5516 | 0 | 0 | 54298.5516 | 56850.5835
CA4400763 | BUENA VISTA MIGRANT CENTER | SANTA CRUZ | 455 | 140 | None | 68250 | 106.6406 | 66498.4531 | 69823.3758 | 0.3 | 19949.5359 | 89772.9117 | 93992.2386
CA2701553 | POND-DEROSA OAKS WC | MONTEREY | 216 | 75 | None | 32400 | 50.625 | 47397.125 | 49766.9812 | 0.3 | 14219.1375 | 63986.1188 | 66993.4663
CA5710005 | CITY OF WINTERS | YOLO | 7417 | 2221 | Some | 1112550 | 1738.3594 | 622914.5469 | 654060.2742 | 0 | 0 | 654060.2742 | 684801.1071
CA0610003 | MAXWELL PUBLIC UTILITY DISTRICT | COLUSA | 1175 | 393 | None | 176250 | 275.3906 | 124042.2031 | 130244.3133 | 0 | 0 | 130244.3133 | 136365.796
CA3500825 | UNION HEIGHTS MWC | SAN BENITO | 98 | 29 | None | 14700 | 22.9688 | 37966.3438 | 39864.6609 | 0.3 | 11389.9031 | 51254.5641 | 53663.5286
CA1400059 | BROOKSIDE MOBILE HOME PARK | INYO | 126 | 45 | None | 18900 | 29.5312 | 40204.1562 | 42214.3641 | 0 | 0 | 42214.3641 | 44198.4392
CA1200538 | MYERS FLAT M.W.S. INC. | HUMBOLDT | 400 | 101 | Some | 60000 | 93.75 | 62102.75 | 65207.8875 | 0 | 0 | 65207.8875 | 68272.6582
CA2210921 | WHISPERING PINES APARTMENTS | MARIPOSA | 74 | 28 | None | 11100 | 17.3438 | 36048.2188 | 37850.6297 | 0 | 0 | 37850.6297 | 39629.6093
CA0707597 | SANDY POINT MOBILE HOME PARK | CONTRA COSTA | 67 | 24 |  | 10050 | 15.7031 | 35488.7656 | 37263.2039 | 0.3 | 10646.6297 | 47909.8336 | 50161.5958
CA4400754 | MONTE VISTA CHRISTIAN SCHOOL | SANTA CRUZ | 1083 | 43 |  | 162450 | 253.8281 | 116689.3906 | 122523.8602 | 0.3 | 35006.8172 | 157530.6773 | 164934.6192
CA5400647 | YOKOHL MUTUAL WATER CO | TULARE | 95 | 32 | None | 14250 | 22.2656 | 37726.5781 | 39612.907 | 0 | 0 | 39612.907 | 41474.7137
CA3610021 | FALLSVALE SERVICE COMPANY | SAN BERNARDINO | 995 | 492 | Some | 149250 | 233.2031 | 109656.2656 | 115139.0789 | 0.3 | 32896.8797 | 148035.9586 | 154993.6486
CA1910246 | LAND PROJECTS MUTUAL WATER CO. | LOS ANGELES | 1500 | 544 | Some | 225000 | 351.5625 | 150016.8125 | 157517.6531 | 0.32 | 48005.38 | 205523.0331 | 215182.6157
CA0706005 | FARRAR PARK PROPERTY OWNERS | CONTRA COSTA | 140 | 70 |  | 21000 | 32.8125 | 41323.0625 | 43389.2156 | 0.3 | 12396.9188 | 55786.1344 | 58408.0827
CA1500544 | ENOS LANE PUBLIC UTILITY DISTRICT | KERN | 365 | 89 | None | 54750 | 85.5469 | 59305.4844 | 62270.7586 | 0 | 0 | 62270.7586 | 65197.4842
CA1500455 | WILLIAM FISHER MEMORIAL WATER COMPANY | KERN | 56 | 16 | None | 8400 | 13.125 | 34609.625 | 36340.1062 | 0 | 0 | 36340.1062 | 38048.0912
CA3400172 | TOKAY PARK WATER CO | SACRAMENTO | 525 | 198 | None | 78750 | 123.0469 | 72092.9844 | 75697.6336 | 0.32 | 23069.755 | 98767.3886 | 103409.4559
CA4200885 | CHALK HILL ESTATES HOA | SANTA BARBARA | 38 | 15 |  | 5700 | 8.9062 | 33171.0312 | 34829.5828 | 0.3 | 9951.3094 | 44780.8922 | 46885.5941
CA5200657 | NORCAL WATER WORKS | TEHAMA | 45 | 17 | NULL | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0 | 0 | 35417.0086 | 37081.608
CA5301201 | SEYMOUR'S MUTUAL WATER SYSTEM | TRINITY | 29 | 27 | NULL | 4350 | 6.7969 | 32451.7344 | 34074.3211 | 0 | 0 | 34074.3211 | 35675.8142
CA3700291 | OCOTILLO OASIS, LLC | SAN DIEGO | 100 | 55 | NULL | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.32 | 12200.38 | 52232.8769 | 54687.8221
CA2700662 | MURPHY HILL WS #01 | MONTEREY | 65 | 29 | NULL | 9750 | 15.2344 | 35328.9219 | 37095.368 | 0.3 | 10598.6766 | 47694.0445 | 49935.6646
CA3910009 | SAN JOAQUIN COUNTY - THORNTON | SAN JOAQUIN | 1033 | 292 | Some | 154950 | 242.1094 | 112693.2969 | 118327.9617 | 0 | 0 | 118327.9617 | 123889.3759
CA3901216 | SANTOS RANCH PWS #5-CSA #35 | SAN JOAQUIN | 250 | 97 | Some | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 55093.3412
CA5200535 | LIVE OAK ACRES MWC INC. | TEHAMA | 80 | 40 |  | 12000 | 18.75 | 36527.75 | 38354.1375 | 0 | 0 | 38354.1375 | 40156.782
CA4100503 | BUTANO CANYON MUTUAL | SAN MATEO | 150 | 94 |  | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0.32 | 13479.13 | 57707.5253 | 60419.779
CA2700606 | HIDDEN VIEWS MHP WS | MONTEREY | 75 | 31 | None | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0.3 | 10838.4422 | 48772.9898 | 51065.3204
CA4900720 | MOBILE HOME ESTATES | SONOMA | 210 | 150 | None | 31500 | 49.2188 | 46917.5938 | 49263.4734 | 0.3 | 14075.2781 | 63338.7516 | 66315.6729
CA0800700 | LAS PALMAS MOBILE HOME PARK | DEL NORTE | 120 | 60 | Some | 18000 | 28.125 | 39724.625 | 41710.8562 | 0 | 0 | 41710.8562 | 43671.2665
CA3701184 | BUTTERFIELD RANCH | SAN DIEGO | 350 | 75 |  | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0.32 | 18594.13 | 79606.1191 | 83347.6067
CA1500231 | VICTORY MUTUAL WATER COMPANY | KERN | 849 | 173 | None | 127350 | 198.9844 | 97987.6719 | 102887.0555 | 0 | 0 | 102887.0555 | 107722.7471
CA5200600 | GURNSEY AVENUE MUTUAL WATER SYSTEM | TEHAMA | 25 | 15 |  | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0 | 0 | 33738.6492 | 35324.3657
CA4600009 | SIERRA CSA #5, SIERRA BROOKS | SIERRA | 515 | 219 | Some | 77250 | 120.7031 | 71293.7656 | 74858.4539 | 0 | 0 | 74858.4539 | 78376.8012
CA2210906 | MARIPOSA PINES MUTUAL | MARIPOSA | 284 | 87 | Some | 42600 | 66.5625 | 52831.8125 | 55473.4031 | 0 | 0 | 55473.4031 | 58080.6531
CA2700624 | LEAFWOOD COMMUNITY WA | MONTEREY | 66 | 23 | NULL | 9900 | 15.4688 | 35408.8438 | 37179.2859 | 0.3 | 10622.6531 | 47801.9391 | 50048.6302
CA1502608 | OWENS PEAK WEST | KERN | 79 | 24 | None | 11850 | 18.5156 | 36447.8281 | 38270.2195 | 0 | 0 | 38270.2195 | 40068.9198
CA3500575 | SPRINGWOOD ESTATES MWC | SAN BENITO | 50 | 15 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0.3 | 10239.0281 | 46075.6266 | 48241.181
CA4300996 | VALLEY VIEW RANCHES | SANTA CLARA | 45 | 16 | None | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0.32 | 10793.755 | 46210.7636 | 48382.6695
CA0707608 | MARINA MOBILE MANOR | CONTRA COSTA | 75 | 24 | None | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0.3 | 10838.4422 | 48772.9898 | 51065.3204
CA2702328 | VENTANA BIG SUR INN WS | MONTEREY | 193 | 26 | Some | 28950 | 45.2344 | 45558.9219 | 47836.868 | 0.3 | 13667.6766 | 61504.5445 | 64395.2581
CA5400718 | WILLIAMS MUTUAL WATER CO | TULARE | 180 | 50 | None | 27000 | 42.1875 | 44519.9375 | 46745.9344 | 0 | 0 | 46745.9344 | 48942.9933
CA0707523 | FLAMINGO MOBILE MANOR | CONTRA COSTA | 200 | 62 | NULL | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.3 | 13835.5125 | 62259.8063 | 65186.0171
CA4510007 | COTTONWOOD COUNTY WATER DIST. | SHASTA | 3316 | 1226 |  | 497400 | 777.1875 | 295154.9375 | 309912.6844 | 0 | 0 | 309912.6844 | 324478.5805
CA0103041 | TRAILER HAVEN MOBILE HOME PARK | ALAMEDA | 459 | 191 | None | 68850 | 107.5781 | 66818.1406 | 70159.0477 | 0.3 | 20045.4422 | 90204.4898 | 94444.1009
CA0400007 | BUTTE CREEK ESTATES MUTUAL WATER CO | BUTTE | 399 | 168 | Some | 59850 | 93.5156 | 62022.8281 | 65123.9695 | 0 | 0 | 65123.9695 | 68184.7961
CA2701820 | CORDA RD WS | MONTEREY | 60 | 19 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA5400602 | EAGLE'S NEST RESORT | TULARE | 279 | 78 | None | 41850 | 65.3906 | 52432.2031 | 55053.8133 | 0 | 0 | 55053.8133 | 57641.3425
CA3301011 | STONE CREEK WATER CO. | RIVERSIDE | 134 | 50 | None | 20100 | 31.4062 | 40843.5312 | 42885.7078 | 0.32 | 13069.93 | 55955.6378 | 58585.5528
CA2510001 | CITY OF ALTURAS | MODOC | 2537 | 1470 | Some | 380550 | 594.6094 | 232895.7969 | 244540.5867 | 0 | 0 | 244540.5867 | 256033.9943
CA4200814 | JONATA HOMEOWNERS ASSOCIATION | SANTA BARBARA | 45 | 16 | NULL | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0.3 | 10119.1453 | 45536.1539 | 47676.3531
CA2701701 | BRADLEY-LOCKWOOD RD WS | MONTEREY | 39 | 16 | NULL | 5850 | 9.1406 | 33250.9531 | 34913.5008 | 0.3 | 9975.2859 | 44888.7867 | 46998.5597
CA2701687 | VALLEY OAKS MHP WS | MONTEREY | 120 | 46 | NULL | 18000 | 28.125 | 39724.625 | 41710.8562 | 0.3 | 11917.3875 | 53628.2438 | 56148.7712
CA4600056 | SIERRA CITY WATER WORKS, INC. | SIERRA | 250 | 89 | NULL | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 55093.3412
CA4000834 | ANZA VINEYARD ESTATES MUTUAL WATER CO | SAN LUIS OBISPO | 60 | 16 | NULL | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.3 | 10478.7938 | 47154.5719 | 49370.8368
CA2500801 | NEWELL COUNTY WATER DISTRICT | MODOC | 300 | 310 | NULL | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 59486.4469
CA2300863 | EEL RIVER CHARTER SCHOOL | MENDOCINO | 0 | 1 | None | 0 | 0 | 30134 | 31640.7 | 0 | 0 | 31640.7 | 32083.6698
CA5800847 | MJUSD LOMA RICA SCHOOL | YUBA | 150 | 6 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 44847.5928
CA4900714 | LIBERTY SCHOOL | SONOMA | 225 | 3 | None | 33750 | 52.7344 | 48116.4219 | 50522.243 | 0.3 | 15156.6729 | 65678.9159 | 66598.4207
CA1502074 | EL TEJON MIDDLE SCHOOL | KERN | 550 | 1 | None | 82500 | 128.9062 | 74091.0312 | 77795.5828 | 0 | 0 | 77795.5828 | 78884.721
CA1503140 | FRAZIER MOUNTAIN HIGH SCHOOL | KERN | 500 | 1 | Some | 75000 | 117.1875 | 70094.9375 | 73599.6844 | 0 | 0 | 73599.6844 | 74630.08
CA1800575 | SHAFFER ELEMENTARY SCHOOL | LASSEN | 320 | 1 |  | 48000 | 75 | 55709 | 58494.45 | 0 | 0 | 58494.45 | 59313.3723
CA5800844 | MJUSD BROWNS VALLEY SCHOOL | YUBA | 155 | 5 | None | 23250 | 36.3281 | 42521.8906 | 44647.9852 | 0 | 0 | 44647.9852 | 45273.0569
CA2300770 | ANDERSON VALLEY ELEMENTARY SCHOOL | MENDOCINO | 350 | 11 |  | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0 | 0 | 61011.9891 | 61866.1569
CA1300556 | MULBERRY UNION SCHOOL | IMPERIAL | 85 | 2 | None | 12750 | 19.9219 | 36927.3594 | 38773.7273 | 0 | 0 | 38773.7273 | 39316.5595
CA4900945 | PRESENTATION SCHOOL | SONOMA | 200 | 4 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.3 | 14527.2881 | 62951.5819 | 63832.904
CA2300764 | ANDERSON VALLEY HIGH SCHOOL | MENDOCINO | 300 | 8 |  | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 57611.5159
CA2900536 | CLEAR CREEK SCHOOL | NEVADA | 160 | 8 | None | 24000 | 37.5 | 42921.5 | 45067.575 | 0 | 0 | 45067.575 | 45698.5211
CA5000273 | GRATTON SCHOOL | STANISLAUS | 110 | 2 | Some | 16500 | 25.7812 | 38925.4062 | 40871.6766 | 0 | 0 | 40871.6766 | 41443.88
CA4901156 | WILLOWSIDE SCHOOL | SONOMA | 460 | 5 | None | 69000 | 107.8125 | 66898.0625 | 70242.9656 | 0.3 | 21072.8897 | 91315.8553 | 92594.2773
CA2702322 | CAPTAIN COOPER SCHOOL WS | MONTEREY | 95 | 1 |  | 14250 | 22.2656 | 37726.5781 | 39612.907 | 0.3 | 11883.8721 | 51496.7791 | 52217.734
CA3400259 | GRANT HIGH SCHOOL [SWS] | SACRAMENTO | 1400 | 12 | NULL | 210000 | 328.125 | 142024.625 | 149125.8563 | 0.32 | 47720.274 | 196846.1302 | 199601.9761
CA1502231 | ROSAMOND SCHOOL WATER SYSTEM | KERN | 940 | 2 | None | 141000 | 220.3125 | 105260.5625 | 110523.5906 | 0 | 0 | 110523.5906 | 112070.9209
CA4100513 | PESCADERO HIGH SCHOOL | SAN MATEO | 192 | 1 | None | 28800 | 45 | 45479 | 47752.95 | 0.32 | 15280.944 | 63033.894 | 63916.3685
CA1000280 | SIERRA HIGH SCHOOL | FRESNO | 690 | 26 |  | 103500 | 161.7188 | 85280.0938 | 89544.0984 | 0 | 0 | 89544.0984 | 90797.7158
CA2702490 | CENTRAL BAY HIGH SCHOOL WS | MONTEREY | 70 | 1 | None | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0.3 | 11254.4873 | 48769.4452 | 49452.2174
CA3400271 | ARCOHE ELEM SCHOOL - MAIN CAMPUS | SACRAMENTO | 465 | 2 | None | 69750 | 108.9844 | 67297.6719 | 70662.5555 | 0.32 | 22612.0177 | 93274.5732 | 94580.4172
CA1000189 | LATON HIGH SCHOOL | FRESNO | 210 | 2 | None | 31500 | 49.2188 | 46917.5938 | 49263.4734 | 0 | 0 | 49263.4734 | 49953.1621
CA1200546 | CASTERLIN SCHOOL | HUMBOLDT | 130 | 1 | None | 19500 | 30.4688 | 40523.8438 | 42550.0359 | 0 | 0 | 42550.0359 | 43145.7364
CA2800847 | NVUSD: CARNEROS SCHOOL | NAPA | 100 | 1 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.3 | 12009.7491 | 52042.2459 | 52770.8374
CA3400253 | COSUMNES RIVER ELEMENTARY SCHOOL | SACRAMENTO | 560 | 8 | None | 84000 | 131.25 | 74890.25 | 78634.7625 | 0.32 | 25163.124 | 103797.8865 | 105251.0569
CA0400063 | MANZANITA ELEMENTARY SCHOOL | BUTTE | 295 | 3 | None | 44250 | 69.1406 | 53710.9531 | 56396.5008 | 0 | 0 | 56396.5008 | 57186.0518
CA3601179 | EL MIRAGE SCHOOL | SAN BERNARDINO | 50 | 9 |  | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0.3 | 10750.9795 | 46587.578 | 47239.8041
CA5100136 | EAST NICOLAUS JOINT UNION HIGH SCHOOL | SUTTER | 338 | 1 | None | 50700 | 79.2188 | 57147.5938 | 60004.9734 | 0 | 0 | 60004.9734 | 60845.0431
CA5100145 | WINSHIP ELEMENTARY SCHOOL | SUTTER | 38 | 2 | None | 5700 | 8.9062 | 33171.0312 | 34829.5828 | 0 | 0 | 34829.5828 | 35317.197
CA2000947 | MINARETS HIGH SCHOOL | MADERA | 450 | 17 |  | 67500 | 105.4688 | 66098.8438 | 69403.7859 | 0 | 0 | 69403.7859 | 70375.4389
CA5200520 | KIRKWOOD ELEMENTARY SCHOOL | TEHAMA | 111 | 4 | None | 16650 | 26.0156 | 39005.3281 | 40955.5945 | 0 | 0 | 40955.5945 | 41528.9729
CA5200544 | VINA ELEMENTARY SCHOOL | TEHAMA | 90 | 2 | None | 13500 | 21.0938 | 37326.9688 | 39193.3172 | 0 | 0 | 39193.3172 | 39742.0236
CA2400065 | PLAINSBURG ELEMENTARY SCHOOL | MERCED | 126 | 5 | None | 18900 | 29.5312 | 40204.1562 | 42214.3641 | 0 | 0 | 42214.3641 | 42805.3652
CA1000204 | AMERICAN UNION SCHOOL | FRESNO | 250 | 33 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 53356.8749
CA4200618 | MIDLAND SCHOOL | SANTA BARBARA | 300 | 48 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0.3 | 17044.8272 | 73860.9178 | 74894.9707
CA5500148 | CHINESE CAMP SCHOOL | TUOLUMNE | 35 | 1 | None | 5250 | 8.2031 | 32931.2656 | 34577.8289 | 0 | 0 | 34577.8289 | 35061.9185
CA2400091 | CHARLESTON SCHOOL | MERCED | 325 | 1 | None | 48750 | 76.1719 | 56108.6094 | 58914.0398 | 0 | 0 | 58914.0398 | 59738.8364
CA2400079 | MCSWAIN ELEMENTARY SCHOOL | MERCED | 950 | 24 | None | 142500 | 222.6562 | 106059.7812 | 111362.7703 | 0 | 0 | 111362.7703 | 112921.8491
CA2000611 | COARSEGOLD SCHOOL | MADERA | 441 | 11 | None | 66150 | 103.3594 | 65379.5469 | 68648.5242 | 0 | 0 | 68648.5242 | 69609.6036
CA1300553 | MAGNOLIA UNION SCHOOL | IMPERIAL | 142 | 1 |  | 21300 | 33.2812 | 41482.9062 | 43557.0516 | 0 | 0 | 43557.0516 | 44166.8503
CA1300560 | PINE UNION SCHOOL | IMPERIAL | 217 | 1 | Some | 32550 | 50.8594 | 47477.0469 | 49850.8992 | 0 | 0 | 49850.8992 | 50548.8118
CA5400850 | PACKWOOD SCHOOL | TULARE | 105 | 2 | Some | 15750 | 24.6094 | 38525.7969 | 40452.0867 | 0 | 0 | 40452.0867 | 41018.4159
CA1000193 | NAVELENCIA SCHOOL | FRESNO | 330 | 1 | None | 49500 | 77.3438 | 56508.2188 | 59333.6297 | 0 | 0 | 59333.6297 | 60164.3005
CA3400248 | FRANKLIN ELEMENTARY SCHOOL | SACRAMENTO | 650 | 13 | None | 97500 | 152.3438 | 82083.2188 | 86187.3797 | 0.32 | 27579.9615 | 113767.3412 | 115360.084
CA5200540 | REEDS CREEK SCHOOL | TEHAMA | 196 | 7 | None | 29400 | 45.9375 | 45798.6875 | 48088.6219 | 0 | 0 | 48088.6219 | 48761.8626
CA1000104 | CENTERVILLE SCHOOL | FRESNO | 375 | 11 | None | 56250 | 87.8906 | 60104.7031 | 63109.9383 | 0 | 0 | 63109.9383 | 63993.4774
CA4300779 | LAKESIDE SD-LAKESIDE SCHOOL | SANTA CLARA | 127 | 4 |  | 19050 | 29.7656 | 40284.0781 | 42298.282 | 0.32 | 13535.4502 | 55833.7323 | 56615.4045
CA1503368 | SOUTH FORK MIDDLE SCHOOL | KERN | 204 | 1 |  | 30600 | 47.8125 | 46438.0625 | 48759.9656 | 0 | 0 | 48759.9656 | 49442.6051
CA5400846 | ELBOW SCHOOL | TULARE | 95 | 3 | Some | 14250 | 22.2656 | 37726.5781 | 39612.907 | 0 | 0 | 39612.907 | 40167.4877
CA0400060 | HONCUT ELEMENTARY SCHOOL | BUTTE | 25 | 3 | None | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0 | 0 | 33738.6492 | 34210.9903
CA1000111 | PINE RIDGE SCHOOL | FRESNO | 100 | 13 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 40592.9518
CA5200513 | EVERGREEN UNION SCHOOL DISTRICT | TEHAMA | 1100 | 8 | Some | 165000 | 257.8125 | 118048.0625 | 123950.4656 | 0 | 0 | 123950.4656 | 125685.7721
CA2300874 | MONTESSORI DEL MAR LEARNING CENTER | MENDOCINO | 50 | 3 |  | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 36338.3108
CA5400519 | PALO VERDE SCHOOL | TULARE | 500 | 26 | None | 75000 | 117.1875 | 70094.9375 | 73599.6844 | 0 | 0 | 73599.6844 | 74630.08
CA2300785 | LEGGETT VALLEY SCHOOL | MENDOCINO | 100 | 5 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 40592.9518
CA5800840 | MJUSD CORDUA SCHOOL | YUBA | 110 | 3 | None | 16500 | 25.7812 | 38925.4062 | 40871.6766 | 0 | 0 | 40871.6766 | 41443.88
CA1502068 | DI GIORGIO SCHOOL WATER SYSTEM | KERN | 232 | 1 |  | 34800 | 54.375 | 48675.875 | 51109.6687 | 0 | 0 | 51109.6687 | 51825.2041
CA5403146 | LIBERTY ELEMENTARY SCHOOL | TULARE | 500 | 5 | None | 75000 | 117.1875 | 70094.9375 | 73599.6844 | 0 | 0 | 73599.6844 | 74630.08
CA1000185 | GREAT WESTERN ELEMENTARY SCHOOL | FRESNO | 411 | 1 | None | 61650 | 96.3281 | 62981.8906 | 66130.9852 | 0 | 0 | 66130.9852 | 67056.8189
CA2210909 | MUSD - MARIPOSA JUNIOR HIGH SCHOOL | MARIPOSA | 152 | 20 | None | 22800 | 35.625 | 42282.125 | 44396.2312 | 0 | 0 | 44396.2312 | 45017.7785
CA4500161 | PRAIRIE ELEMENTARY SCHOOL | SHASTA | 375 | 1 |  | 56250 | 87.8906 | 60104.7031 | 63109.9383 | 0 | 0 | 63109.9383 | 63993.4774
CA2400097 | CRESSEY SCHOOL | MERCED | 155 | 7 | None | 23250 | 36.3281 | 42521.8906 | 44647.9852 | 0 | 0 | 44647.9852 | 45273.0569
CA3901325 | RIPON CHRISTIAN SCHOOLS | SAN JOAQUIN | 900 | 1 |  | 135000 | 210.9375 | 102063.6875 | 107166.8719 | 0 | 0 | 107166.8719 | 108667.2081
CA3900757 | LINDEN USD-WATERLOO ELEMENTARY | SAN JOAQUIN | 225 | 1 |  | 33750 | 52.7344 | 48116.4219 | 50522.243 | 0 | 0 | 50522.243 | 51229.5544
CA1000315 | CLAY JOINT ELEMENTARY SCHOOL | FRESNO | 275 | 5 | None | 41250 | 64.4531 | 52112.5156 | 54718.1414 | 0 | 0 | 54718.1414 | 55484.1954
CA5400886 | COLUMBINE SCHOOL | TULARE | 250 | 8 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 53356.8749
CA2400075 | EL NIDO ELEMENTARY SCHOOL | MERCED | 219 | 2 | None | 32850 | 51.3281 | 47636.8906 | 50018.7352 | 0 | 0 | 50018.7352 | 50718.9974
CA1000182 | BURREL UNION ELEMENTARY SCHOOL | FRESNO | 178 | 2 | None | 26700 | 41.7188 | 44360.0938 | 46578.0984 | 0 | 0 | 46578.0984 | 47230.1918
CA5400624 | KINGS RIVER ELEMENTARY SCHOOL | TULARE | 550 | 9 | None | 82500 | 128.9062 | 74091.0312 | 77795.5828 | 0 | 0 | 77795.5828 | 78884.721
CA2210910 | MUSD - WOODLAND ELEMENTARY SCHOOL | MARIPOSA | 446 | 24 | None | 66900 | 104.5312 | 65779.1562 | 69068.1141 | 0 | 0 | 69068.1141 | 70035.0677
CA2400099 | GRACE MENNONITE SCHOOL | MERCED | 100 | 1 |  | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 40592.9518
CA2400113 | SCHELBY SCHOOL | MERCED | 290 | 9 | None | 43500 | 67.9688 | 53311.3438 | 55976.9109 | 0 | 0 | 55976.9109 | 56760.5877
CA1000201 | SUN EMPIRE SCHOOL | FRESNO | 780 | 10 | None | 117000 | 182.8125 | 92473.0625 | 97096.7156 | 0 | 0 | 97096.7156 | 98456.0696
CA1200681 | CUDDEBACK GRAMMAR SCHOOL | HUMBOLDT | 165 | 1 | None | 24750 | 38.6719 | 43321.1094 | 45487.1648 | 0 | 0 | 45487.1648 | 46123.9852
CA1300579 | MCCABE UNION SCHOOL | IMPERIAL | 1350 | 1 | None | 202500 | 316.4062 | 138028.5312 | 144929.9578 | 0 | 0 | 144929.9578 | 146958.9772
CA0500085 | TOYON MIDDLE SCHOOL | CALAVERAS | 200 | 6 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 49102.2339
CA5200507 | BERRENDOS SCHOOL | TEHAMA | 325 | 4 |  | 48750 | 76.1719 | 56108.6094 | 58914.0398 | 0 | 0 | 58914.0398 | 59738.8364
CA5800006 | YES CHARTER ACADEMY | YUBA | 125 | 1 | None | 18750 | 29.2969 | 40124.2344 | 42130.4461 | 0 | 0 | 42130.4461 | 42720.2723
CA3901169 | MUSD-NILE GARDEN SCHOOL | SAN JOAQUIN | 804 | 3 | None | 120600 | 188.4375 | 94391.1875 | 99110.7469 | 0 | 0 | 99110.7469 | 100498.2973
CA5000132 | VALLEY HOME SCHOOL TEXAS | STANISLAUS | 80 | 1 | None | 12000 | 18.75 | 36527.75 | 38354.1375 | 0 | 0 | 38354.1375 | 38891.0954
CA3900848 | LODI USD-TURNER ACADEMY AT TOKAY COLONY | SAN JOAQUIN | 166 | 2 | Some | 24900 | 38.9062 | 43401.0312 | 45571.0828 | 0 | 0 | 45571.0828 | 46209.078
CA4900711 | GRAVENSTEIN SCHOOL DISTRICT-HILLCREST | SONOMA | 289 | 1 | None | 43350 | 67.7344 | 53231.4219 | 55892.993 | 0.3 | 16767.8979 | 72660.8909 | 73678.1433
CA1600015 | KINGS RIVER HARDWICK SCHOOL | KINGS | 908 | 7 | None | 136200 | 212.8125 | 102703.0625 | 107838.2156 | 0 | 0 | 107838.2156 | 109347.9506
CA5400714 | SUNDALE UNION SCHOOL | TULARE | 827 | 11 | None | 124050 | 193.8281 | 96229.3906 | 101040.8602 | 0 | 0 | 101040.8602 | 102455.4322
CA4900704 | ALEXANDER VALLEY UNION SCHOOL DISTRICT | SONOMA | 200 | 5 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.3 | 14527.2881 | 62951.5819 | 63832.904
CA3901014 | BANTA ELEMENTARY SCHOOL | SAN JOAQUIN | 200 | 1 | Some | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 49102.2339
CA5400882 | PLEASANT VIEW WEST SCHOOL | TULARE | 220 | 9 | None | 33000 | 51.5625 | 47716.8125 | 50102.6531 | 0 | 0 | 50102.6531 | 50804.0903
CA5700623 | DAVIS JUSD - FAIRFIELD SCHOOL | YOLO | 65 | 1 | None | 9750 | 15.2344 | 35328.9219 | 37095.368 | 0 | 0 | 37095.368 | 37614.7031
CA5200538 | LASSEN VIEW UNION ELEMENTARY SCHOOL DIST | TEHAMA | 350 | 4 | NULL | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0 | 0 | 61011.9891 | 61866.1569
CA4900716 | CINNABAR ELEMENTARY SCHOOL | SONOMA | 228 | 2 | None | 34200 | 53.4375 | 48356.1875 | 50773.9969 | 0.3 | 15232.1991 | 66006.1959 | 66930.2827
CA5000101 | CHATOM SCHOOL (EH) | STANISLAUS | 500 | 1 | None | 75000 | 117.1875 | 70094.9375 | 73599.6844 | 0 | 0 | 73599.6844 | 74630.08
CA0900304 | SILVERFORK SCHOOL | EL DORADO | 25 | 2 |  | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0.3 | 10121.5948 | 43860.244 | 44474.2874
CA4500183 | BLACK BUTTE ELEMENTARY SCHOOL | SHASTA | 250 | 1 |  | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 53356.8749
CA5403130 | ELEANOR ROOSEVELT COMM LEARNING CTR | TULARE | 295 | 5 | None | 44250 | 69.1406 | 53710.9531 | 56396.5008 | 0 | 0 | 56396.5008 | 57186.0518
CA5304105 | BURNT RANCH SCHOOL | TRINITY | 125 | 2 |  | 18750 | 29.2969 | 40124.2344 | 42130.4461 | 0 | 0 | 42130.4461 | 42720.2723
CA5601405 | SANTA CLARA SCHOOL | VENTURA | 39 | 1 | None | 5850 | 9.1406 | 33250.9531 | 34913.5008 | 0.32 | 11172.3203 | 46085.821 | 46731.0225
CA3901167 | EUSD-VAN ALLEN SCHOOL | SAN JOAQUIN | 200 | 1 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 49102.2339
CA5800845 | MJUSD DOBBINS SCHOOL | YUBA | 85 | 3 | None | 12750 | 19.9219 | 36927.3594 | 38773.7273 | 0 | 0 | 38773.7273 | 39316.5595
CA1600009 | HANFORD CHRISTIAN SCHOOL | KINGS | 175 | 14 | None | 26250 | 41.0156 | 44120.3281 | 46326.3445 | 0 | 0 | 46326.3445 | 46974.9134
CA4500322 | BLACK BUTTE JUNIOR HIGH SCHOOL | SHASTA | 100 | 1 |  | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 40592.9518
CA1100448 | PLAZA ELEMENTARY SCHOOL | GLENN | 250 | 4 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 53356.8749
CA5100172 | ENCINAL ELEMENTARY SCHOOL | SUTTER | 128 | 1 | None | 19200 | 30 | 40364 | 42382.2 | 0 | 0 | 42382.2 | 42975.5508
CA5305107 | SO TRINITY UNIFIED SCHOOL DIST. | TRINITY | 100 | 6 |  | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 40592.9518
CA3900748 | ESCALON USD- COLLEGEVILLE SCH | SAN JOAQUIN | 100 | 1 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 40592.9518
CA4900703 | OAK GROVE SCHOOL | SONOMA | 500 | 7 | None | 75000 | 117.1875 | 70094.9375 | 73599.6844 | 0.3 | 22079.9053 | 95679.5897 | 97019.1039
CA4900907 | SUMMERFIELD WALDORF SCHOOL | SONOMA | 299 | 13 | None | 44850 | 70.0781 | 54030.6406 | 56732.1727 | 0.3 | 17019.6518 | 73751.8245 | 74784.35
CA4700591 | DELPHIC ELEMENTARY SCHOOL | SISKIYOU | 50 | 1 |  | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 36338.3108
CA2000600 | HOWARD ELEMENTARY SCHOOL | MADERA | 1081 | 7 | None | 162150 | 253.3594 | 116529.5469 | 122356.0242 | 0 | 0 | 122356.0242 | 124069.0086
CA4200747 | VISTA DE LAS CRUCES | SANTA BARBARA | 50 | 2 |  | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0.3 | 10750.9795 | 46587.578 | 47239.8041
CA2400134 | BUHACH PRESCHOOL (KINDERCARE) | MERCED | 110 | 3 | None | 16500 | 25.7812 | 38925.4062 | 40871.6766 | 0 | 0 | 40871.6766 | 41443.88
CA2901208 | DONNER TRAIL ELEMENTARY SCHOOL | NEVADA | 60 | 1 |  | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 37189.239
CA2100538 | TOMALES HIGH SCHOOL | MARIN | 227 | 2 | None | 34050 | 53.2031 | 48276.2656 | 50690.0789 | 0.3 | 15207.0237 | 65897.1026 | 66819.662
CA4700577 | BIG SPRINGS UNION ELEM. SCHOOL | SISKIYOU | 95 | 2 | None | 14250 | 22.2656 | 37726.5781 | 39612.907 | 0 | 0 | 39612.907 | 40167.4877
CA3500801 | WILLOW GROVE UNION ELEMENTARY SCHOOL | SAN BENITO | 25 | 4 | None | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0.3 | 10121.5948 | 43860.244 | 44474.2874
CA3400251 | SIERRA ENTERPRISE ELEMENTARY SCHOOL | SACRAMENTO | 430 | 13 | None | 64500 | 100.7812 | 64500.4062 | 67725.4266 | 0.32 | 21672.1365 | 89397.5631 | 90649.1289
CA2900593 | TWIN RIDGES OAK TREE SCHOOL | NEVADA | 120 | 8 |  | 18000 | 28.125 | 39724.625 | 41710.8562 | 0 | 0 | 41710.8562 | 42294.8082
CA1000105 | MADISON ELEMENTARY SCHOOL | FRESNO | 900 | 8 | Some | 135000 | 210.9375 | 102063.6875 | 107166.8719 | 0 | 0 | 107166.8719 | 108667.2081
CA4900679 | FORT ROSS SCHOOL DISTRICT | SONOMA | 100 | 2 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.3 | 12009.7491 | 52042.2459 | 52770.8374
CA4901215 | PLUMFIELD ACADEMY (OCCIDENTAL RD.) | SONOMA | 30 | 1 | None | 4500 | 7.0312 | 32531.6562 | 34158.2391 | 0.3 | 10247.4717 | 44405.7108 | 45027.3907
CA2700577 | ELKHORN SCHOOL WS | MONTEREY | 694 | 1 | None | 104100 | 162.6562 | 85599.7812 | 89879.7703 | 0.3 | 26963.9311 | 116843.7014 | 118479.5132
CA5304209 | JUNCTION CITY SCHOOL | TRINITY | 80 | 2 | None | 12000 | 18.75 | 36527.75 | 38354.1375 | 0 | 0 | 38354.1375 | 38891.0954
CA0900111 | PIONEER ELEMENTARY SCHOOL | EL DORADO | 250 | 19 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0.3 | 15786.0577 | 68406.2498 | 69363.9373
CA0400062 | RICHVALE ELEMENTARY SCHOOL | BUTTE | 63 | 4 | None | 9450 | 14.7656 | 35169.0781 | 36927.532 | 0 | 0 | 36927.532 | 37444.5175
CA2100560 | TOMALES ELEM & MIDDLE SCHOOL | MARIN | 265 | 4 | None | 39750 | 62.1094 | 51313.2969 | 53878.9617 | 0.3 | 16163.6885 | 70042.6502 | 71023.2473
CA3700018 | CAMPO ELEMENTARY SCHOOL | SAN DIEGO | 300 | 3 |  | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0.32 | 18181.149 | 74997.2396 | 76047.201
CA1502260 | SOUTH FORK ELEMENTARY SCHOOL WATER SYS | KERN | 154 | 2 |  | 23100 | 36.0938 | 42441.9688 | 44564.0672 | 0 | 0 | 44564.0672 | 45187.9641
CA5800843 | MJUSD FOOTHILL INTERMEDIATE SCHOOL | YUBA | 325 | 2 | None | 48750 | 76.1719 | 56108.6094 | 58914.0398 | 0 | 0 | 58914.0398 | 59738.8364
CA3901163 | MUSD-NEW HAVEN SCHOOL | SAN JOAQUIN | 300 | 3 | Some | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0 | 0 | 56816.0906 | 57611.5159
CA2700705 | PRUNEDALE SCHOOL WS | MONTEREY | 655 | 1 | None | 98250 | 153.5156 | 82482.8281 | 86606.9695 | 0.3 | 25982.0909 | 112589.0604 | 114165.3072
CA2700552 | ECHO VALLEY SCHOOL WS | MONTEREY | 579 | 1 | None | 86850 | 135.7031 | 76408.7656 | 80229.2039 | 0.3 | 24068.7612 | 104297.9651 | 105758.1366
CA3500905 | ANZAR HIGH SCHOOL | SAN BENITO | 328 | 9 | None | 49200 | 76.875 | 56348.375 | 59165.7937 | 0.3 | 17749.7381 | 76915.5319 | 77992.3493
CA4500181 | WHITMORE UNION ELEM SCHOOL | SHASTA | 35 | 2 | None | 5250 | 8.2031 | 32931.2656 | 34577.8289 | 0 | 0 | 34577.8289 | 35061.9185
CA0400068 | BERRY CREEK SCHOOL | BUTTE | 95 | 6 | None | 14250 | 22.2656 | 37726.5781 | 39612.907 | 0 | 0 | 39612.907 | 40167.4877
CA5200565 | RICHFIELD ELEMENTARY SCHOOL | TEHAMA | 280 | 9 | None | 42000 | 65.625 | 52512.125 | 55137.7312 | 0 | 0 | 55137.7312 | 55909.6595
CA2800848 | NVUSD: MT. GEORGE SCHOOL | NAPA | 100 | 1 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.3 | 12009.7491 | 52042.2459 | 52770.8374
CA4700582 | GAZELLE SCHOOL | SISKIYOU | 60 | 1 |  | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 37189.239
CA1100104 | WILLOW CREEK CHRISTIAN SCHOOL | GLENN | 47 | 2 |  | 7050 | 11.0156 | 33890.3281 | 35584.8445 | 0 | 0 | 35584.8445 | 36083.0324
CA5500152 | CURTIS CREEK ELEMENTARY SCHOOL | TUOLUMNE | 546 | 1 |  | 81900 | 127.9688 | 73771.3438 | 77459.9109 | 0 | 0 | 77459.9109 | 78544.3497
CA2701221 | WASHINGTON SCHOOL WS | MONTEREY | 250 | 2 |  | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0.3 | 15786.0577 | 68406.2498 | 69363.9373
CA1000367 | SELMA HIGH SCHOOL | FRESNO | 2225 | 21 | None | 333750 | 521.4844 | 207960.1719 | 218358.1805 | 0 | 0 | 218358.1805 | 221415.195
CA4900694 | WRIGHT ELEMENTARY SCHOOL | SONOMA | 500 | 11 |  | 75000 | 117.1875 | 70094.9375 | 73599.6844 | 0.3 | 22079.9053 | 95679.5897 | 97019.1039
CA2000846 | SIERRA VIEW SCHOOL | MADERA | 250 | 23 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 53356.8749
CA2000616 | WASUMA SCHOOL | MADERA | 354 | 5 |  | 53100 | 82.9688 | 58426.3438 | 61347.6609 | 0 | 0 | 61347.6609 | 62206.5282
CA5000568 | GREGORI HIGH SCHOOL | STANISLAUS | 2000 | 9 | None | 300000 | 468.75 | 189977.75 | 199476.6375 | 0 | 0 | 199476.6375 | 202269.3104
CA1300554 | MEADOWS UNION ELEMENTARY SCHOOL | IMPERIAL | 550 | 6 | None | 82500 | 128.9062 | 74091.0312 | 77795.5828 | 0 | 0 | 77795.5828 | 78884.721
CA4900699 | OLIVET ELEMENTARY SCHOOL | SONOMA | 400 | 6 | None | 60000 | 93.75 | 62102.75 | 65207.8875 | 0.3 | 19562.3662 | 84770.2538 | 85957.0373
CA2000844 | RIVERGOLD ELEMENTARY SCHOOL | MADERA | 485 | 9 | None | 72750 | 113.6719 | 68896.1094 | 72340.9148 | 0 | 0 | 72340.9148 | 73353.6877
CA0202501 | DIAMOND VALLEY SCHOOL | ALPINE | 100 | 5 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 40592.9518
CA1502154 | LAKESIDE SCHOOL | KERN | 800 | 1 | None | 120000 | 187.5 | 94071.5 | 98775.075 | 0 | 0 | 98775.075 | 100157.926
CA4200833 | BONITA SCHOOL | SANTA BARBARA | 589 | 1 |  | 88350 | 138.0469 | 77207.9844 | 81068.3836 | 0.3 | 24320.5151 | 105388.8987 | 106864.3433
CA5602406 | RIO SCHOOL DIST/RIO DEL VALLE SCHOOL | VENTURA | 820 | 1 | None | 123000 | 192.1875 | 95669.9375 | 100453.4344 | 0.32 | 32145.099 | 132598.5334 | 134454.9128
CA4900705 | GEYSERVILLE NEWTECH ACADEMY | SONOMA | 200 | 1 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.3 | 14527.2881 | 62951.5819 | 63832.904
CA1400019 | ROUND VALLEY SCHOOL | INYO | 143 | 2 | None | 21450 | 33.5156 | 41562.8281 | 43640.9695 | 0 | 0 | 43640.9695 | 44251.9431
CA4200879 | CUYAMA ELEMENTARY SCHOOL | SANTA BARBARA | 250 | 1 |  | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0.3 | 15786.0577 | 68406.2498 | 69363.9373
CA5400636 | OROSI HIGH SCHOOL | TULARE | 1200 | 8 | None | 180000 | 281.25 | 126040.25 | 132342.2625 | 0 | 0 | 132342.2625 | 134195.0542
CA0400067 | FEATHER RIVER SCHOOL | BUTTE | 25 | 2 | None | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0 | 0 | 33738.6492 | 34210.9903
CA5400844 | ELBOW CREEK SCHOOL | TULARE | 530 | 11 | Some | 79500 | 124.2188 | 72492.5938 | 76117.2234 | 0 | 0 | 76117.2234 | 77182.8646
CA2000598 | ALVIEW SCHOOL | MADERA | 200 | 1 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 49102.2339
CA2300755 | POTTER VALLEY SCHOOL DISTRICT | MENDOCINO | 309 | 36 | None | 46350 | 72.4219 | 54829.8594 | 57571.3523 | 0 | 0 | 57571.3523 | 58377.3513
CA3901090 | NORTH VALLEY SCHOOL PWS | SAN JOAQUIN | 35 | 1 | Some | 5250 | 8.2031 | 32931.2656 | 34577.8289 | 0 | 0 | 34577.8289 | 35061.9185
CA3900850 | LODI USD-HOUSTON SCHOOL | SAN JOAQUIN | 405 | 4 | Some | 60750 | 94.9219 | 62502.3594 | 65627.4773 | 0 | 0 | 65627.4773 | 66546.262
CA3901085 | LODI USD-DAVIS SCHOOL | SAN JOAQUIN | 630 | 1 | Some | 94500 | 147.6562 | 80484.7812 | 84509.0203 | 0 | 0 | 84509.0203 | 85692.1466
CA1100749 | RIVER VALLEY CHRISTIAN SCHOOL | GLENN | 80 | 2 |  | 12000 | 18.75 | 36527.75 | 38354.1375 | 0 | 0 | 38354.1375 | 38891.0954
CA4900710 | TWIN HILLS SCHOOL DIST-APPLE BLOSSOM SCH | SONOMA | 400 | 1 | None | 60000 | 93.75 | 62102.75 | 65207.8875 | 0.3 | 19562.3662 | 84770.2538 | 85957.0373
CA4000774 | PLEASANT VALLEY ELEMENTARY | SAN LUIS OBISPO | 100 | 1 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.3 | 12009.7491 | 52042.2459 | 52770.8374
CA1100527 | CAPAY JOINT UNION ELEM. SCHOOL | GLENN | 230 | 1 |  | 34500 | 53.9062 | 48516.0312 | 50941.8328 | 0 | 0 | 50941.8328 | 51655.0185
CA2400064 | MERQUIN ELEMENTARY SCHOOL | MERCED | 284 | 2 | None | 42600 | 66.5625 | 52831.8125 | 55473.4031 | 0 | 0 | 55473.4031 | 56250.0308
CA2400071 | WASHINGTON SCHOOL | MERCED | 230 | 4 | None | 34500 | 53.9062 | 48516.0312 | 50941.8328 | 0 | 0 | 50941.8328 | 51655.0185
CA0400073 | NORD COUNTRY SCHOOL | BUTTE | 66 | 5 | None | 9900 | 15.4688 | 35408.8438 | 37179.2859 | 0 | 0 | 37179.2859 | 37699.7959
CA3301308 | COTTONWOOD SCHOOL | RIVERSIDE | 312 | 7 | None | 46800 | 73.125 | 55069.625 | 57823.1062 | 0.32 | 18503.394 | 76326.5002 | 77395.0713
CA2702254 | PACIFIC VALLEY SCHOOL WS | MONTEREY | 25 | 5 | NULL | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0.3 | 10121.5948 | 43860.244 | 44474.2874
CA2400219 | MERCED NEW LIFE SCHOOL | MERCED | 36 | 2 |  | 5400 | 8.4375 | 33011.1875 | 34661.7469 | 0 | 0 | 34661.7469 | 35147.0113
CA3107342 | LINCOLN HIGH SCHOOL FARM | PLACER | 50 | 1 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 36338.3108
CA2300584 | MENDOCINO SCHOOL DISTRICT- MENDOCINO | MENDOCINO | 768 | 15 | None | 115200 | 180 | 91514 | 96089.7 | 0 | 0 | 96089.7 | 97434.9558
CA5200506 | PLUM VALLEY ELEM SCHOOL (NEW SCHOOL) | TEHAMA | 70 | 1 |  | 10500 | 16.4062 | 35728.5312 | 37514.9578 | 0 | 0 | 37514.9578 | 38040.1672
CA4901168 | SALMON CREEK MIDDLE SCHOOL | SONOMA | 300 | 14 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0.3 | 17044.8272 | 73860.9178 | 74894.9707
CA4000767 | SANTA LUCIA SCHOOL | SAN LUIS OBISPO | 52 | 1 | None | 7800 | 12.1875 | 34289.9375 | 36004.4344 | 0.3 | 10801.3303 | 46805.7647 | 47461.0454
CA1000186 | HELM SCHOOL | FRESNO | 146 | 11 | None | 21900 | 34.2188 | 41802.5938 | 43892.7234 | 0 | 0 | 43892.7234 | 44507.2216
CA2100582 | NICASIO SCHOOL | MARIN | 40 | 5 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0.3 | 10499.2256 | 45496.6444 | 46133.5974
CA5602407 | RIO MESA HIGH SCHOOL/OXNARD UHS | VENTURA | 2600 | 13 | None | 390000 | 609.375 | 237930.875 | 249827.4188 | 0.32 | 79944.774 | 329772.1927 | 334389.0034
CA4400875 | SANTA CRUZ WALDORF SCHOOL | SANTA CRUZ | 190 | 2 | None | 28500 | 44.5312 | 45319.1562 | 47585.1141 | 0.3 | 14275.5342 | 61860.6483 | 62726.6974
CA5402008 | HOT SPRINGS SCHOOL | TULARE | 42 | 1 | None | 6300 | 9.8438 | 33490.7188 | 35165.2547 | 0 | 0 | 35165.2547 | 35657.5683
CA2210908 | MUSD -COULTERVILLE - GREELEY HILL SCHOOL | MARIPOSA | 91 | 6 | None | 13650 | 21.3281 | 37406.8906 | 39277.2352 | 0 | 0 | 39277.2352 | 39827.1164
CA1000180 | ALTA ELEMENTARY SCHOOL | FRESNO | 384 | 1 | None | 57600 | 90 | 60824 | 63865.2 | 0 | 0 | 63865.2 | 64759.3128
CA0105009 | MOUNTAIN HOUSE SCHOOL | ALAMEDA | 50 | 1 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0.3 | 10750.9795 | 46587.578 | 47239.8041
CA2300846 | MENDOCINO SCHOOL DISTRICT-ALBION SCHOOL | MENDOCINO | 25 | 2 |  | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0 | 0 | 33738.6492 | 34210.9903
CA2000612 | NORTH FORK ELEMENTARY SCHOOL | MADERA | 500 | 18 |  | 75000 | 117.1875 | 70094.9375 | 73599.6844 | 0 | 0 | 73599.6844 | 74630.08
CA5100143 | PLEASANT GROVE ELEM. SCHOOL | SUTTER | 185 | 1 | None | 27750 | 43.3594 | 44919.5469 | 47165.5242 | 0 | 0 | 47165.5242 | 47825.8416
CA5000155 | ROBERTS FERRY SCHOOL CAFETERIA | STANISLAUS | 100 | 2 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 40592.9518
CA4900693 | BELLEVUE UNION SCH DIST-BELLEVUE SCHOOL | SONOMA | 591 | 2 | None | 88650 | 138.5156 | 77367.8281 | 81236.2195 | 0.3 | 24370.8659 | 105607.0854 | 107085.5846
CA5000255 | MOUNTAIN VIEW ELEMENTARY SCHOOL | STANISLAUS | 364 | 1 | None | 54600 | 85.3125 | 59225.5625 | 62186.8406 | 0 | 0 | 62186.8406 | 63057.4564
CA1800577 | JANESVILLE ELEMENTARY SCHOOL | LASSEN | 425 | 1 | None | 63750 | 99.6094 | 64100.7969 | 67305.8367 | 0 | 0 | 67305.8367 | 68248.1184
CA1600017 | ISLAND UNION SCHOOL | KINGS | 416 | 17 | None | 62400 | 97.5 | 63381.5 | 66550.575 | 0 | 0 | 66550.575 | 67482.283
CA5700509 | CLARKSBURG MIDDLE SCHOOL | YOLO | 460 | 3 | None | 69000 | 107.8125 | 66898.0625 | 70242.9656 | 0 | 0 | 70242.9656 | 71226.3671
CA5000133 | HART- RANSOM UNION SCHOOL & DISTRICT | STANISLAUS | 650 | 4 | None | 97500 | 152.3438 | 82083.2188 | 86187.3797 | 0 | 0 | 86187.3797 | 87394.003
CA5100141 | MERIDIAN ELEMENTARY SCHOOL | SUTTER | 100 | 1 |  | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 40592.9518
CA1000476 | FOOTHILL ELEMENTARY SCHOOL | FRESNO | 900 | 12 |  | 135000 | 210.9375 | 102063.6875 | 107166.8719 | 0 | 0 | 107166.8719 | 108667.2081
CA1000181 | ALVINA SCHOOL | FRESNO | 240 | 8 | None | 36000 | 56.25 | 49315.25 | 51781.0125 | 0 | 0 | 51781.0125 | 52505.9467
CA3901209 | ST MARYS HIGH SCHOOL | SAN JOAQUIN | 950 | 11 | Some | 142500 | 222.6562 | 106059.7812 | 111362.7703 | 0 | 0 | 111362.7703 | 112921.8491
CA3900849 | LODI USD-LIVE OAK SCHOOL | SAN JOAQUIN | 100 | 1 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 40592.9518
CA2800970 | HOWELL MOUNTAIN SCHOOL | NAPA | 100 | 2 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.3 | 12009.7491 | 52042.2459 | 52770.8374
CA5000249 | STANISLAUS UNION SCHOOL DIST | STANISLAUS | 390 | 1 | None | 58500 | 91.4062 | 61303.5312 | 64368.7078 | 0 | 0 | 64368.7078 | 65269.8697
CA1000198 | TERRY SCHOOL | FRESNO | 236 | 25 | None | 35400 | 55.3125 | 48995.5625 | 51445.3406 | 0 | 0 | 51445.3406 | 52165.5754
CA4900708 | GRAVENSTEIN SCHOOL DISTRICT-GRAVENSTEIN | SONOMA | 398 | 7 |  | 59700 | 93.2812 | 61942.9062 | 65040.0516 | 0.3 | 19512.0155 | 84552.067 | 85735.796
CA4300593 | MORGAN HILL USD-MACHADO SCHOOL | SANTA CLARA | 60 | 1 | None | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0.32 | 11736.249 | 48412.0271 | 49089.7955
CA4700559 | BUTTEVILLE UNION SCHOOL | SISKIYOU | 165 | 2 |  | 24750 | 38.6719 | 43321.1094 | 45487.1648 | 0 | 0 | 45487.1648 | 46123.9852
CA5400972 | OUTSIDE CREEK SCHOOL | TULARE | 125 | 2 | None | 18750 | 29.2969 | 40124.2344 | 42130.4461 | 0 | 0 | 42130.4461 | 42720.2723
CA5100140 | MARCUM ILLINOIS ELEMENTARY SCHOOL | SUTTER | 185 | 7 | None | 27750 | 43.3594 | 44919.5469 | 47165.5242 | 0 | 0 | 47165.5242 | 47825.8416
CA1200817 | KNEELAND SCHOOL | HUMBOLDT | 32 | 1 | None | 4800 | 7.5 | 32691.5 | 34326.075 | 0 | 0 | 34326.075 | 34806.6401
CA1000192 | MONROE SCHOOL | FRESNO | 200 | 3 |  | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 49102.2339
CA5200519 | GERBER UNION ELEMENTARY SCHOOL DISTRICT | TEHAMA | 625 | 1 |  | 93750 | 146.4844 | 80085.1719 | 84089.4305 | 0 | 0 | 84089.4305 | 85266.6825
CA2400122 | LONGVIEW MENNONITE SCHOOL | MERCED | 120 | 1 |  | 18000 | 28.125 | 39724.625 | 41710.8562 | 0 | 0 | 41710.8562 | 42294.8082
CA1600011 | PIONEER ELEMENTARY SCHOOL | KINGS | 750 | 6 | Some | 112500 | 175.7812 | 90075.4062 | 94579.1766 | 0 | 0 | 94579.1766 | 95903.285
CA2300826 | MANCHESTER UNION ELEMENTARY SCHOOL | MENDOCINO | 75 | 1 |  | 11250 | 17.5781 | 36128.1406 | 37934.5477 | 0 | 0 | 37934.5477 | 38465.6313
CA3701005 | SPENCER VALLEY SCHOOL DISTRICT | SAN DIEGO | 40 | 4 | None | 6000 | 9.375 | 33330.875 | 34997.4187 | 0.32 | 11199.174 | 46196.5928 | 46843.345
CA0706028 | KNIGHTSEN ELEMENTARY SCHOOL | CONTRA COSTA | 350 | 4 | NULL | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0.3 | 18303.5967 | 79315.5858 | 80426.004
CA3900846 | OAK VIEW UNION ELEMENTARY SCH | SAN JOAQUIN | 350 | 1 | None | 52500 | 82.0312 | 58106.6562 | 61011.9891 | 0 | 0 | 61011.9891 | 61866.1569
CA1000194 | PACIFIC UNION ELEMENTARY SCHOOL | FRESNO | 490 | 1 | None | 73500 | 114.8438 | 69295.7188 | 72760.5047 | 0 | 0 | 72760.5047 | 73779.1518
CA5100138 | BROWNS ELEMENTARY SCHOOL | SUTTER | 160 | 1 | None | 24000 | 37.5 | 42921.5 | 45067.575 | 0 | 0 | 45067.575 | 45698.5211
CA2400062 | SNELLING MERCED FALLS SCHOOL | MERCED | 85 | 4 | None | 12750 | 19.9219 | 36927.3594 | 38773.7273 | 0 | 0 | 38773.7273 | 39316.5595
CA1502607 | PIUTE MOUNTAIN SCHOOL WATER | KERN | 50 | 5 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 36338.3108
CA1900750 | DEL SUR SCHOOL/WESTSIDE UNION DISTRICT | LOS ANGELES | 825 | 1 |  | 123750 | 193.3594 | 96069.5469 | 100873.0242 | 0.32 | 32279.3678 | 133152.392 | 135016.5255
CA4500041 | ANDERSON UNION HIGH SCHOOL | SHASTA | 700 | 2 |  | 105000 | 164.0625 | 86079.3125 | 90383.2781 | 0 | 0 | 90383.2781 | 91648.644
CA4300721 | LOMA PRIETA JUSD-LOMA PRIETA SCHOOL | SANTA CLARA | 560 | 8 | Some | 84000 | 131.25 | 74890.25 | 78634.7625 | 0.32 | 25163.124 | 103797.8865 | 105251.0569
CA1000196 | RIVERVIEW SCHOOL | FRESNO | 469 | 1 | None | 70350 | 109.9219 | 67617.3594 | 70998.2273 | 0 | 0 | 70998.2273 | 71992.2025
CA3100083 | OPHIR ELEMENTARY SCHOOL WATER SYSTEM | PLACER | 260 | 1 |  | 39000 | 60.9375 | 50913.6875 | 53459.3719 | 0 | 0 | 53459.3719 | 54207.8031
CA3901331 | RIPON USD-COLONY OAK SCHOOL | SAN JOAQUIN | 100 | 1 | Some | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 40592.9518
CA1000184 | DUNLAP K-8 SCHOOL | FRESNO | 408 | 1 | None | 61200 | 95.625 | 62742.125 | 65879.2312 | 0 | 0 | 65879.2312 | 66801.5405
CA1900707 | ILEAD AGUA DULCE CHARTER SCHOOL | LOS ANGELES | 450 | 6 |  | 67500 | 105.4688 | 66098.8438 | 69403.7859 | 0.32 | 22209.2115 | 91612.9974 | 92895.5794
CA5500242 | SIERRA WALDORF SCHOOL | TUOLUMNE | 132 | 17 | None | 19800 | 30.9375 | 40683.6875 | 42717.8719 | 0 | 0 | 42717.8719 | 43315.9221
CA2900535 | PLEASANT RIDGE SCHOOL | NEVADA | 120 | 4 |  | 18000 | 28.125 | 39724.625 | 41710.8562 | 0 | 0 | 41710.8562 | 42294.8082
CA3400391 | BRADSHAW CHRISTIAN SCHOOL | SACRAMENTO | 935 | 8 | NULL | 140250 | 219.1406 | 104860.9531 | 110104.0008 | 0.32 | 35233.2803 | 145337.281 | 147372.003
CA1200778 | BRIDGEVILLE ELEM. SCHOOL | HUMBOLDT | 50 | 1 | None | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 36338.3108
CA2000601 | LA VINA SCHOOL | MADERA | 513 | 7 | None | 76950 | 120.2344 | 71133.9219 | 74690.618 | 0 | 0 | 74690.618 | 75736.2866
CA4400758 | RENAISSANCE HIGH SCHOOL | SANTA CRUZ | 250 | 2 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0.3 | 15786.0577 | 68406.2498 | 69363.9373
CA5000295 | SHILOH SCHOOL DISTRICT | STANISLAUS | 105 | 7 | None | 15750 | 24.6094 | 38525.7969 | 40452.0867 | 0 | 0 | 40452.0867 | 41018.4159
CA4400756 | MOUNTAIN ELEMENTARY SCHOOL | SANTA CRUZ | 250 | 1 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0.3 | 15786.0577 | 68406.2498 | 69363.9373
CA3600790 | NEWBERRY ELEMENTARY SCHOOL | SAN BERNARDINO | 255 | 2 |  | 38250 | 59.7656 | 50514.0781 | 53039.782 | 0.3 | 15911.9346 | 68951.7166 | 69917.0407
CA3400273 | WILTON BIBLE CHURCH | SACRAMENTO | 125 | 5 | None | 18750 | 29.2969 | 40124.2344 | 42130.4461 | 0.32 | 13481.7427 | 55612.1888 | 56390.7595
CA5100149 | BARRY ELEMENTARY SCHOOL | SUTTER | 650 | 1 | None | 97500 | 152.3438 | 82083.2188 | 86187.3797 | 0 | 0 | 86187.3797 | 87394.003
CA2900578 | TWIN RIDGES GRIZZLY HILL SCHOOL | NEVADA | 125 | 11 |  | 18750 | 29.2969 | 40124.2344 | 42130.4461 | 0 | 0 | 42130.4461 | 42720.2723
CA2210907 | MUSD - SIERRA FOOTHILL CHARTER SCHOOL | MARIPOSA | 157 | 9 | None | 23550 | 36.7969 | 42681.7344 | 44815.8211 | 0 | 0 | 44815.8211 | 45443.2426
CA5400713 | OAK VALLEY SCHOOL | TULARE | 652 | 10 | None | 97800 | 152.8125 | 82243.0625 | 86355.2156 | 0 | 0 | 86355.2156 | 87564.1886
CA1000190 | LONE STAR SCHOOL | FRESNO | 436 | 6 | None | 65400 | 102.1875 | 64979.9375 | 68228.9344 | 0 | 0 | 68228.9344 | 69184.1395
CA5400994 | HOPE ELEMENTARY SCHOOL | TULARE | 275 | 7 | None | 41250 | 64.4531 | 52112.5156 | 54718.1414 | 0 | 0 | 54718.1414 | 55484.1954
CA4901436 | SEBASTOPOL CHARTER SCHOOL | SONOMA | 360 | 1 | None | 54000 | 84.375 | 58905.875 | 61851.1687 | 0.3 | 18555.3506 | 80406.5194 | 81532.2106
CA5400795 | WAUKENA ELEMENTARY SCHOOL | TULARE | 255 | 7 | None | 38250 | 59.7656 | 50514.0781 | 53039.782 | 0 | 0 | 53039.782 | 53782.339
CA3400250 | PLEASANT GROVE ELEMENTARY SCHOOL | SACRAMENTO | 185 | 10 | None | 27750 | 43.3594 | 44919.5469 | 47165.5242 | 0.32 | 15092.9677 | 62258.492 | 63130.1109
CA4901190 | LIETO WATER SYSTEM (REACH CHARTR SCHOOL) | SONOMA | 134 | 2 |  | 20100 | 31.4062 | 40843.5312 | 42885.7078 | 0.3 | 12865.7123 | 55751.4202 | 56531.94
CA3700963 | POTRERO ELEMENTARY SCHOOL | SAN DIEGO | 300 | 19 |  | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0.32 | 18181.149 | 74997.2396 | 76047.201
CA1502221 | POND SCHOOL WATER SYSTEM | KERN | 250 | 2 |  | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 53356.8749
CA1600013 | LAKESIDE ELEMENTARY SCHOOL | KINGS | 388 | 5 | None | 58200 | 90.9375 | 61143.6875 | 64200.8719 | 0 | 0 | 64200.8719 | 65099.6841
CA4900739 | DUNHAM SCHOOL | SONOMA | 200 | 2 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.3 | 14527.2881 | 62951.5819 | 63832.904
CA5200518 | FLOURNOY SCHOOL | TEHAMA | 32 | 2 | None | 4800 | 7.5 | 32691.5 | 34326.075 | 0 | 0 | 34326.075 | 34806.6401
CA1000577 | DUNLAP LEADERSHIP ACADEMY | FRESNO | 78 | 1 | None | 11700 | 18.2812 | 36367.9062 | 38186.3016 | 0 | 0 | 38186.3016 | 38720.9098
CA4500163 | JUNCTION SCHOOL DISTRICT | SHASTA | 700 | 2 |  | 105000 | 164.0625 | 86079.3125 | 90383.2781 | 0 | 0 | 90383.2781 | 91648.644
CA4500180 | MILLVILLE ELEMENTARY SCHOOL | SHASTA | 110 | 2 | NULL | 16500 | 25.7812 | 38925.4062 | 40871.6766 | 0 | 0 | 40871.6766 | 41443.88
CA2900587 | MOUNTAIN VALLEY CHILD AND FAMILY SERVICE | NEVADA | 50 | 10 | NULL | 7500 | 11.7188 | 34130.0938 | 35836.5984 | 0 | 0 | 35836.5984 | 36338.3108
CA2000597 | DAIRYLAND SCHOOL | MADERA | 250 | 8 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 53356.8749
CA0400064 | CONCOW ELEMENTARY SCHOOL | BUTTE | 115 | 11 | None | 17250 | 26.9531 | 39325.0156 | 41291.2664 | 0 | 0 | 41291.2664 | 41869.3441
CA5400709 | SEQUOIA UNION ELEMENTARY SCHOOL | TULARE | 400 | 26 | None | 60000 | 93.75 | 62102.75 | 65207.8875 | 0 | 0 | 65207.8875 | 66120.7979
CA3301309 | HAMILTON SCHOOL | RIVERSIDE | 958 | 20 | None | 143700 | 224.5312 | 106699.1562 | 112034.1141 | 0.32 | 35850.9165 | 147885.0306 | 149955.421
CA1000316 | KINGS CANYON HIGH SCHOOL | FRESNO | 120 | 1 | None | 18000 | 28.125 | 39724.625 | 41710.8562 | 0 | 0 | 41710.8562 | 42294.8082
CA5000277 | VALLEY HOME SCHOOL PIONEER | STANISLAUS | 26 | 1 | None | 3900 | 6.0938 | 32211.9688 | 33822.5672 | 0 | 0 | 33822.5672 | 34296.0831
CA1900886 | HUGHES-ELIZABETH LAKE UNIFIED SCHOOL DIS | LOS ANGELES | 550 | 2 |  | 82500 | 128.9062 | 74091.0312 | 77795.5828 | 0.32 | 24894.5865 | 102690.1693 | 104127.8317
CA4500214 | WEST VALLEY HIGH SCHOOL | SHASTA | 850 | 1 |  | 127500 | 199.2188 | 98067.5938 | 102970.9734 | 0 | 0 | 102970.9734 | 104412.5671
CA5400711 | SIERRA VIEW JR ACADEMY | TULARE | 104 | 5 | None | 15600 | 24.375 | 38445.875 | 40368.1687 | 0 | 0 | 40368.1687 | 40933.3231
CA4500190 | OAK RUN ELEMENTARY SCHOOL | SHASTA | 125 | 1 | None | 18750 | 29.2969 | 40124.2344 | 42130.4461 | 0 | 0 | 42130.4461 | 42720.2723
CA3901107 | JEFFERSON ESD-JEFFERSON SCHOOL | SAN JOAQUIN | 60 | 1 | Some | 9000 | 14.0625 | 34929.3125 | 36675.7781 | 0 | 0 | 36675.7781 | 37189.239
CA5000584 | MESA ELEMENTARY SCHOOL | STANISLAUS | 860 | 5 |  | 129000 | 201.5625 | 98866.8125 | 103810.1531 | 0 | 0 | 103810.1531 | 105263.4953
CA2702317 | MISSION SCHOOL WS | MONTEREY | 100 | 1 |  | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.3 | 12009.7491 | 52042.2459 | 52770.8374
CA4500162 | INDIAN SPRINGS SCHOOL | SHASTA | 25 | 1 | None | 3750 | 5.8594 | 32132.0469 | 33738.6492 | 0 | 0 | 33738.6492 | 34210.9903
CA2000567 | YOSEMITE HIGH SCHOOL | MADERA | 862 | 32 | None | 129300 | 202.0312 | 99026.6562 | 103977.9891 | 0 | 0 | 103977.9891 | 105433.6809
CA3200215 | SCHRAMEL WATER SYSTEM | PLUMAS | 100 | 1 |  | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 40592.9518
CA5400884 | ROCKFORD SCHOOL | TULARE | 285 | 4 | None | 42750 | 66.7969 | 52911.7344 | 55557.3211 | 0 | 0 | 55557.3211 | 56335.1236
CA5700510 | DELTA HIGH SCHOOL | YOLO | 250 | 7 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 53356.8749
CA2700964 | BRADLEY UNION SCHOOL WS | MONTEREY | 100 | 1 | None | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0.3 | 12009.7491 | 52042.2459 | 52770.8374
CA2702180 | GRAVES SCHOOL WS | MONTEREY | 56 | 2 |  | 8400 | 13.125 | 34609.625 | 36340.1062 | 0.3 | 10902.0319 | 47242.1381 | 47903.5281
CA3700118 | CAMP LOCKETT MIDDLE SCHOOL | SAN DIEGO | 150 | 4 |  | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0.32 | 14153.0865 | 58381.4818 | 59198.8226
CA3702364 | CLOVER FLAT ELEMENTARY SCHOOL | SAN DIEGO | 160 | 5 |  | 24000 | 37.5 | 42921.5 | 45067.575 | 0.32 | 14421.624 | 59489.199 | 60322.0478
CA4700585 | JUNCTION ELEMENTARY SCHOOL | SISKIYOU | 40 | 1 |  | 6000 | 9.375 | 33330.875 | 34997.4187 | 0 | 0 | 34997.4187 | 35487.3826
CA2000602 | RIPPERDAN COMMUNITY DAY SCHOOL | MADERA | 113 | 4 | None | 16950 | 26.4844 | 39165.1719 | 41123.4305 | 0 | 0 | 41123.4305 | 41699.1585
CA2600570 | COLEVILLE HIGH SCHOOL | MONO | 216 | 4 | None | 32400 | 50.625 | 47397.125 | 49766.9812 | 0 | 0 | 49766.9812 | 50463.719
CA4700569 | WILLOW CREEK SCHOOL | SISKIYOU | 100 | 1 |  | 15000 | 23.4375 | 38126.1875 | 40032.4969 | 0 | 0 | 40032.4969 | 40592.9518
CA3701010 | WARNER UNIFIED SCHOOL DISTRICT | SAN DIEGO | 250 | 15 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0.32 | 16838.4615 | 69458.6537 | 70431.0748
CA3400268 | WALNUT GROVE ELEMENTARY SCHOOL | SACRAMENTO | 200 | 2 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.32 | 15495.774 | 63920.0678 | 64814.9487
CA2000607 | SPRING VALLEY SCHOOL | MADERA | 150 | 10 |  | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 44847.5928
CA3500571 | SAN BENITO HIGH SCHOOL | SAN BENITO | 3310 | 61 | None | 496500 | 775.7812 | 294675.4062 | 309409.1766 | 0.3 | 92822.753 | 402231.9295 | 407863.1765
CA0900309 | MOUNTAIN CREEK SCHOOL | EL DORADO | 125 | 8 | None | 18750 | 29.2969 | 40124.2344 | 42130.4461 | 0.3 | 12639.1338 | 54769.5799 | 55536.354
CA3500521 | SOUTHSIDE ELEMENTARY SCHOOL | SAN BENITO | 300 | 2 | None | 45000 | 70.3125 | 54110.5625 | 56816.0906 | 0.3 | 17044.8272 | 73860.9178 | 74894.9707
CA4900695 | NORTHWEST PREP | SONOMA | 325 | 1 | None | 48750 | 76.1719 | 56108.6094 | 58914.0398 | 0.3 | 17674.212 | 76588.2518 | 77660.4873
CA5400704 | THREE RIVERS ELEMENTARY SCHOOL | TULARE | 180 | 6 | None | 27000 | 42.1875 | 44519.9375 | 46745.9344 | 0 | 0 | 46745.9344 | 47400.3775
CA4000732 | CARRISA PLAINS ELEMENTARY | SAN LUIS OBISPO | 65 | 1 |  | 9750 | 15.2344 | 35328.9219 | 37095.368 | 0.3 | 11128.6104 | 48223.9784 | 48899.1141
CA1100440 | LAKE ELEMENTARY SCHOOL | GLENN | 205 | 1 |  | 30750 | 48.0469 | 46517.9844 | 48843.8836 | 0 | 0 | 48843.8836 | 49527.698
CA2000150 | LIBERTY HIGH SCHOOL | MADERA | 1340 | 1 | Some | 201000 | 314.0625 | 137229.3125 | 144090.7781 | 0 | 0 | 144090.7781 | 146108.049
CA3700117 | MOUNTAIN EMPIRE HIGH SCHOOL | SAN DIEGO | 1000 | 12 |  | 150000 | 234.375 | 110055.875 | 115558.6687 | 0.32 | 36978.774 | 152537.4427 | 154672.9669
CA5400558 | SAUCELITO ELEMENTARY SCHOOL | TULARE | 91 | 11 | None | 13650 | 21.3281 | 37406.8906 | 39277.2352 | 0 | 0 | 39277.2352 | 39827.1164
CA4400751 | BONNY DOON SCHOOL | SANTA CRUZ | 160 | 10 |  | 24000 | 37.5 | 42921.5 | 45067.575 | 0.3 | 13520.2725 | 58587.8475 | 59408.0774
CA4300605 | GILROY USD-RUCKER SCHOOL | SANTA CLARA | 688 | 1 |  | 103200 | 161.25 | 85120.25 | 89376.2625 | 0.32 | 28600.404 | 117976.6665 | 119628.3398
CA5400919 | BUENA VISTA SCHOOL | TULARE | 250 | 9 | None | 37500 | 58.5938 | 50114.4688 | 52620.1922 | 0 | 0 | 52620.1922 | 53356.8749
CA0706029 | EXCELSIOR MIDDLE SCHOOL | CONTRA COSTA | 600 | 2 | None | 90000 | 140.625 | 78087.125 | 81991.4812 | 0.3 | 24597.4444 | 106588.9256 | 108081.1706
CA1900751 | EASTSIDE UNION SCHOOL DISTRICT | LOS ANGELES | 650 | 18 |  | 97500 | 152.3438 | 82083.2188 | 86187.3797 | 0.32 | 27579.9615 | 113767.3412 | 115360.084
CA3100072 | LIVE OAK WALDORF SCHOOL | PLACER | 200 | 1 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0 | 0 | 48424.2937 | 49102.2339
CA1502229 | RIO BRAVO GREELEY SCHOOL WATER SYSTEM | KERN | 887 | 16 | None | 133050 | 207.8906 | 101024.7031 | 106075.9383 | 0 | 0 | 106075.9383 | 107561.0014
CA2000760 | DIXIELAND ELEMENTARY SCHOOL | MADERA | 338 | 4 | None | 50700 | 79.2188 | 57147.5938 | 60004.9734 | 0 | 0 | 60004.9734 | 60845.0431
CA4900719 | WEST SIDE UNION SCHOOL DISTRICT | SONOMA | 200 | 5 | None | 30000 | 46.875 | 46118.375 | 48424.2937 | 0.3 | 14527.2881 | 62951.5819 | 63832.904
CA3400267 | BATES ELEMENTARY SCHOOL | SACRAMENTO | 375 | 10 | None | 56250 | 87.8906 | 60104.7031 | 63109.9383 | 0.32 | 20195.1803 | 83305.1185 | 84471.3902
CA3500507 | BITTERWATER-TULLY SCHOOL WS | SAN BENITO | 45 | 2 |  | 6750 | 10.5469 | 33730.4844 | 35417.0086 | 0.3 | 10625.1026 | 46042.1112 | 46686.7007
CA1400522 | PALISADE GLACIER HIGH SCHOOL | INYO | 244 | 7 | None | 36600 | 57.1875 | 49634.9375 | 52116.6844 | 0 | 0 | 52116.6844 | 52846.318
CA2400066 | PLANADA ELEMENTARYSCHOOL | MERCED | 567 | 1 | None | 85050 | 132.8906 | 75449.7031 | 79222.1883 | 0 | 0 | 79222.1883 | 80331.2989
CA5602403 | LAGUNA VISTA SCHOOL/OCEANVIEW SCHOOL DIS | VENTURA | 600 | 1 |  | 90000 | 140.625 | 78087.125 | 81991.4812 | 0.32 | 26237.274 | 108228.7553 | 109743.9578
CA4400754 | MONTE VISTA CHRISTIAN SCHOOL | SANTA CRUZ | 1083 | 43 |  | 162450 | 253.8281 | 116689.3906 | 122523.8602 | 0.3 | 36757.158 | 159281.0182 | 161510.9525
CA1800574 | JOHNSTONVILLE ELEMENTARY SCHOOL | LASSEN | 223 | 1 | None | 33450 | 52.2656 | 47956.5781 | 50354.407 | 0 | 0 | 50354.407 | 51059.3687
CA1800576 | LONG VALLEY CHARTER SCHOOL | LASSEN | 150 | 1 | None | 22500 | 35.1562 | 42122.2812 | 44228.3953 | 0 | 0 | 44228.3953 | 44847.5928
CA4300610 | ANCHORPOINT CHRISTIAN SCHOOL | SANTA CLARA | 167 | 1 | None | 25050 | 39.1406 | 43480.9531 | 45655.0008 | 0.32 | 14609.6002 | 60264.601 | 61108.3054
Total | [12 empty] | 244936712.6461

## Sounder Cost
PWSID | Water System Name | Service Connections | Population | Well Count | 2020 EAR - Sources Monitor Static | County | County multiplier 2 | Sounder Cost | Cost with County M. | Final Cost with inflation
CA0103041 | TRAILER HAVEN MOBILE HOME PARK | 191 | 459 | 1 | No | ALAMEDA | 0.3 | 1700 | 2210 | 2313.87
CA0202501 | DIAMOND VALLEY SCHOOL | 5 | 100 | 1 | No | ALPINE | 0 | 1700 | 1700 | 1779.9
CA0202503 | WOODFORDS MUTUAL WATER COMPANY | 16 | 50 | 2 | No | ALPINE | 0 | 1700 | 1700 | 1779.9
CA0202522 | SIERRA PINES MOBILE HOME PARK | 32 | 70 | 1 |  | ALPINE | 0 | 1700 | 1700 | 1779.9
CA0300011 | SUTTER PINES MHP | 20 | 40 | 1 | No | AMADOR | 0 | 1700 | 1700 | 1779.9
CA0300016 | VOLCANO COMMUNITY SERVICE DIST | 80 | 160 | 3 | No | AMADOR | 0 | 1700 | 1700 | 1779.9
CA0300019 | FIDDLETOWN COMMUNITY SERVICE | 66 | 100 | 1 | No | AMADOR | 0 | 1700 | 1700 | 1779.9
CA0300024 | TABEAU MOBILE HOME PARK | 22 | 62 | 1 | No | AMADOR | 0 | 1700 | 1700 | 1779.9
CA0300053 | RANCHO DEL ORO MHP | 24 | 44 | 1 |  | AMADOR | 0 | 1700 | 1700 | 1779.9
CA0310004 | PLYMOUTH, CITY OF | 520 | 1060 | 2 | N/A | AMADOR | 0 | 1700 | 1700 | 1779.9
CA0400001 | YOUTH WITH A MISSION-SPRINGS OF LIVING W | 52 | 150 | 2 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400003 | HARTLEY MUTUAL WATER SYSTEM | 15 | 31 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400007 | BUTTE CREEK ESTATES MUTUAL WATER CO | 168 | 399 | 3 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400012 | FARM LABOR HOUSING | 135 | 460 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400013 | MERRY MOUNTAIN MUTUAL | 97 | 100 | 4 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400014 | LAKE MADRONE WATER DISTRICT | 123 | 297 | 3 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400019 | OROVILLE MOBILE HOME PARK | 35 | 74 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400020 | PLEASANT GROVE MHP | 88 | 327 | 2 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400021 | ROBINSON'S CORNER MHP | 22 | 20 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400023 | GOLDEN OAKS MOBILE ESTATES | 25 | 34 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400026 | MEADOWBROOK OAKS | 26 | 50 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400027 | FOOTHILL SOLAR COMPANY | 127 | 180 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400030 | GOLDEN FEATHER MHP | 101 | 275 | 2 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400036 | MOUNTAIN VIEW MHC LLC | 129 | 230 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400040 | ALMOND GROVE MOBILE PARK | 175 | 250 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400041 | FOREST RANCH MOBILE PARK | 16 | 25 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400042 | FOREST VILLAGE LLC | 21 | 34 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400051 | DINGERVILLE USA PARK | 80 | 447 | 2 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400060 | HONCUT ELEMENTARY SCHOOL | 3 | 25 | 2 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400062 | RICHVALE ELEMENTARY SCHOOL | 4 | 63 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400063 | MANZANITA ELEMENTARY SCHOOL | 3 | 295 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400064 | CONCOW ELEMENTARY SCHOOL | 11 | 115 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400067 | FEATHER RIVER SCHOOL | 2 | 25 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400073 | NORD COUNTRY SCHOOL | 5 | 66 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400078 | FOREST KNOLLS MUTUAL WATER CO | 21 | 46 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400079 | FOREST RANCH CHARTER SCHOOL | 4 | 146 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400081 | FEATHER RIDGE ESTATES WATER CO | 15 | 37 | 2 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400090 | MOUNTAIN VILLAGE HOMEOWNER'S ASSOC | 17 | 40 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400149 | HUMBOLDT WOODLANDS MUTUAL | 31 | 75 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400151 | KEEFER CREEK ESTATES | 55 | 160 | 2 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0400155 | BIGGERS GLEN MUTUAL WATER CO | 29 | 25 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0409183 | SIERRA MOON WATER COMPANY | 86 | 120 | 2 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0410003 | DURHAM IRRIGATION DISTRICT | 479 | 1561 | 3 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0410007 | PARADISE IRRIGATION DISTRICT | 2369 | 4600 | 1 | No | BUTTE | 0 | 1700 | 1700 | 1779.9
CA0500019 | MINERAL MOUNTAIN MUTUAL WATER | 38 | 125 | 5 |  | CALAVERAS | 0 | 1700 | 1700 | 1779.9
CA0500027 | LILI VALLEY WATER CO. | 70 | 99 | 2 |  | CALAVERAS | 0 | 1700 | 1700 | 1779.9
CA0500068 | DUNROVIN MOBILE HOME VILLAGE | 42 | 99 | 2 |  | CALAVERAS | 0 | 1700 | 1700 | 1779.9
CA0500075 | LAKESIDE MOBILE ESTATES | 24 | 54 | 1 | No | CALAVERAS | 0 | 1700 | 1700 | 1779.9
CA0500085 | TOYON MIDDLE SCHOOL | 6 | 200 | 4 | No | CALAVERAS | 0 | 1700 | 1700 | 1779.9
CA0500091 | RITE OF PASSAGE/SIERRA RIDGE | 13 | 150 | 3 | NULL | CALAVERAS | 0 | 1700 | 1700 | 1779.9
CA0510019 | CCWD - WALLACE | 110 | 340 | 2 |  | CALAVERAS | 0 | 1700 | 1700 | 1779.9
CA0600005 | COLUSA CO. SERVICE AREA #2-STONYFORD | 63 | 250 | 1 |  | COLUSA | 0 | 1700 | 1700 | 1779.9
CA0600008 | COLUSA CO. WWD #1 - GRIMES | 123 | 305 | 2 | No | COLUSA | 0 | 1700 | 1700 | 1779.9
CA0600012 | COLUSA CO. SERVICE AREA #1-CENTURY RANCH | 88 | 246 | 3 |  | COLUSA | 0 | 1700 | 1700 | 1779.9
CA0600013 | COLUSA CO. WWD #2 - PRINCETON | 120 | 382 | 2 | No | COLUSA | 0 | 1700 | 1700 | 1779.9
CA0706004 | OAKLEY MUTUAL WATER COMPANY | 50 | 170 | 2 |  | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0706028 | KNIGHTSEN ELEMENTARY SCHOOL | 4 | 350 | 1 |  | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0706029 | EXCELSIOR MIDDLE SCHOOL | 2 | 600 | 1 | No | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707507 | WILLOW PARK MARINA | 125 | 380 | 2 | No | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707519 | DUTCH SLOUGH WATER WORKS | 58 | 49 | 1 | No | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707523 | FLAMINGO MOBILE MANOR | 62 | 200 | 1 | NULL | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707553 | RIVERVIEW MOBILE HOMES | 45 | 216 | 1 | No | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707572 | BETHEL ISLAND MUTUAL WATER CO | 45 | 149 | 1 | No | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707573 | DELTA MUTUAL WATER COMPANY | 119 | 225 | 2 |  | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707574 | SANTIAGO ISLAND VILLAGE | 211 | 400 | 1 |  | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707575 | BETHEL ISLAND MHC | 66 | 185 | 1 | No | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707585 | MORAGA HEIGHTS MUTUAL WATER | 20 | 60 | 1 |  | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707589 | BELLA VISTA WATER SYS | 33 | 93 | 1 | No | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707594 | CASA MEDANOS WATER SYSTEM | 16 | 45 | 1 | No | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707597 | SANDY POINT MOBILE HOME PARK | 24 | 67 | 1 | No | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707598 | CAMINO MOBILEHOME | 75 | 210 | 1 |  | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707601 | RUSSOS MOBILE PARK | 20 | 110 | 1 | No | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707608 | MARINA MOBILE MANOR | 24 | 75 | 1 | No | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707613 | WILLOW MOBILE HOME PARK | 172 | 350 | 1 |  | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707615 | DOUBLETREE RANCH WATER SYSTEM | 20 | 49 | 2 | No | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707620 | CANYON SCHOOL | 1 | 200 | 1 |  | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0707623 | WILCOX STATION RANCH | 15 | 90 | 1 | No | CONTRA COSTA | 0.3 | 1700 | 2210 | 2313.87
CA0800526 | REDWOOD PARK C.S.D. | 44 | 200 | 3 | No | DEL NORTE | 0 | 1700 | 1700 | 1779.9
CA0800548 | KLAMATH C.S.D. | 59 | 100 | 3 | No | DEL NORTE | 0 | 1700 | 1700 | 1779.9
CA0800552 | NORTHCREST TRAILER CITY | 89 | 250 | 2 | No | DEL NORTE | 0 | 1700 | 1700 | 1779.9
CA0800556 | HRC C.S.D. | 54 | 150 | 1 | No | DEL NORTE | 0 | 1700 | 1700 | 1779.9
CA0800603 | BUTTE COURT MOBILE HOME PARK | 23 | 67 | 1 | No | DEL NORTE | 0 | 1700 | 1700 | 1779.9
CA0800605 | WEST PARK PROPERTIES | 42 | 112 | 1 | No | DEL NORTE | 0 | 1700 | 1700 | 1779.9
CA0800647 | REDWOOD MAINT. & OPER. | 1 | 421 | 1 | No | DEL NORTE | 0 | 1700 | 1700 | 1779.9
CA0800649 | MARGARET KEATING MAIN. & OPER. | 1 | 135 | 1 | No | DEL NORTE | 0 | 1700 | 1700 | 1779.9
CA0800700 | LAS PALMAS MOBILE HOME PARK | 60 | 120 | 2 | No | DEL NORTE | 0 | 1700 | 1700 | 1779.9
CA0800800 | PINE GROVE TRAILER PARK | 51 | 100 | 1 | No | DEL NORTE | 0 | 1700 | 1700 | 1779.9
CA0800825 | JED SMITH HOMEOWNERS ASSN. | 27 | 58 | 3 | No | DEL NORTE | 0 | 1700 | 1700 | 1779.9
CA0800861 | RESERVATION RANCH | 20 | 50 | 1 |  | DEL NORTE | 0 | 1700 | 1700 | 1779.9
CA0900102 | GOLD BEACH PARK | 40 | 100 | 1 | No | EL DORADO | 0.3 | 1700 | 2210 | 2313.87
CA0900111 | PIONEER ELEMENTARY SCHOOL | 19 | 250 | 2 |  | EL DORADO | 0.3 | 1700 | 2210 | 2313.87
CA0900210 | MILLERS HILL SCHOOL | 7 | 120 | 3 | No | EL DORADO | 0.3 | 1700 | 2210 | 2313.87
CA0900300 | KYBURZ MUTUAL WATER COMPANY | 118 | 150 | 1 | No | EL DORADO | 0.3 | 1700 | 2210 | 2313.87
CA0900304 | SILVERFORK SCHOOL | 2 | 25 | 1 |  | EL DORADO | 0.3 | 1700 | 2210 | 2313.87
CA0900309 | MOUNTAIN CREEK SCHOOL | 8 | 125 | 3 | No | EL DORADO | 0.3 | 1700 | 2210 | 2313.87
CA0900404 | OAKLANE MOBILE VILLAGE, LLC. | 35 | 75 | 1 | No | EL DORADO | 0.3 | 1700 | 2210 | 2313.87
CA0900410 | LATROBE ELEMENTARY SCHOOL | 5 | 65 | 1 | No | EL DORADO | 0.3 | 1700 | 2210 | 2313.87
CA0900422 | CRYSTAL CAVES MHP | 40 | 112 | 1 |  | EL DORADO | 0.3 | 1700 | 2210 | 2313.87
CA0901217 | BEAR STATE WATER WORKS | 56 | 100 | 2 | No | EL DORADO | 0.3 | 1700 | 2210 | 2313.87
CA1000056 | MEADOW LAKES CLUB | 120 | 240 | 3 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000104 | CENTERVILLE SCHOOL | 11 | 375 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000105 | MADISON ELEMENTARY SCHOOL | 8 | 900 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000111 | PINE RIDGE SCHOOL | 13 | 100 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000182 | BURREL UNION ELEMENTARY SCHOOL | 2 | 178 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000187 | INDIANOLA SCHOOL | 10 | 511 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000190 | LONE STAR SCHOOL | 6 | 436 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000192 | MONROE SCHOOL | 3 | 200 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000194 | PACIFIC UNION ELEMENTARY SCHOOL | 1 | 490 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000204 | AMERICAN UNION SCHOOL | 33 | 250 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000206 | HOUGHTON-KEARNEY SCHOOL | 4 | 310 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000208 | ROOSEVELT ELEMENTARY SCHOOL | 12 | 370 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000217 | CENTRAL HIGH SCHOOL WEST | 10 | 1127 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000238 | CAMDEN TRAILER PARK | 26 | 75 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000259 | NEW HORIZONS MOBILE/RV PARK | 77 | 82 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000260 | SANDY CREEK VILLAGE MHP | 45 | 88 | 2 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000265 | MARY LOU MOBILE HOME PARK | 34 | 60 | 2 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000267 | KINGS CANYON MOBILE HOME PARK | 26 | 120 | 3 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000280 | SIERRA HIGH SCHOOL | 26 | 690 | 3 |  | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000295 | KINGS PARK APARTMENTS | 41 | 120 | 1 |  | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000298 | WOODWARD BLUFFS MHP | 172 | 300 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000315 | CLAY JOINT ELEMENTARY SCHOOL | 5 | 275 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000369 | ZONNEVELD DAIRY - CEDAR | 15 | 70 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000378 | SUNSET WEST COMMUNITY LLC | 159 | 350 | 2 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000405 | PIEDRA PARK ASSOCIATION | 15 | 25 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000426 | RIVERBEND MOBILE HOME & RV PARK | 49 | 400 | 2 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000476 | FOOTHILL ELEMENTARY SCHOOL | 12 | 900 | 3 |  | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1000627 | ZONNEVELD DAIRY - CERINI | 17 | 48 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1009051 | CANTUA CREEK VINEYARDS, IV, LLC. | 16 | 50 | 1 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1010049 | BIOLA COMMUNITY SERVICES DIST | 1200 | 1623 | 2 |  | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1010501 | NPS-GRANT GROVE | 100 | 2950 | 2 | No | FRESNO | 0 | 1700 | 1700 | 1779.9
CA1100104 | WILLOW CREEK CHRISTIAN SCHOOL | 2 | 47 | 1 | No | GLENN | 0 | 1700 | 1700 | 1779.9
CA1100237 | WILLOWS MOBILE HOME COMMUNITY & RV PARK | 87 | 190 | 1 | No | GLENN | 0 | 1700 | 1700 | 1779.9
CA1100254 | VOYLES TRAILER PARK | 15 | 27 | 1 | No | GLENN | 0 | 1700 | 1700 | 1779.9
CA1100436 | ORLAND OAKS MHP | 83 | 186 | 1 | No | GLENN | 0 | 1700 | 1700 | 1779.9
CA1100444 | ORLAND ESTATES MOBILE H.P. | 74 | 200 | 2 | No | GLENN | 0 | 1700 | 1700 | 1779.9
CA1100445 | ORLAND MOBILE H.P. | 54 | 178 | 1 |  | GLENN | 0 | 1700 | 1700 | 1779.9
CA1100448 | PLAZA ELEMENTARY SCHOOL | 4 | 250 | 1 | No | GLENN | 0 | 1700 | 1700 | 1779.9
CA1100452 | SHADY OAKS TRAILER PARK | 43 | 57 | 1 | No | GLENN | 0 | 1700 | 1700 | 1779.9
CA1100527 | CAPAY JOINT UNION ELEM. SCHOOL | 1 | 230 | 1 |  | GLENN | 0 | 1700 | 1700 | 1779.9
CA1100711 | BUTTE CITY COMMUNITY S.D. | 48 | 75 | 1 | No | GLENN | 0 | 1700 | 1700 | 1779.9
CA1100749 | RIVER VALLEY CHRISTIAN SCHOOL | 2 | 80 | 1 | No | GLENN | 0 | 1700 | 1700 | 1779.9
CA1200518 | RIVERSIDE CSD | 103 | 293 | 2 |  | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1200538 | MYERS FLAT M.W.S. INC. | 101 | 400 | 2 |  | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1200541 | PHILLIPSVILLE C.S.D. | 66 | 300 | 1 | No | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1200546 | CASTERLIN SCHOOL | 1 | 130 | 1 | No | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1200547 | MILL CREEK M.W.C. | 36 | 85 | 2 | No | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1200591 | BIG LAGOON PARK WATER CO. | 76 | 70 | 2 | No | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1200681 | CUDDEBACK GRAMMAR SCHOOL | 1 | 165 | 1 | No | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1200684 | MATTOLE ELEMENTARY SCHOOL | 1 | 50 | 2 | NULL | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1200687 | RIVERBEND MOBILE HOME PARK | 29 | 60 | 1 | NULL | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1200701 | ORICK C.S.D. | 141 | 450 | 2 | No | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1200707 | MIRANDA C.S.D. | 149 | 600 | 2 | No | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1200715 | GREEN DIAMOND RESOURCE COMPANY - KORBEL | 18 | 250 | 2 | No | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1200718 | WADDINGTON W.W. | 25 | 75 | 1 | No | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1200778 | BRIDGEVILLE ELEM. SCHOOL | 1 | 50 | 1 | No | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1210008 | GARBERVILLE SANITARY DISTRICT | 442 | 1500 | 1 | No | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1210012 | RIO DELL, CITY OF | 1316 | 3300 | 2 | No | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1210015 | WILLOW CREEK C.S.D. | 931 | 1710 | 5 |  | HUMBOLDT | 0 | 1700 | 1700 | 1779.9
CA1300546 | GOLD ROCK RANCH | 76 | 50 | 2 | No | IMPERIAL | 0 | 1700 | 1700 | 1779.9
CA1300588 | IID VILLAGE | 18 | 30 | 2 | No | IMPERIAL | 0 | 1700 | 1700 | 1779.9
CA1300616 | PALO VERDE COUNTY WATER DIST. | 134 | 410 | 2 |  | IMPERIAL | 0 | 1700 | 1700 | 1779.9
CA1300622 | SPORTSMANS PARADISE | 30 | 60 | 2 | No | IMPERIAL | 0 | 1700 | 1700 | 1779.9
CA1400010 | ROLLING GREEN UTILITIES, INC. | 285 | 1225 | 3 |  | INYO | 0 | 1700 | 1700 | 1779.9
CA1400020 | ABERDEEN WATER SYSTEM | 75 | 23 | 1 |  | INYO | 0 | 1700 | 1700 | 1779.9
CA1400025 | VALLEY VISTA MUTUAL WATER COMPANY | 25 | 70 | 1 | No | INYO | 0 | 1700 | 1700 | 1779.9
CA1400026 | RAWSON CREEK MUTUAL WATER COMPANY | 40 | 90 | 2 |  | INYO | 0 | 1700 | 1700 | 1779.9
CA1400030 | GLENWOOD MOBILE ESTATES | 170 | 448 | 3 | No | INYO | 0 | 1700 | 1700 | 1779.9
CA1400037 | FOOTHILL MOBILE HOME PARK | 48 | 60 | 2 |  | INYO | 0 | 1700 | 1700 | 1779.9
CA1400045 | PRIMROSE LANE APARTMENTS | 26 | 73 | 2 |  | INYO | 0 | 1700 | 1700 | 1779.9
CA1400056 | BROOKSIDE ESTATES MUTUAL WATER COMPANY | 21 | 59 | 2 |  | INYO | 0 | 1700 | 1700 | 1779.9
CA1400059 | BROOKSIDE MOBILE HOME PARK | 45 | 126 | 2 | No | INYO | 0 | 1700 | 1700 | 1779.9
CA1400066 | ASPENDELL MUTUAL WATER COMPANY | 94 | 60 | 2 | No | INYO | 0 | 1700 | 1700 | 1779.9
CA1400078 | SCE BISHOP CREEK PLANT 4 | 15 | 38 | 1 |  | INYO | 0 | 1700 | 1700 | 1779.9
CA1400099 | MOUNTAIN VIEW TRAILER COURT | 24 | 53 | 1 | No | INYO | 0 | 1700 | 1700 | 1779.9
CA1400109 | SIERRA NORTH COMMUNITY SERVICE DISTRICT | 16 | 45 | 1 | No | INYO | 0 | 1700 | 1700 | 1779.9
CA1400110 | PARK WEST MUTUAL WATER COMPANY | 67 | 200 | 3 |  | INYO | 0 | 1700 | 1700 | 1779.9
CA1400135 | WILSON CIRCLE MUTUAL WATER COMPANY | 48 | 129 | 3 | No | INYO | 0 | 1700 | 1700 | 1779.9
CA1400518 | VAN LOON WATER ASSOCIATION | 15 | 25 | 2 |  | INYO | 0 | 1700 | 1700 | 1779.9
CA1400522 | PALISADE GLACIER HIGH SCHOOL | 7 | 244 | 1 |  | INYO | 0 | 1700 | 1700 | 1779.9
CA1410505 | NPS - DEATH VALLEY, FURNACE CREEK | 150 | 150 | 3 |  | INYO | 0 | 1700 | 1700 | 1779.9
CA1500209 | ALTA SIERRA MUTUAL WATER CO. | 225 | 143 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500231 | VICTORY MUTUAL WATER COMPANY | 173 | 849 | 2 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500252 | KERN VALLEY MUTUAL WATER COMPANY | 47 | 47 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500289 | ATHAL MUTUAL WATER SYSTEM | 55 | 150 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500290 | NORTH MUROC MUTUAL WATER COMPANY | 198 | 270 | 1 | N/A | KERN | 0 | 1700 | 1700 | 1779.9
CA1500296 | FULLER ACRES MUTUAL WATER COMPANY | 165 | 545 | 2 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500340 | WEST TEHACHAPI MUTUAL | 36 | 150 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500341 | SIERRA BELLA MUTUAL WATER COMPANY | 180 | 60 | 5 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500344 | SOUTH KERN MUTUAL WATER COMPANY | 15 | 32 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500349 | STOCKDALE MUTUAL WATER CO. | 81 | 200 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500378 | MAHER MUTUAL WATER COMPANY | 50 | 150 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500380 | DE RANCHO Y MOBILE VILLA WATER | 90 | 200 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500393 | RAINBIRD VALLEY MUTUAL WATER COMPANY | 85 | 238 | 2 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500406 | TRADEWIND WATER ASSOC. | 234 | 632 | 2 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500409 | BROCK MUTUAL WATER COMPANY | 155 | 462 | 2 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500426 | ROSE VILLA APARTMENTS | 32 | 65 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500436 | HUNGRY GULCH MWC | 36 | 74 | 3 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500443 | CANYON MEADOWS MUTUAL WATER | 141 | 394 | 3 | NULL | KERN | 0 | 1700 | 1700 | 1779.9
CA1500447 | SIERRA BREEZE MUTUAL WATER COMPANY | 60 | 150 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500448 | HILLVIEW ACRES MUTUAL WATER COMPANY | 47 | 36 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500455 | WILLIAM FISHER MEMORIAL WATER COMPANY | 16 | 56 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500458 | R.S. MUTUAL WATER COMPANY | 24 | 67 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500465 | OAK KNOLLS MUTUAL WATER COMPANY | 47 | 123 | 3 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500483 | ALLEN ROAD MUTUAL WATER SYSTEM | 59 | 195 | 2 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500485 | ANTELOPE VALLEY MOBILE ESTATES | 28 | 60 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500493 | EL ADOBE POA, INC. | 80 | 200 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500494 | WILSON ROAD WATER COMMUNITY | 20 | 66 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500507 | ST. CLAIR RANCHOS MUTUAL WATER CO. | 32 | 105 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500535 | MANON MANOR MUTUAL WATER COMPANY | 55 | 200 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500542 | WILLOW SPRINGS MOBILE HOME PARK | 104 | 275 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500543 | AGAPE MUTUAL WATER SYSTEM | 16 | 60 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500544 | ENOS LANE PUBLIC UTILITY DISTRICT | 89 | 365 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500546 | HARVEST MOON MUTUAL WATER CO | 49 | 138 | 2 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500550 | WEST VALLEY MUTUAL WATER COMPANY | 41 | 70 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500553 | RANCHOS DEL RIO | 24 | 62 | 2 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500554 | EAST INYOKERN MUTUAL WATER | 28 | 87 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500555 | MUSTANG MUTUAL WATER SYSTEM | 51 | 200 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500557 | STOCKDALE RANCHOS MUTUAL WATER CO | 95 | 393 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500560 | KRANENBURG WATER SYSTEM | 15 | 42 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500561 | ROUND MOUNTAIN WATER COMPANY | 18 | 50 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500563 | CHINA LAKE ACRES MUTUAL WATER COMPANY | 60 | 198 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500569 | VALLEY VIEW ESTATES MUTUAL WATER CO | 50 | 94 | 4 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500571 | KERN MOBILE ESTATES LLC | 60 | 73 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500575 | SAN JOAQUIN ESTATES MUTUAL WATER COMPANY | 61 | 165 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500579 | LIFE WATER CO-OP | 18 | 27 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500584 | GOOSELAKE WATER COMPANY | 32 | 90 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1500585 | OASIS PROPERTY OWNERS ASSOCIATION | 39 | 100 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500588 | SON SHINE PROPERTIES | 106 | 438 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500591 | SWEET WATER CO-OP | 15 | 47 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500593 | UPLANDS OF THE KERN MUTUAL WATER COMPANY | 20 | 80 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1500599 | CHOCTAW VALLEY MUTUAL WATER CO. | 18 | 44 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1502068 | DI GIORGIO SCHOOL WATER SYSTEM | 1 | 232 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1502154 | LAKESIDE SCHOOL | 1 | 800 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1502164 | LLANAS CAMP FOUR WATER SYSTEM | 55 | 54 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1502221 | POND SCHOOL WATER SYSTEM | 2 | 250 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1502229 | RIO BRAVO GREELEY SCHOOL WATER SYSTEM | 16 | 887 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1502232 | ROSAMOND MOBILEHOME PARK | 79 | 175 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1502247 | DESERT BREEZE MOBILE HOME ESTATES | 63 | 82 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1502260 | SOUTH FORK ELEMENTARY SCHOOL WATER SYS | 2 | 154 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1502383 | NORD ROAD WATER ASSOCIATION | 16 | 32 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1502449 | CYPRESS CANYON WATER SYSTEM | 16 | 44 | 2 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1502465 | PANAMA ROAD PROPERTY OWNERS ASSOC | 16 | 45 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1502564 | SIERRA MEADOWS | 51 | 68 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1502607 | PIUTE MOUNTAIN SCHOOL WATER | 5 | 50 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1502608 | OWENS PEAK WEST | 24 | 79 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1502620 | POND MUTUAL WATER COMPANY | 18 | 48 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1502622 | GOSFORD ROAD WATER COMPANY | 15 | 50 | 2 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1502645 | MEADOWS OF THE KERN MUTUAL WATER COMPANY | 16 | 32 | 4 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1502653 | BELLA VISTA MUTUAL WATER COMPANY | 46 | 150 | 2 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1502659 | OWENS PEAK SOUTH | 17 | 40 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1502663 | TOWN & COUNTRY WATER COMPANY | 22 | 73 | 2 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1502690 | DUNE 3 MUTUAL WATER COMPANY, LLC | 36 | 119 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1502750 | RIVERVIEW HOMEOWNERS ASSOCIATION | 20 | 40 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1503368 | SOUTH FORK MIDDLE SCHOOL | 1 | 204 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1503475 | WESTERN ACRES MUTUAL WATER COMPANY | 90 | 310 | 3 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1503536 | GLENNVILLE MUTUAL WATER COMPANY | 25 | 100 | 1 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1510004 | CASA LOMA WATER CO, INC. | 248 | 900 | 2 |  | KERN | 0 | 1700 | 1700 | 1779.9
CA1510009 | ERSKINE CREEK WC | 1111 | 2500 | 3 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1510027 | DESERT LAKE COMM SERV DIST | 251 | 1036 | 1 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1510801 | WASCO ST. PRISON RECEPTION CTR | 1768 | 6068 | 2 | No | KERN | 0 | 1700 | 1700 | 1779.9
CA1600002 | SUNSET VISTA ESTATES MHP | 108 | 400 | 1 | No | KINGS | 0 | 1700 | 1700 | 1779.9
CA1600009 | HANFORD CHRISTIAN SCHOOL | 14 | 175 | 1 | No | KINGS | 0 | 1700 | 1700 | 1779.9
CA1600011 | PIONEER ELEMENTARY SCHOOL | 6 | 750 | 2 | No | KINGS | 0 | 1700 | 1700 | 1779.9
CA1600013 | LAKESIDE ELEMENTARY SCHOOL | 5 | 388 | 1 | No | KINGS | 0 | 1700 | 1700 | 1779.9
CA1600015 | KINGS RIVER HARDWICK SCHOOL | 7 | 908 | 1 | No | KINGS | 0 | 1700 | 1700 | 1779.9
CA1600507 | HARDWICK WATER COMPANY | 20 | 69 | 1 | No | KINGS | 0 | 1700 | 1700 | 1779.9
CA1700527 | MOUNTAIN OF ATTENTION WATER | 26 | 40 | 1 | No | LAKE | 0 | 1700 | 1700 | 1779.9
CA1700536 | SUNRISE SHORE MUTUAL WATER COMPANY | 42 | 83 | 1 | No | LAKE | 0 | 1700 | 1700 | 1779.9
CA1700549 | CORINTHIAN BAY MUTUAL WATER COMPANY | 74 | 150 | 2 | No | LAKE | 0 | 1700 | 1700 | 1779.9
CA1700579 | VILLA BLUE ESTATES WATER DISTRICT | 21 | 60 | 1 | No | LAKE | 0 | 1700 | 1700 | 1779.9
CA1700589 | BLUE LAKES MOBILE HOME PARK | 24 | 32 | 1 | No | LAKE | 0 | 1700 | 1700 | 1779.9
CA1700592 | KONOCTI SHORES | 99 | 99 | 2 | No | LAKE | 0 | 1700 | 1700 | 1779.9
CA1700595 | CAL 20 VILLAGE AND MEADOW POINTE PARK | 93 | 175 | 2 | No | LAKE | 0 | 1700 | 1700 | 1779.9
CA1700596 | BLUE LAKES VILLAGE | 44 | 65 | 1 | No | LAKE | 0 | 1700 | 1700 | 1779.9
CA1700606 | BAYCLIFF WATER | 56 | 70 | 1 | No | LAKE | 0 | 1700 | 1700 | 1779.9
CA1700610 | BELLA LAGO MOBILE HOME PARK | 46 | 152 | 1 | No | LAKE | 0 | 1700 | 1700 | 1779.9
CA1700630 | PIER 1900 HOMEOWNER S ASSOCIATION | 54 | 152 | 1 | No | LAKE | 0 | 1700 | 1700 | 1779.9
CA1700657 | WINDFLOWER POINT MUTUAL WATER COMPANY | 25 | 25 | 1 | No | LAKE | 0 | 1700 | 1700 | 1779.9
CA1700702 | INNISFREE WATER COMPANY | 17 | 56 | 1 | No | LAKE | 0 | 1700 | 1700 | 1779.9
CA1710006 | KONOCTI COUNTY WATER DISTRICT | 1800 | 5928 | 1 | N/A | LAKE | 0 | 1700 | 1700 | 1779.9
CA1800503 | SUSAN RIVER PARK WATER CO. | 50 | 140 | 2 | No | LASSEN | 0 | 1700 | 1700 | 1779.9
CA1800511 | LAKE FOREST MUTUAL W.C. | 220 | 565 | 2 | No | LASSEN | 0 | 1700 | 1700 | 1779.9
CA1800516 | LITTLE VALLEY CSD | 44 | 70 | 1 | NULL | LASSEN | 0 | 1700 | 1700 | 1779.9
CA1800523 | PINEVIEW MOBILE HOME PARK | 52 | 113 | 1 |  | LASSEN | 0 | 1700 | 1700 | 1779.9
CA1800524 | LASSEN MOBILE HOME PARK | 30 | 62 | 1 | No | LASSEN | 0 | 1700 | 1700 | 1779.9
CA1800529 | SUSAN HILLS ESTATES WC | 98 | 316 | 2 | No | LASSEN | 0 | 1700 | 1700 | 1779.9
CA1800573 | RICHMOND ELEMENTARY SCHOOL | 1 | 247 | 1 | No | LASSEN | 0 | 1700 | 1700 | 1779.9
CA1800574 | JOHNSTONVILLE ELEMENTARY SCHOOL | 1 | 223 | 2 | No | LASSEN | 0 | 1700 | 1700 | 1779.9
CA1800575 | SHAFFER ELEMENTARY SCHOOL | 1 | 320 | 1 | No | LASSEN | 0 | 1700 | 1700 | 1779.9
CA1800576 | LONG VALLEY CHARTER SCHOOL | 1 | 150 | 1 |  | LASSEN | 0 | 1700 | 1700 | 1779.9
CA1800577 | JANESVILLE ELEMENTARY SCHOOL | 1 | 425 | 1 |  | LASSEN | 0 | 1700 | 1700 | 1779.9
CA1810003 | LASSEN COUNTY WATER DISTRICT #1 | 147 | 450 | 2 | No | LASSEN | 0 | 1700 | 1700 | 1779.9
CA1900038 | LANCASTER PARK MOBILE HOME PARK | 21 | 61 | 1 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900075 | BLEICH FLATS MUTUAL | 34 | 93 | 4 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900100 | METTLER VALLEY MUTUAL | 98 | 135 | 2 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900145 | REESEDALE MUTUAL | 23 | 76 | 2 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900146 | SUNNYSIDE FARMS MUTUAL WATER COMPANY | 158 | 326 | 5 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900154 | TIERRA BONITA MUTUAL WATER | 32 | 75 | 1 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900155 | WILSONA GARDENS MUTUAL | 39 | 74 | 1 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900158 | LITTLE BALDY WATER | 36 | 55 | 2 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900301 | SHADOW ACRES MUTUAL WATER COMPANY | 162 | 431 | 2 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900520 | THE VILLAGE MOBILE HOME PARK | 34 | 50 | 1 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900529 | CAMP WILLIAMS-RESORT WATER | 69 | 80 | 2 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900537 | OAK GROVE FAMILY PARK | 40 | 109 | 1 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900541 | WESTERN SKIES MOBILE HOME PARK | 61 | 198 | 1 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900636 | EL RANCHO MOBILE HOME PARK | 76 | 215 | 1 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900649 | GOLDEN SANDS MOBILE HOME PARK | 152 | 450 | 1 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900693 | DESERT PALMS MOBILE HOME PARK | 56 | 140 | 1 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900707 | ILEAD AGUA DULCE CHARTER SCHOOL | 6 | 450 | 1 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900721 | TERRA NOVA MOBILE HOME PARK | 75 | 140 | 1 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900750 | DEL SUR SCHOOL/WESTSIDE UNION DISTRICT | 1 | 825 | 1 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900751 | EASTSIDE UNION SCHOOL DISTRICT | 18 | 650 | 1 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900785 | MITCHELL'S AVENUE E MOBILE HOME PARK | 24 | 24 | 1 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900803 | EL DORADO MUTUAL WATER CO. | 237 | 660 | 1 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900804 | EVERGREEN MUTUAL WATER COMPANY | 46 | 95 | 1 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900808 | LANCASTER WATER COMPANY | 22 | 80 | 2 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900817 | CLEAR SKIES MOBILE HOME PARK | 47 | 131 | 1 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900843 | CALIFORNIAN MOBILE HOME PARK | 133 | 372 | 1 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900868 | RIVERS END TRAILER PARK | 45 | 35 | 1 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900886 | HUGHES-ELIZABETH LAKE UNIFIED SCHOOL DIS | 2 | 550 | 2 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900903 | SLEEPY VALLEY WATER COMPANY | 58 | 130 | 3 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900907 | SHERWOOD MOBILE HOME PARK | 185 | 540 | 2 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900936 | AQUA J. MUTUAL WATER COMPANY | 48 | 165 | 1 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900961 | WINTERHAVEN MOBILE ESTATES | 20 | 56 | 1 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900975 | CALI LAKE RV RESORT | 47 | 99 | 1 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1900976 | THE OAKS | 26 | 67 | 4 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1910056 | LAKE ELIZABETH MUTUAL WATER CO. | 724 | 1790 | 2 | No | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA1910103 | PALM RANCH IRRIGATION DIST. | 1702 | 5564 | 4 |  | LOS ANGELES | 0.32 | 1700 | 2244 | 2349.468
CA2000150 | LIBERTY HIGH SCHOOL | 1 | 1340 | 2 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000501 | BASS LAKE ANNEX 3 | 28 | 42 | 2 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000502 | BASS LAKE HEIGHTS MUTUAL WATER | 90 | 250 | 3 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000509 | CASCADEL MUTUAL WATER SYSTEM | 120 | 314 | 3 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000521 | BROADVIEW TERRACE MUTUAL WATER COMPANY | 178 | 498 | 4 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000524 | SKY ACRES MUTUAL WATER CORP | 64 | 175 | 4 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000526 | PIKE RANCH MUTUAL WATER CO | 20 | 74 | 1 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000527 | YOSEMITE FORKS EST MUTUAL | 99 | 110 | 3 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000529 | BONADELLE RANCHOS MUTUAL WATER | 23 | 50 | 1 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000534 | LEISURE ACRES MUTUAL WATER COMPANY | 24 | 45 | 2 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000567 | YOSEMITE HIGH SCHOOL | 32 | 862 | 1 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000573 | THE VILLAGE | 21 | 40 | 2 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000589 | MAMMOTH POOL MOBILE HOME PARK | 32 | 60 | 1 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000593 | OAKHURST MOBILE HOME ESTATES | 116 | 164 | 2 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000597 | DAIRYLAND SCHOOL | 8 | 250 | 1 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000598 | ALVIEW SCHOOL | 1 | 200 | 2 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000600 | HOWARD ELEMENTARY SCHOOL | 7 | 1081 | 1 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000601 | LA VINA SCHOOL | 7 | 513 | 1 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000602 | RIPPERDAN COMMUNITY DAY SCHOOL | 4 | 113 | 1 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000605 | WHISPERING PINES MHP | 30 | 36 | 2 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000607 | SPRING VALLEY SCHOOL | 10 | 150 | 1 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000611 | COARSEGOLD SCHOOL | 11 | 441 | 2 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000612 | NORTH FORK ELEMENTARY SCHOOL | 18 | 500 | 1 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000616 | WASUMA SCHOOL | 5 | 354 | 1 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000647 | JOHN HOVANNISIAN WATER SYSTEM | 18 | 80 | 2 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000688 | ECCO | 15 | 100 | 3 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000760 | DIXIELAND ELEMENTARY SCHOOL | 4 | 338 | 1 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000828 | SHADY OAKS MOBILE HOME PARK LLC | 21 | 27 | 2 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000844 | RIVERGOLD ELEMENTARY SCHOOL | 9 | 485 | 1 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000846 | SIERRA VIEW SCHOOL | 23 | 250 | 1 | No | MADERA | 0 | 1700 | 1700 | 1779.9
CA2000947 | MINARETS HIGH SCHOOL | 17 | 450 | 3 |  | MADERA | 0 | 1700 | 1700 | 1779.9
CA2100519 | ESTERO MUTUAL | 145 | 186 | 3 | No | MARIN | 0.3 | 1700 | 2210 | 2313.87
CA2100538 | TOMALES HIGH SCHOOL | 2 | 227 | 3 | No | MARIN | 0.3 | 1700 | 2210 | 2313.87
CA2100560 | TOMALES ELEM & MIDDLE SCHOOL | 4 | 265 | 1 | No | MARIN | 0.3 | 1700 | 2210 | 2313.87
CA2100582 | NICASIO SCHOOL | 5 | 40 | 1 | No | MARIN | 0.3 | 1700 | 2210 | 2313.87
CA2110007 | COAST SPRINGS - CAL. WATER SERVICE (PUC) | 251 | 210 | 9 | No | MARIN | 0.3 | 1700 | 2210 | 2313.87
CA2110008 | LAWSON S LANDING | 66 | 962 | 3 | No | MARIN | 0.3 | 1700 | 2210 | 2313.87
CA2210515 | YOSEMITE NPS-EL PORTAL | 235 | 635 | 6 | No | MARIPOSA | 0 | 1700 | 1700 | 1779.9
CA2210921 | WHISPERING PINES APARTMENTS | 28 | 74 | 3 |  | MARIPOSA | 0 | 1700 | 1700 | 1779.9
CA2210925 | YOSEMITE TERRACE ESTATES | 53 | 130 | 1 | No | MARIPOSA | 0 | 1700 | 1700 | 1779.9
CA2300502 | ALBION MUTUAL WATER COMPANY | 27 | 40 | 2 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300506 | MEADOW ESTATES MUTUAL | 35 | 100 | 3 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300514 | ELK COUNTY WATER DISTRICT | 99 | 380 | 1 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300545 | SHORELANDS ROAD & WATER COMPANY | 47 | 85 | 5 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300584 | MENDOCINO SCHOOL DISTRICT- MENDOCINO | 15 | 768 | 2 |  | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300596 | BIG RIVER VISTA MUTUAL WATER COMPANY | 19 | 36 | 1 |  | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300604 | POINT OF VIEW MUTUAL WATER CO | 30 | 56 | 4 |  | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300606 | LAKE VIEW MUTUAL WATER CO. | 29 | 90 | 4 |  | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300609 | SEAFAIR ROAD AND WATER COMPANY | 31 | 50 | 6 |  | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300610 | CASPAR SOUTH SERVICE COMPANY | 95 | 188 | 8 |  | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300644 | WOODSIDE RV PARK | 58 | 280 | 5 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300646 | BELLA SHORES MOBILE HOME PARK | 60 | 80 | 1 |  | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300667 | WOODS, THE (MENDOCINO) | 115 | 153 | 1 |  | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300668 | POINT CABRILLO HIGHLANDS | 21 | 42 | 1 |  | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300705 | LITTLE LAKE MOBILE HOME PARK | 19 | 38 | 1 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300708 | RIDGEWOOD WATER SYSTEM | 167 | 220 | 1 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300717 | CREEKSIDE CABINS & RV RESORT | 55 | 124 | 1 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300730 | WESTPORT COUNTY WATER DISTRICT | 73 | 369 | 1 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300735 | HOLLY RANCH VILLAGE | 19 | 50 | 2 |  | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300743 | DOLPHIN ISLE MARINA | 86 | 560 | 1 |  | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300764 | ANDERSON VALLEY HIGH SCHOOL | 8 | 300 | 3 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300770 | ANDERSON VALLEY ELEMENTARY SCHOOL | 11 | 350 | 1 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300785 | LEGGETT VALLEY SCHOOL | 5 | 100 | 2 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300826 | MANCHESTER UNION ELEMENTARY SCHOOL | 1 | 75 | 1 |  | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300829 | ROUND VALLEY HIGH SCHOOL | 1 | 162 | 1 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300830 | ROUND VALLEY ELEMENTARY SCHOOL | 1 | 263 | 1 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300832 | HILLS RANCH MUTUAL WATER COMPANY | 48 | 77 | 4 |  | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300837 | YOKAYO TRIBE OF INDIANS | 23 | 75 | 1 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300846 | MENDOCINO SCHOOL DISTRICT-ALBION SCHOOL | 2 | 25 | 1 |  | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300863 | EEL RIVER CHARTER SCHOOL | 1 | 73 | 1 |  | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300874 | MONTESSORI DEL MAR LEARNING CENTER | 3 | 50 | 1 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2300892 | COVELO MOBILE HOME PARK | 30 | 30 | 2 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2310013 | POINT ARENA WATER WORKS | 234 | 472 | 2 | No | MENDOCINO | 0 | 1700 | 1700 | 1779.9
CA2400062 | SNELLING MERCED FALLS SCHOOL | 4 | 85 | 1 | No | MERCED | 0 | 1700 | 1700 | 1779.9
CA2400064 | MERQUIN ELEMENTARY SCHOOL | 2 | 284 | 1 |  | MERCED | 0 | 1700 | 1700 | 1779.9
CA2400065 | PLAINSBURG ELEMENTARY SCHOOL | 5 | 126 | 2 | No | MERCED | 0 | 1700 | 1700 | 1779.9
CA2400066 | PLANADA ELEMENTARYSCHOOL | 1 | 567 | 1 | No | MERCED | 0 | 1700 | 1700 | 1779.9
CA2400071 | WASHINGTON SCHOOL | 4 | 230 | 1 | No | MERCED | 0 | 1700 | 1700 | 1779.9
CA2400075 | EL NIDO ELEMENTARY SCHOOL | 2 | 219 | 1 | No | MERCED | 0 | 1700 | 1700 | 1779.9
CA2400079 | MCSWAIN ELEMENTARY SCHOOL | 24 | 950 | 2 | No | MERCED | 0 | 1700 | 1700 | 1779.9
CA2400091 | CHARLESTON SCHOOL | 1 | 325 | 1 | No | MERCED | 0 | 1700 | 1700 | 1779.9
CA2400097 | CRESSEY SCHOOL | 7 | 155 | 1 | No | MERCED | 0 | 1700 | 1700 | 1779.9
CA2400099 | GRACE MENNONITE SCHOOL | 1 | 100 | 1 |  | MERCED | 0 | 1700 | 1700 | 1779.9
CA2400113 | SCHELBY SCHOOL | 9 | 290 | 2 | No | MERCED | 0 | 1700 | 1700 | 1779.9
CA2400122 | LONGVIEW MENNONITE SCHOOL | 1 | 120 | 1 |  | MERCED | 0 | 1700 | 1700 | 1779.9
CA2400134 | BUHACH PRESCHOOL (KINDERCARE) | 3 | 110 | 1 | No | MERCED | 0 | 1700 | 1700 | 1779.9
CA2400167 | BALLICO CSD | 73 | 238 | 1 | No | MERCED | 0 | 1700 | 1700 | 1779.9
CA2400219 | MERCED NEW LIFE SCHOOL | 2 | 36 | 1 |  | MERCED | 0 | 1700 | 1700 | 1779.9
CA2500801 | NEWELL COUNTY WATER DISTRICT | 310 | 300 | 3 | NULL | MODOC | 0 | 1700 | 1700 | 1779.9
CA2600532 | LUNDY MUTUAL WATER COMPANY | 32 | 70 | 1 |  | MONO | 0 | 1700 | 1700 | 1779.9
CA2600546 | CROWLEY LAKE MUTUAL WATER COMPANY | 57 | 175 | 1 | No | MONO | 0 | 1700 | 1700 | 1779.9
CA2600568 | EDNA BEAMAN ELEMENTARY SCHOOL | 2 | 26 | 1 | No | MONO | 0 | 1700 | 1700 | 1779.9
CA2600570 | COLEVILLE HIGH SCHOOL | 4 | 216 | 2 | No | MONO | 0 | 1700 | 1700 | 1779.9
CA2600621 | WHITE MOUNTAIN MUTUAL WATER COMPANY | 43 | 142 | 1 | No | MONO | 0 | 1700 | 1700 | 1779.9
CA2600622 | SIERRA EAST HOA | 30 | 84 | 2 | No | MONO | 0 | 1700 | 1700 | 1779.9
CA2600699 | CHALFANT VALLEY WEST M.W.C. | 15 | 45 | 2 | No | MONO | 0 | 1700 | 1700 | 1779.9
CA2600733 | COLD WATER CANYON MWC | 45 | 90 | 2 | NULL | MONO | 0 | 1700 | 1700 | 1779.9
CA2700503 | ASSISI MWC | 42 | 126 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700509 | OAK MANOR WS | 28 | 92 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700522 | CABANA HOLIDAY WS | 146 | 400 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700523 | CALERA CANYON HEIGHTS HOA | 17 | 74 | 3 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700534 | COLONIAL OAK WC INC | 66 | 198 | 4 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700535 | JOST POST WA | 20 | 60 | 1 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700536 | CORRAL DE TIERRA ESTATES WC | 16 | 45 | 2 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700541 | DEL MONTE FARMS RD WS #03 | 16 | 55 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700547 | DESMOND RD WS #03 | 19 | 56 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700548 | DOLAN RD MWC | 40 | 120 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700552 | ECHO VALLEY SCHOOL WS | 1 | 579 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700577 | ELKHORN SCHOOL WS | 1 | 694 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700586 | GABILAN WC | 162 | 535 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700589 | GLENN AVE WS #01 | 26 | 73 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700594 | HIDDEN VALLEY WA | 32 | 164 | 2 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700606 | HIDDEN VIEWS MHP WS | 31 | 75 | 2 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700612 | LAGUNA SECA WC | 58 | 162 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700622 | OUTLOOK WA | 18 | 45 | 3 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700624 | LEAFWOOD COMMUNITY WA | 23 | 66 | 1 | NULL | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700629 | MANZANITA HILLS WA | 31 | 75 | 2 | NULL | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700634 | CHETMOORE ACRES WA | 25 | 70 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700656 | MORO COJO MWA | 19 | 67 | 3 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700665 | OAK HEIGHTS W & R CO INC | 35 | 105 | 3 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700669 | ORCHARD LN WS #02 | 16 | 32 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700674 | PARADISE LAKE MUTUAL WATER CO. | 76 | 180 | 3 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700678 | PARADISE RD WS #05 | 15 | 42 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700682 | PARADISE RD WS #09 | 17 | 206 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700686 | GARLEN COURT WS | 17 | 65 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700687 | PESANTE RD WS #02 | 40 | 120 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700691 | PESANTE RD WS #06 | 16 | 48 | 1 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700702 | PRUNEDALE MWC | 84 | 277 | 3 | NULL | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700705 | PRUNEDALE SCHOOL WS | 1 | 655 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700709 | RANCHO BORROMEO MWS | 36 | 100 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700713 | ROLLING HILLS RANCHO WA | 56 | 184 | 3 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700727 | SAN ANTONIO SCHOOL DISTRICT WS | 1 | 300 | 1 | NULL | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700731 | Z RANCH MWC | 27 | 62 | 5 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700733 | SAN JUAN RD WS #01 | 15 | 49 | 1 | N/A | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700738 | SAN MIGUEL WS #01 | 34 | 100 | 3 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700766 | STRAWBERRY RD WS #06 | 27 | 78 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700772 | STRUVE RD WS #02 | 105 | 166 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700775 | TIERRA VERDE MWC | 16 | 48 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700792 | SUMMERHILL MHP WS | 34 | 95 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700799 | VISTA DEL TORO WS | 28 | 92 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700838 | SPRING CANYON WA | 33 | 99 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700842 | BAUMANN RD WS #01 | 17 | 40 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700970 | ROYAL SIERRA ESTATES WS | 19 | 36 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2700992 | MILLER'S LODGE WS | 51 | 25 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701034 | APPLE AVE WS #02 | 18 | 75 | 1 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701036 | APPLE AVE WS #03 | 20 | 60 | 1 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701040 | MCCOY RD WS #05 | 24 | 72 | 1 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701046 | CAMPHORA APARTMENTS | 42 | 126 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701063 | RIVER RD WS #25 | 19 | 65 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701068 | IVERSON & JACKS APTS WS | 31 | 150 | 2 | NULL | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701221 | WASHINGTON SCHOOL WS | 2 | 250 | 1 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701254 | CARMEL RIVIERA MWC | 177 | 584 | 10 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701355 | PRINCES CAMP RESORT WS | 55 | 126 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701364 | PEDRAZZI MWC | 96 | 273 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701367 | TIERRA MEADOWS HOA WS | 21 | 63 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701403 | PINE ST WS #01 | 17 | 36 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701423 | ECHO VALLEY RD WS #05 | 16 | 45 | 2 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701498 | HARBOR VIEW WA | 29 | 75 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701503 | MESA DEL TORO MWC | 35 | 90 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701553 | POND-DEROSA OAKS WC | 75 | 216 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701570 | LOS CARNEROS MWA | 24 | 105 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701589 | SUNNY ACRES MWS | 15 | 45 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701633 | PARADISE RD WS #21 | 16 | 48 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701647 | GREEN ACRES WA | 20 | 50 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701658 | ARROYO CENTER WC | 60 | 130 | 2 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701676 | SAN LUCAS WD | 98 | 315 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701687 | VALLEY OAKS MHP WS | 46 | 120 | 1 | NULL | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701701 | BRADLEY-LOCKWOOD RD WS | 16 | 39 | 2 | NULL | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701731 | BRANDON CREEK MWS | 26 | 41 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701740 | BLUFFS WS | 44 | 120 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701742 | CALIFORNIA ORCHARD WS | 50 | 150 | 2 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701789 | HOLLY HILLS MWC | 27 | 108 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701800 | TULARCITOS MWC | 46 | 129 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701820 | CORDA RD WS | 19 | 60 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701822 | ROBLEY PROPERTY MWS | 33 | 92 | 2 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701888 | CACHAGUA MUTUAL WS (#4) | 24 | 55 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701897 | BERRY DR WS #02 | 19 | 50 | 1 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701898 | CLEAR RIDGE WA | 41 | 123 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701904 | SAN JERARDO COOP WS | 67 | 249 | 1 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701906 | LAKE SAN ANTONIO PARK WS | 30 | 54 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701918 | LOMAS DEL SOL MWS | 32 | 93 | 2 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701926 | MORO RD WS #09 | 65 | 210 | 3 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701935 | MOUNT TORO RANCHOS MWA | 19 | 45 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701956 | PIONEER PLACE MWS | 22 | 66 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2701959 | TIERRA VISTA MWC | 18 | 54 | 1 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702003 | VIERRA MEADOWS MWC | 25 | 65 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702026 | APRICOT LN WS | 16 | 53 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702055 | VIERRA KNOLLS MWC | 22 | 66 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702073 | SAN MIGUEL WS #22 | 31 | 93 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702110 | DELANY WC | 17 | 60 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702140 | WOODSIDE WA | 26 | 73 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702148 | ASOLEADO MWC | 36 | 101 | 5 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702180 | GRAVES SCHOOL WS | 2 | 56 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702254 | PACIFIC VALLEY SCHOOL WS | 5 | 25 | 1 | NULL | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702256 | NORTH SHORE ESTATES WS | 33 | 60 | 2 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702299 | POST RANCH INN WS | 58 | 286 | 5 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702317 | MISSION SCHOOL WS | 1 | 100 | 1 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702322 | CAPTAIN COOPER SCHOOL WS | 1 | 95 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702325 | FERNWOOD WS | 17 | 133 | 1 |  | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702328 | VENTANA BIG SUR INN WS | 26 | 193 | 4 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702374 | COUNTRYSIDE ESTATES MWC | 23 | 223 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702388 | ROYAL OAK PLACE WS | 20 | 60 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702405 | JENSEN MHP WS | 26 | 56 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702409 | EL CAMINO WC INC | 21 | 133 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702439 | WOODLAND HEIGHTS MWC | 37 | 57 | 2 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702490 | CENTRAL BAY HIGH SCHOOL WS | 1 | 70 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2702608 | THIMIO MWC | 21 | 60 | 1 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2710016 | LITTLE BEAR WATER COMPANY | 705 | 2327 | 3 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2710702 | FORT HUNTER LIGGETT | 160 | 5000 | 3 | No | MONTEREY | 0.3 | 1700 | 2210 | 2313.87
CA2800516 | TUCKER ACRES MUTUAL WATER CO. | 23 | 200 | 2 | No | NAPA | 0.3 | 1700 | 2210 | 2313.87
CA2800525 | LA TIERRA HEIGHTS MUTUAL | 19 | 67 | 2 | No | NAPA | 0.3 | 1700 | 2210 | 2313.87
CA2800527 | LINDA FALLS TERRACE MUTUAL | 17 | 35 | 1 | No | NAPA | 0.3 | 1700 | 2210 | 2313.87
CA2800531 | MOORE'S RESORT | 20 | 70 | 1 | No | NAPA | 0.3 | 1700 | 2210 | 2313.87
CA2800532 | VAILIMA ESTATES MUTUAL WATER | 15 | 25 | 2 | No | NAPA | 0.3 | 1700 | 2210 | 2313.87
CA2800593 | R RANCH AT THE LAKE | 16 | 28 | 3 | No | NAPA | 0.3 | 1700 | 2210 | 2313.87
CA2800847 | NVUSD: CARNEROS SCHOOL | 1 | 100 | 1 | No | NAPA | 0.3 | 1700 | 2210 | 2313.87
CA2800848 | NVUSD: MT. GEORGE SCHOOL | 1 | 100 | 1 | No | NAPA | 0.3 | 1700 | 2210 | 2313.87
CA2800970 | HOWELL MOUNTAIN SCHOOL | 2 | 100 | 2 | No | NAPA | 0.3 | 1700 | 2210 | 2313.87
CA2801080 | MILTON ROAD WATER COMPANY | 24 | 55 | 1 | No | NAPA | 0.3 | 1700 | 2210 | 2313.87
CA2900511 | SHADY LAKE WATER ASSOCIATION | 28 | 90 | 1 | No | NEVADA | 0 | 1700 | 1700 | 1779.9
CA2900529 | GOLD COUNTRY HOME PARK - WATER SYSTEM | 27 | 60 | 2 | No | NEVADA | 0 | 1700 | 1700 | 1779.9
CA2900530 | ROUGH & READY MOBILEHOME VILLAGE | 56 | 268 | 2 | No | NEVADA | 0 | 1700 | 1700 | 1779.9
CA2900531 | CREEKSIDE VILLAGE | 131 | 300 | 1 | No | NEVADA | 0 | 1700 | 1700 | 1779.9
CA2900535 | PLEASANT RIDGE SCHOOL | 4 | 120 | 1 | No | NEVADA | 0 | 1700 | 1700 | 1779.9
CA2900536 | CLEAR CREEK SCHOOL | 8 | 160 | 1 | No | NEVADA | 0 | 1700 | 1700 | 1779.9
CA2900541 | CHRISTIAN ENCOUNTER MINISTRIES | 16 | 35 | 1 | No | NEVADA | 0 | 1700 | 1700 | 1779.9
CA2900546 | SIERRA FRIENDS CENTER | 13 | 125 | 2 | No | NEVADA | 0 | 1700 | 1700 | 1779.9
CA2900548 | SIERRA ESTATES MUTUAL WATER COMPANY | 32 | 100 | 1 | No | NEVADA | 0 | 1700 | 1700 | 1779.9
CA2900578 | TWIN RIDGES GRIZZLY HILL SCHOOL | 11 | 125 | 1 | No | NEVADA | 0 | 1700 | 1700 | 1779.9
CA2900587 | MOUNTAIN VALLEY CHILD AND FAMILY SERVICE | 10 | 50 | 1 | No | NEVADA | 0 | 1700 | 1700 | 1779.9
CA2900593 | TWIN RIDGES OAK TREE SCHOOL | 8 | 120 | 2 | No | NEVADA | 0 | 1700 | 1700 | 1779.9
CA2901208 | DONNER TRAIL ELEMENTARY SCHOOL | 1 | 60 | 1 |  | NEVADA | 0 | 1700 | 1700 | 1779.9
CA3000519 | HYNES ESTATES MUTUAL WATER CO. | 42 | 139 | 2 | No | ORANGE | 0.3 | 1700 | 2210 | 2313.87
CA3000618 | LIBERTY PARK WATER ASSOCIATION | 27 | 89 | 1 | No | ORANGE | 0.3 | 1700 | 2210 | 2313.87
CA3100011 | AUBURN VALLEY COMMUNITY SERVICE DIS | 143 | 290 | 5 | No | PLACER | 0 | 1700 | 1700 | 1779.9
CA3100019 | NORTH EDEN VALLEY | 21 | 52 | 2 | No | PLACER | 0 | 1700 | 1700 | 1779.9
CA3100023 | AUBURN MOBILE HOME VILLAGE | 23 | 59 | 1 | No | PLACER | 0 | 1700 | 1700 | 1779.9
CA3100043 | GOLD HILL MOBILEHOME PARK | 32 | 75 | 1 |  | PLACER | 0 | 1700 | 1700 | 1779.9
CA3100061 | SIERRA MEADOWS APARTMENT | 28 | 52 | 1 | No | PLACER | 0 | 1700 | 1700 | 1779.9
CA3100069 | AUBURN RIDGE WOODS | 54 | 131 | 1 | No | PLACER | 0 | 1700 | 1700 | 1779.9
CA3100072 | LIVE OAK WALDORF SCHOOL | 1 | 200 | 1 | No | PLACER | 0 | 1700 | 1700 | 1779.9
CA3100083 | OPHIR ELEMENTARY SCHOOL WATER SYSTEM | 1 | 260 | 1 | No | PLACER | 0 | 1700 | 1700 | 1779.9
CA3100538 | ROSECREST MUTUAL | 15 | 31 | 1 | No | PLACER | 0 | 1700 | 1700 | 1779.9
CA3103310 | EMIGRANT GAP MUTUAL WATER CO. | 43 | 125 | 2 |  | PLACER | 0 | 1700 | 1700 | 1779.9
CA3107342 | LINCOLN HIGH SCHOOL FARM | 1 | 50 | 1 | No | PLACER | 0 | 1700 | 1700 | 1779.9
CA3110003 | FORESTHILL PUBLIC UTILITY DIST | 2032 | 6000 | 2 | No | PLACER | 0 | 1700 | 1700 | 1779.9
CA3110017 | SIERRA LAKES COUNTY WATER DIST | 825 | 185 | 1 | No | PLACER | 0 | 1700 | 1700 | 1779.9
CA3110042 | TAHOE SWISS VILLAGE UTILITY | 395 | 300 | 2 | No | PLACER | 0 | 1700 | 1700 | 1779.9
CA3110048 | PLACER CSA - SHERIDAN | 196 | 726 | 3 | No | PLACER | 0 | 1700 | 1700 | 1779.9
CA3200078 | FRCCSD OLD MILL RANCH | 23 | 32 | 1 |  | PLUMAS | 0 | 1700 | 1700 | 1779.9
CA3200079 | PUSD TAYLORSVILLE ELEMENTARY SCHOOL | 1 | 70 | 1 | NULL | PLUMAS | 0 | 1700 | 1700 | 1779.9
CA3200127 | ARLINGTON HEIGHTS MHP | 39 | 33 | 1 |  | PLUMAS | 0 | 1700 | 1700 | 1779.9
CA3200138 | MEADOW EDGE MHP | 31 | 53 | 4 | No | PLUMAS | 0 | 1700 | 1700 | 1779.9
CA3200148 | FEATHER RIVER RV & MHP | 21 | 700 | 2 | No | PLUMAS | 0 | 1700 | 1700 | 1779.9
CA3200155 | FRCCSD HOT SPRINGS | 17 | 25 | 1 |  | PLUMAS | 0 | 1700 | 1700 | 1779.9
CA3200188 | GREENHORN CREEK CSD | 136 | 280 | 2 | No | PLUMAS | 0 | 1700 | 1700 | 1779.9
CA3200189 | VALIVU ESTATES MHP | 19 | 54 | 1 | No | PLUMAS | 0 | 1700 | 1700 | 1779.9
CA3200195 | GREENHAVEN HOA | 18 | 38 | 1 | No | PLUMAS | 0 | 1700 | 1700 | 1779.9
CA3200215 | SCHRAMEL WATER SYSTEM | 1 | 100 | 1 |  | PLUMAS | 0 | 1700 | 1700 | 1779.9
CA3200510 | IVCSD CRESCENT MILLS | 78 | 258 | 1 | No | PLUMAS | 0 | 1700 | 1700 | 1779.9
CA3205001 | WALKER RANCH CSD | 1107 | 50 | 1 | No | PLUMAS | 0 | 1700 | 1700 | 1779.9
CA3205003 | GOLD MOUNTAIN CSD | 100 | 100 | 4 |  | PLUMAS | 0 | 1700 | 1700 | 1779.9
CA3210001 | IVCSD-GREENVILLE | 191 | 630 | 2 | No | PLUMAS | 0 | 1700 | 1700 | 1779.9
CA3210009 | CHESTER PUBLIC U.D. | 1209 | 2316 | 4 | No | PLUMAS | 0 | 1700 | 1700 | 1779.9
CA3210010 | HAMILTON BRANCH CSD | 616 | 1874 | 2 | N/A | PLUMAS | 0 | 1700 | 1700 | 1779.9
CA3301011 | STONE CREEK WATER CO. | 50 | 134 | 2 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301018 | ANZA PINES MOBILE HOME PARK | 47 | 150 | 3 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301028 | BALDY MOUNTAIN RANCH | 80 | 144 | 1 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301040 | RIVERDALE ESTATES | 186 | 300 | 1 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301045 | BLYTHE MOBILE HOME ESTATES | 25 | 35 | 1 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301107 | CARVER TRACT MUTUAL WATER COMP | 188 | 300 | 1 |  | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301209 | DESERT VIEW TRAILER PARK | 22 | 60 | 1 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301247 | ELMS MOBILE PARK | 47 | 100 | 1 |  | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301267 | FISHERMAN'S RETREAT | 172 | 402 | 1 |  | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301294 | GLEN IVY HOT SPRINGS | 49 | 653 | 1 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301330 | INDIAN OAKS TRAILER PARK | 63 | 90 | 1 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301355 | ANZA RV RESORT | 101 | 120 | 2 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301380 | SAINT ANTHONY TRAILER PARK | 68 | 340 | 1 |  | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301428 | BLYTHE - MESA RANCH | 189 | 561 | 2 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301482 | ORTEGA OAKS RV PARK&CAMPGROUND | 77 | 180 | 2 |  | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301491 | ALPINE VILLAGE | 60 | 198 | 5 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301511 | PINYON CREST HOA | 90 | 104 | 3 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301528 | OAK HAVEN ASSOCIATION | 36 | 92 | 3 |  | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301529 | RAMONA WATER COMPANY | 95 | 250 | 4 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301588 | ROYAL CARRIZO HOA | 20 | 25 | 2 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301630 | BLYTHE - HIDDEN BEACHES | 116 | 383 | 1 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301682 | TRAILS END MUTUAL WATER COMPANY | 34 | 52 | 1 |  | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301717 | VALLEY VIEW TRAILER PARK | 37 | 135 | 1 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301800 | STONEWOOD CANYON ESTATES | 26 | 40 | 1 |  | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301877 | BLOCK 77 WATER COMPANY | 18 | 50 | 1 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3301990 | AMEZCUA - GARCIA WATER | 113 | 316 | 1 |  | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3303003 | GALINDO HOUSING FACILITY | 38 | 50 | 1 |  | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3303035 | THERMAL PARK | 22 | 73 | 1 |  | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3303087 | VARGAS MHP/SAN JOSE COMMUNITY WS | 15 | 71 | 1 |  | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3310802 | CHUCKAWALLA VALLEY STATE PRISON | 1864 | 6507 | 4 | No | RIVERSIDE | 0.32 | 1700 | 2244 | 2349.468
CA3400103 | B & W RESORT MARINA | 37 | 100 | 2 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400107 | RIVER'S EDGE MARINA & RESORT | 83 | 150 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400121 | EL DORADO MOBILE HOME PARK | 128 | 256 | 2 |  | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400122 | EL DORADO WEST MHP | 128 | 172 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400130 | THE COURTLAND GROUP | 34 | 40 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400137 | LINCOLN CHAN-HOME RANCH | 19 | 33 | 2 |  | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400138 | LOCKE WATER WORKS CO [SWS] | 44 | 80 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400150 | DELTA CROSSING MHP | 22 | 30 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400155 | SEQUOIA WATER ASSOC | 18 | 54 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400169 | SPINDRIFT MARINA | 50 | 100 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400172 | TOKAY PARK WATER CO | 198 | 525 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400179 | MC CLELLAN MHP | 199 | 700 | 2 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400181 | LAGUNA DEL SOL INC | 112 | 470 | 2 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400191 | ELEVEN OAKS MOBILE HOME COMMUNITY | 136 | 262 | 3 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400192 | TUNNEL TRAILER PARK | 21 | 44 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400217 | HOMETOWN COLONIAL ESTATES LLC | 146 | 438 | 3 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400248 | FRANKLIN ELEMENTARY SCHOOL | 13 | 650 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400250 | PLEASANT GROVE ELEMENTARY SCHOOL | 10 | 185 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400251 | SIERRA ENTERPRISE ELEMENTARY SCHOOL | 13 | 430 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400253 | COSUMNES RIVER ELEMENTARY SCHOOL | 8 | 560 | 2 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400254 | DILLARD ELEMENTARY SCHOOL | 4 | 350 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400267 | BATES ELEMENTARY SCHOOL | 10 | 375 | 2 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400268 | WALNUT GROVE ELEMENTARY SCHOOL | 2 | 200 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400271 | ARCOHE ELEM SCHOOL - MAIN CAMPUS | 2 | 465 | 2 |  | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400273 | WILTON BIBLE CHURCH | 5 | 125 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400296 | SAC CITY MOBILE HOME COMMUNITY LP | 164 | 350 | 2 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400335 | HOLIDAY MOBILE VILLAGE | 115 | 200 | 2 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400391 | BRADSHAW CHRISTIAN SCHOOL | 8 | 935 | 1 |  | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400397 | LAGUNA VILLAGE RV PARK | 28 | 32 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400401 | PLANTATION MOBILE HOME PARK | 44 | 44 | 1 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3400433 | EDGEWATER MOBILE HOME PARK | 22 | 40 | 2 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3410026 | CALIFORNIA STATE FAIR | 269 | 650 | 4 | No | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3410033 | FLORIN COUNTY WATER DISTRICT | 2323 | 7831 | 10 |  | SACRAMENTO | 0.32 | 1700 | 2244 | 2349.468
CA3500505 | THOUSAND TRAILS SAN BENITO PRESERVE | 365 | 1025 | 3 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500509 | TRES PINOS CWD | 121 | 350 | 1 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500510 | MCMAHON ROAD MUTUAL WATER COMPANY | 32 | 102 | 1 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500511 | CASA DE FRUTA ORCHARDS | 20 | 53 | 1 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500521 | SOUTHSIDE ELEMENTARY SCHOOL | 2 | 300 | 1 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500524 | RIVER OAKS R.V.P. | 15 | 52 | 1 |  | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500527 | VALENZUELA WATER SYSTEM | 17 | 55 | 1 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500549 | ROSA MORADA MUTUAL WATER COMPANY | 21 | 69 | 2 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500552 | VENTURE ESTATES MWC | 18 | 60 | 1 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500556 | MISSION FARM R.V. PARK | 173 | 110 | 1 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500571 | SAN BENITO HIGH SCHOOL | 61 | 3310 | 1 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500575 | SPRINGWOOD ESTATES MWC | 15 | 50 | 1 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500579 | VINEYARD ESTATES MWC | 26 | 90 | 1 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500581 | RANCHO SAN JOAQUIN MWC | 30 | 96 | 1 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500801 | WILLOW GROVE UNION ELEMENTARY SCHOOL | 4 | 25 | 1 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500823 | BEST ROAD MWC | 48 | 133 | 2 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500836 | BETABEL RV RESORT | 176 | 49 | 1 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500905 | ANZAR HIGH SCHOOL | 9 | 328 | 1 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500910 | DUNNEVILLE ESTATES CSA #50 | 30 | 120 | 2 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3500911 | CREEKBRIDGE MUTUAL WATER COMPANY | 22 | 69 | 1 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3510002 | SAN JUAN BAUTISTA, CITY OF | 834 | 2335 | 2 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3510006 | MISSION OAKS MOBILE HOME PARK | 238 | 550 | 1 | No | SAN BENITO | 0.3 | 1700 | 2210 | 2313.87
CA3600008 | APPLE VALLEY FOOTHILL CWD | 218 | 729 | 2 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600009 | APPLE VALLEY HEIGHTS CWD | 296 | 986 | 2 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600070 | CENTER WATER CO | 50 | 662 | 2 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600071 | CHAMISAL MWC | 29 | 63 | 1 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600088 | DESERT DAWN MWC | 45 | 150 | 2 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600089 | DESERT SPRINGS MWC | 79 | 325 | 2 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600107 | FOREST PARK MWC | 93 | 415 | 4 |  | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600155 | RIVER RANCH MHP | 136 | 176 | 2 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600156 | LUCERNE VALLEY MWC | 69 | 275 | 2 |  | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600158 | LYTLE SPRINGS WC | 141 | 475 | 2 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600166 | MILL CREEK MSC | 72 | 315 | 2 | N/A | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600184 | NORTH SHORE MWC | 32 | 25 | 2 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600187 | OLIVE DELL RANCH | 100 | 350 | 2 |  | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600222 | JUNIPER RIVIERA CWD | 250 | 441 | 3 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600258 | SKY FOREST MWC | 159 | 605 | 2 |  | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600262 | SNOWCREST HEIGHTS IMP ASSOC | 125 | 600 | 3 | N/A | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600297 | GORDON ACRES WATER CO | 66 | 200 | 2 |  | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600301 | STRAWBERRY LODGE MWC | 137 | 640 | 1 |  | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600306 | THUNDERBIRD CWD | 302 | 997 | 3 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600308 | FREEDOM ACRES THE RESORT | 100 | 500 | 2 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600385 | BROOKSIDE MHP | 19 | 65 | 1 |  | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600386 | FOOTHILL ESTATES MHP | 33 | 135 | 1 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600388 | DESERT VIEW MOBILE PARK | 28 | 130 | 2 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600397 | MOSS MOBILE MANOR | 43 | 290 | 1 |  | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600400 | APPLE VALLEY VILLAGE MHE | 93 | 180 | 1 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600504 | KNOLL ENTERPRISES | 25 | 500 | 3 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600785 | LAKE JODIE WATER SYSTEM | 50 | 250 | 2 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3600790 | NEWBERRY ELEMENTARY SCHOOL | 2 | 255 | 1 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3601015 | IRONWOOD CAMP | 74 | 1000 | 2 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3601036 | CALICO LAKE HOMEOWNERS | 56 | 150 | 2 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3601045 | BEAR VALLEY MHP | 98 | 150 | 2 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3601179 | EL MIRAGE SCHOOL | 9 | 50 | 2 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3610022 | DWP - FAWNSKIN | 724 | 469 | 5 |  | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3610026 | SBDNO COUNTY SERVICE AREA 70 CEDAR GLEN | 342 | 1236 | 2 | N/A | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3610032 | NEEDLES, CITY OF | 1706 | 5183 | 4 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3610046 | VALLEY VIEW PARK MWC | 218 | 499 | 3 | No | SAN BERNARDINO | 0.3 | 1700 | 2210 | 2313.87
CA3700018 | CAMPO ELEMENTARY SCHOOL | 3 | 300 | 2 |  | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3700041 | BARRETT LAKE MH AND RV LLC | 58 | 150 | 2 | No | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3700071 | HEAVENLY OAKS | 102 | 300 | 2 | No | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3700073 | H & J WATER COMPANY | 39 | 50 | 1 | No | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3700117 | MOUNTAIN EMPIRE HIGH SCHOOL | 12 | 1000 | 2 |  | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3700118 | CAMP LOCKETT MIDDLE SCHOOL | 4 | 150 | 1 |  | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3700291 | OCOTILLO OASIS, LLC | 55 | 100 | 3 | NULL | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3700422 | LAGUNA MOUNTIAN MUTUAL WATER CO. | 28 | 100 | 1 |  | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3700866 | DEL DIOS MUTUAL WATER COMPANY | 150 | 330 | 3 | No | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3700900 | LAKE HENSHAW RESORT INC. | 101 | 300 | 2 | No | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3700918 | RANCHO SANTA TERESA MW CO. | 37 | 95 | 2 |  | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3700922 | LIVE OAK SPRINGS WATER SYSTEM | 94 | 300 | 1 | No | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3700924 | LAKE MORENA VIEWS MWC | 123 | 360 | 4 | No | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3700962 | OAKVALE PARK | 70 | 100 | 3 | No | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3700963 | POTRERO ELEMENTARY SCHOOL | 19 | 300 | 1 |  | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3701005 | SPENCER VALLEY SCHOOL DISTRICT | 4 | 40 | 1 | No | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3701010 | WARNER UNIFIED SCHOOL DISTRICT | 15 | 250 | 3 | No | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3701184 | BUTTERFIELD RANCH | 75 | 350 | 1 |  | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3701341 | QUIET OAKS MOBILE HOME PARK | 45 | 120 | 1 | No | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3701780 | RICHARDSON BEARDSLEY PARK INC. | 20 | 28 | 2 | No | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3702364 | CLOVER FLAT ELEMENTARY SCHOOL | 5 | 160 | 1 |  | SAN DIEGO | 0.32 | 1700 | 2244 | 2349.468
CA3900505 | FARMINGTON WATER COMPANY | 78 | 270 | 2 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900569 | EL RIO MOBILE HOME PARK | 28 | 60 | 2 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900579 | CENTURY MOBILE HOME PARK | 19 | 50 | 1 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900586 | B&G MOBILE HOME PARK LLC WS | 22 | 50 | 1 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900607 | COUNTRY SQUIRE MOBILE ESTATES & WATER SY | 49 | 64 | 1 |  | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900624 | IL VINETO | 83 | 160 | 2 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900637 | BIG WHEEL MOBILE HOME PARK | 63 | 120 | 2 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900649 | GLENWOOD MOBILE HOME PARK | 50 | 100 | 1 |  | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900653 | ISLANDER MARINA | 73 | 150 | 2 |  | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900661 | MAPACHE TRAILER PARK | 99 | 275 | 1 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900682 | LOCKEFORD MOBILE HOME PARK WTR SYS | 43 | 100 | 1 |  | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900705 | FINNLEES TRAILER PARK | 26 | 55 | 1 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900719 | MOKELUMNE MOBILE SENIOR PARK | 25 | 55 | 1 |  | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900721 | WOODBRIDGE MOBILE ESTATES | 37 | 110 | 1 |  | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900732 | V & P TRAILER COURT WATER SYSTEM | 15 | 35 | 1 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900733 | COUNTRY CLUB VISTA MUTUAL WATER CO | 31 | 75 | 1 |  | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900755 | SHADY REST TRAILER COURT | 49 | 120 | 1 |  | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900756 | LINDEN USD-GLENWOOD SCHOOL | 1 | 100 | 1 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900757 | LINDEN USD-WATERLOO ELEMENTARY | 1 | 225 | 1 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900762 | RIVERSIDE MOBILE HOME PARK | 58 | 55 | 2 |  | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900831 | ARBOR MOBILE HOME PARK WS | 173 | 340 | 1 |  | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900835 | WAYSIDE MOTEL APARTMENTS WTR SYS | 25 | 70 | 1 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900964 | SAHARA MOBILE COURT | 162 | 300 | 1 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900978 | SJ COUNTY-REDWOOD SCHOOL | 1 | 83 | 1 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3900993 | NEW JERUSALEM SCHOOL | 1 | 210 | 1 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3901031 | 132 INVESTMENTS WATER SYSTEM | 93 | 100 | 1 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3901074 | TWIN OAKS MOBILE PARK | 85 | 255 | 2 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3901081 | MOBILE VILLAS TRAILER PARK | 36 | 130 | 2 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3901114 | KING ISLAND TRAILER PARK WATER SYSTEM | 76 | 200 | 1 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3901325 | RIPON CHRISTIAN SCHOOLS | 1 | 900 | 1 |  | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3902136 | LINDEN USD-CHARTVILLE SCHOOL | 1 | 40 | 1 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3910018 | SAN JOAQUIN RIVER CLUB INC | 385 | 600 | 2 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA3910020 | STOCKTON VERDE MOBILE HOME PARK | 293 | 712 | 2 | No | SAN JOAQUIN | 0 | 1700 | 1700 | 1779.9
CA4000200 | BASSI RANCH MUTUAL WATER CO. | 24 | 85 | 3 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000214 | BARON CANYON MUTUAL WATER CO. | 25 | 81 | 3 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000501 | HALCYON WATER SYSTEM | 46 | 105 | 1 | No | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000506 | WOODLAND PARK MUTUAL WATER CO | 162 | 534 | 2 | No | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000507 | GARDEN FARMS C.W.D. | 107 | 240 | 3 | NULL | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000563 | HIGUERA APARTMENTS | 24 | 30 | 1 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000631 | ALMIRA WATER ASSOCIATION | 20 | 40 | 1 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000637 | COUNTRY HILLS ESTATES | 20 | 60 | 2 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000648 | KEN MAR GARDENS | 45 | 84 | 1 | No | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000649 | LOS ROBLES MOBILE HOME ESTATES | 160 | 420 | 3 | No | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000653 | RANCHO COLINA MOBILE HOME PARK | 127 | 250 | 3 | No | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000654 | RESTHAVEN MOBILE HOME PARK | 47 | 75 | 2 | No | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000660 | BEAR VALLEY WATER COMPANY | 17 | 45 | 5 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000675 | BRANCH ELEMENTARY SCHOOL | 1 | 500 | 1 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000693 | CRESTON ELEMENTARY SCHOOL | 1 | 100 | 2 | No | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000705 | LAGUNA NEGRA MUTUAL WATER CO. | 29 | 80 | 2 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000732 | CARRISA PLAINS ELEMENTARY | 1 | 65 | 1 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000749 | TERRA DE ORO WATER COMPANY | 17 | 38 | 2 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000750 | RIM ROCK WATER COMPANY | 25 | 55 | 2 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000767 | SANTA LUCIA SCHOOL | 1 | 52 | 1 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000774 | PLEASANT VALLEY ELEMENTARY | 1 | 100 | 2 | No | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000775 | MUSTANG SPRINGS MUTUAL WATER | 16 | 30 | 1 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000802 | SANTA YSABEL RANCH MWC | 151 | 238 | 2 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000803 | RANCHO SALINAS MBWC | 20 | 50 | 2 | No | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000805 | CALLENDER GROVE MUTUAL WATER | 37 | 30 | 2 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000808 | MONTE SERENO MUTUAL BENEFIT WATER | 26 | 60 | 2 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000815 | LAS VENTANAS RANCH | 33 | 108 | 2 |  | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4000834 | ANZA VINEYARD ESTATES MUTUAL WATER CO | 16 | 60 | 3 | NULL | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4010081 | WOODLANDS DEVELOPMENT | 1276 | 2918 | 3 | No | SAN LUIS OBISPO | 0.3 | 1700 | 2210 | 2313.87
CA4100513 | PESCADERO HIGH SCHOOL | 1 | 192 | 1 | No | SAN MATEO | 0.32 | 1700 | 2244 | 2349.468
CA4100533 | SKYLONDA MUTUAL | 154 | 420 | 3 | No | SAN MATEO | 0.32 | 1700 | 2244 | 2349.468
CA4100538 | CAMP JONES GULCH | 65 | 357 | 2 | No | SAN MATEO | 0.32 | 1700 | 2244 | 2349.468
CA4110010 | MONTARA WATER AND SANITARY DISTRICT | 1673 | 5289 | 12 | No | SAN MATEO | 0.32 | 1700 | 2244 | 2349.468
CA4110012 | CUESTA LA HONDA GUILD INC | 297 | 832 | 1 | No | SAN MATEO | 0.32 | 1700 | 2244 | 2349.468
CA4200619 | SANTA YNEZ RANCHO ESTATES | 92 | 304 | 3 |  | SANTA BARBARA | 0.3 | 1700 | 2210 | 2313.87
CA4200693 | ELLWOOD MUTUAL WATER COMPANY | 56 | 186 | 2 | No | SANTA BARBARA | 0.3 | 1700 | 2210 | 2313.87
CA4200747 | VISTA DE LAS CRUCES | 2 | 50 | 3 |  | SANTA BARBARA | 0.3 | 1700 | 2210 | 2313.87
CA4200814 | JONATA HOMEOWNERS ASSOCIATION | 16 | 45 | 1 | NULL | SANTA BARBARA | 0.3 | 1700 | 2210 | 2313.87
CA4200827 | SANTA YNEZ ROBLAR MOBILE HOME PARK | 19 | 25 | 1 |  | SANTA BARBARA | 0.3 | 1700 | 2210 | 2313.87
CA4200833 | BONITA SCHOOL | 1 | 589 | 1 |  | SANTA BARBARA | 0.3 | 1700 | 2210 | 2313.87
CA4200837 | RANCHO YNECITA | 39 | 129 | 3 |  | SANTA BARBARA | 0.3 | 1700 | 2210 | 2313.87
CA4200842 | SAINT MARIE MOBILE HOME PARK | 80 | 315 | 1 | No | SANTA BARBARA | 0.3 | 1700 | 2210 | 2313.87
CA4200870 | CASMALIA COMMUNITY SERVICES DISTRICT | 53 | 234 | 1 | N/A | SANTA BARBARA | 0.3 | 1700 | 2210 | 2313.87
CA4200879 | CUYAMA ELEMENTARY SCHOOL | 1 | 250 | 1 |  | SANTA BARBARA | 0.3 | 1700 | 2210 | 2313.87
CA4200918 | LOS PRIETOS COMPLEX | 39 | 845 | 2 | No | SANTA BARBARA | 0.3 | 1700 | 2210 | 2313.87
CA4300525 | MELODY WOODS WATER COMPANY | 51 | 168 | 2 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300543 | WEST SAN MARTIN WATER WORKS INC | 317 | 1173 | 3 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300567 | BURCHELL ROAD WATER ASSOCIATION | 27 | 132 | 2 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300571 | SULLIVAN MUTUAL WATER | 16 | 53 | 1 |  | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300573 | GREEN ACRES MUTUAL WATER | 19 | 53 | 2 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300575 | TWIN VALLEY INC | 96 | 317 | 5 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300577 | RANCHO ROBLES MUTUAL WATER COMPANY | 37 | 103 | 3 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300578 | ANGELO LANE WATER COMPANY | 15 | 52 | 1 |  | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300581 | VELLADAO MOBILE HOME PARK | 27 | 75 | 1 |  | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300593 | MORGAN HILL USD-MACHADO SCHOOL | 1 | 60 | 1 |  | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300603 | OAK DELL PARK | 53 | 100 | 1 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300605 | GILROY USD-RUCKER SCHOOL | 1 | 688 | 1 |  | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300610 | ANCHORPOINT CHRISTIAN SCHOOL | 1 | 167 | 1 |  | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300611 | CASA DE FRUTA WATER SYSTEM | 37 | 250 | 2 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300615 | THOUSAND TRAILS - MORGAN HILL | 320 | 508 | 1 |  | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300637 | LOS RANCHOS DE UVAS WATER COMPANY | 21 | 58 | 3 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300638 | SAN MARTIN FOOTHILLS WATER COMPANY | 44 | 145 | 2 |  | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300721 | LOMA PRIETA JUSD-LOMA PRIETA SCHOOL | 8 | 560 | 3 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300740 | MOUNTAIN SPRINGS MUTUAL WATER COMPANY | 18 | 37 | 1 |  | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300760 | SANTA TERESA MEADOWS WATER COMPANY | 23 | 68 | 2 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300779 | LAKESIDE SD-LAKESIDE SCHOOL | 4 | 127 | 1 |  | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300792 | ABORN HEIGHTS WATER MUTUAL ASSOCIATION | 19 | 45 | 1 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300912 | MECCHI WATER COMPANY | 27 | 104 | 1 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300924 | PARKWAY LAKES RV PARK | 121 | 250 | 1 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300979 | QUAIL CREEK ESTATES MUTUAL WATER COMPANY | 39 | 55 | 2 |  | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300994 | COYOTE VALLEY RV RESORT | 129 | 500 | 1 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300996 | VALLEY VIEW RANCHES | 16 | 45 | 1 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4300999 | UVAS PINES RV PARK | 43 | 86 | 1 | No | SANTA CLARA | 0.32 | 1700 | 2244 | 2349.468
CA4400557 | ST FRANCIS TRACT WATER SYSTEM | 29 | 118 | 1 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400572 | FERN GROVE WATER CLUB | 67 | 182 | 2 |  | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400582 | PINE TREE LANE MUTUAL WATER CO | 36 | 80 | 1 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400585 | RIDGEVIEW ESTATES MWC | 18 | 45 | 1 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400598 | PURESOURCE WATER, INC | 77 | 200 | 2 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400604 | BRACKEN BRAE COUNTRY CLUB | 24 | 54 | 1 |  | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400605 | CRESTWOOD HEIGHTS WATER ASSN | 45 | 126 | 2 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400613 | LAS COLINAS ROAD & WATER ASSN | 24 | 70 | 1 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400624 | RANCHO CORRALITOS | 31 | 60 | 2 |  | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400625 | VISTA ROBLES ASSOCIATION | 19 | 50 | 2 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400631 | LAS CUMBRES MUTUAL WATER CO | 125 | 402 | 4 |  | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400642 | CATHEDRAL WOOD MUTUAL WATER COMPANY | 20 | 60 | 1 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400645 | HIDDEN MEADOW MUTUAL WATER CO | 18 | 45 | 2 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400652 | CATHEDRAL HILLS MWC, INC | 25 | 60 | 2 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400665 | MEADOWRIDGE MUTUAL WATER CO | 18 | 42 | 2 |  | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400692 | ALLAN LANE WATER ASSOCIATION | 17 | 68 | 1 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400723 | MISSION SPRINGS CONFERENCE CENTER | 141 | 1310 | 2 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400750 | APTOS HIGH SCHOOL | 6 | 1925 | 1 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400751 | BONNY DOON SCHOOL | 10 | 160 | 1 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400754 | MONTE VISTA CHRISTIAN SCHOOL | 43 | 1083 | 2 |  | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400755 | MONTEREY BAY ACADEMY | 78 | 400 | 2 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400756 | MOUNTAIN ELEMENTARY SCHOOL | 1 | 250 | 1 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400757 | ALIANZA CHARTER SCHOOL/WCSA | 3 | 967 | 1 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400758 | RENAISSANCE HIGH SCHOOL | 2 | 250 | 1 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400763 | BUENA VISTA MIGRANT CENTER | 140 | 455 | 1 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4400875 | SANTA CRUZ WALDORF SCHOOL | 2 | 190 | 2 | No | SANTA CRUZ | 0.3 | 1700 | 2210 | 2313.87
CA4500007 | VERDE VALE WATER COMPANY | 108 | 356 | 2 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500009 | CORTLAND PINES MUTUAL WATER CO | 33 | 92 | 1 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500012 | CASCADE RACQUET CLUB MUTUAL WATER | 27 | 89 | 1 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500018 | SALT CREEK SUMMER HOMES | 47 | 151 | 1 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500041 | ANDERSON UNION HIGH SCHOOL | 2 | 700 | 2 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500054 | BALLS FERRY FISHING RESORT | 75 | 204 | 1 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500062 | LONE TREE MOBILE HOME PARK | 26 | 85 | 1 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500081 | LAZY LANDING MOBILE HOME PARK | 110 | 250 | 2 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500082 | MIDWAY MOBILEHOME PARK | 29 | 50 | 1 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500089 | PINE RIDGE PARK ESTATES | 27 | 44 | 1 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500092 | RIVER BREEZE MOBILE HOME PARK | 32 | 87 | 1 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500093 | RED HILL MOBILEHOME PARK | 24 | 35 | 2 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500094 | RIVERLAND MOBILEHOME PARK | 93 | 274 | 2 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500098 | ANDERSON MOBILE HOME PARK | 21 | 70 | 1 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500101 | LAKE SHASTA PINES RV PARK & CAMPGROUND | 50 | 121 | 2 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500102 | NORTH REDDING RV VILLAGE | 100 | 78 | 2 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500104 | SUNRISE MOBILEHOME PARK | 16 | 35 | 1 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500107 | ZUFALL'S MOBILEHOME PARK | 78 | 96 | 3 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500160 | PACHECO ELEMENTARY SCHOOL | 2 | 400 | 1 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500161 | PRAIRIE ELEMENTARY SCHOOL | 1 | 375 | 1 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500163 | JUNCTION SCHOOL DISTRICT | 2 | 700 | 2 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500180 | MILLVILLE ELEMENTARY SCHOOL | 2 | 110 | 1 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500181 | WHITMORE UNION ELEM SCHOOL | 2 | 35 | 2 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500183 | BLACK BUTTE ELEMENTARY SCHOOL | 1 | 250 | 1 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500190 | OAK RUN ELEMENTARY SCHOOL | 1 | 125 | 1 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500193 | VERDE VALE ELEMENTARY SCHOOL | 1 | 290 | 1 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500194 | VILLAGE GREEN | 32 | 90 | 1 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500195 | STARLITE PINES MUTUAL WATER CO INC | 165 | 510 | 2 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500203 | RAPID RIVER MOBILEHOME PARK | 44 | 92 | 1 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500210 | LASSEN PINES MUTUAL WATER CO INC | 198 | 600 | 3 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500214 | WEST VALLEY HIGH SCHOOL | 1 | 850 | 1 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500219 | CREEKSIDE MOBILEHOME PARK | 41 | 85 | 2 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500235 | WOODRIDGE MUTUAL WATER CO | 71 | 187 | 3 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500246 | EL RIO ESTATES | 155 | 434 | 2 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500247 | WEST COTTONWOOD APARTMENTS | 17 | 35 | 1 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500254 | ANDERSON PARK VILLAGE | 45 | 112 | 1 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500303 | TUCKER OAKS EAST WATER DISTRICT | 34 | 95 | 1 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4500322 | BLACK BUTTE JUNIOR HIGH SCHOOL | 1 | 100 | 1 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4510002 | MOUNTAIN GATE C.S.D. | 669 | 2227 | 3 | No | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4510007 | COTTONWOOD COUNTY WATER DIST. | 1226 | 3316 | 5 |  | SHASTA | 0 | 1700 | 1700 | 1779.9
CA4700521 | SISKIYOU CO.SERVICE AREA #5/CARRICK | 58 | 92 | 1 |  | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4700523 | GRENADA SANITARY DISTRICT | 103 | 289 | 1 |  | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4700531 | TENNANT C.S.D. | 102 | 75 | 1 | No | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4700541 | CHATEAU SHASTA MOBILE HOME & RV PARK | 63 | 55 | 3 | No | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4700542 | ABRAMS LAKE MOBILE ESTATES | 86 | 135 | 1 |  | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4700559 | BUTTEVILLE UNION SCHOOL | 2 | 165 | 1 |  | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4700582 | GAZELLE SCHOOL | 1 | 60 | 1 | No | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4700585 | JUNCTION ELEMENTARY SCHOOL | 1 | 40 | 1 |  | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4700591 | DELPHIC ELEMENTARY SCHOOL | 1 | 50 | 1 | No | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4700626 | COVE MOBILE VILLA | 47 | 105 | 1 | No | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4700627 | JUNIPER CREEK ESTATES | 51 | 130 | 1 |  | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4700630 | SHASTA VIEW HEIGHTS OWNERS ASSOCIATION | 24 | 50 | 1 | No | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4700686 | SUN MOUNTAIN M.W.C. | 31 | 55 | 1 | No | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4700803 | SHADOW MOUNTAIN MHP | 73 | 100 | 3 |  | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4700880 | SISKIYOU LAKE HIGHLANDS MWC | 83 | 539 | 3 | No | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4710009 | WEED, CITY OF | 1110 | 2963 | 4 |  | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4710010 | TULELAKE, CITY OF | 471 | 1000 | 2 | No | SISKIYOU | 0 | 1700 | 1700 | 1779.9
CA4800531 | VACA VILLA APARTMENTS | 40 | 60 | 1 | No | SOLANO | 0.3 | 1700 | 2210 | 2313.87
CA4800561 | SNUG HARBOR RV LP | 110 | 125 | 2 | No | SOLANO | 0.3 | 1700 | 2210 | 2313.87
CA4800564 | HIDDEN ACRES TRAILER VILLA | 54 | 80 | 3 | No | SOLANO | 0.3 | 1700 | 2210 | 2313.87
CA4800753 | VINEYARD RV PARK | 360 | 365 | 2 | No | SOLANO | 0.3 | 1700 | 2210 | 2313.87
CA4900510 | SOUTH CLOVERDALE WATER COMPANY | 39 | 90 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900512 | HAPPY ACRES MUTUAL BENEFIT WATER SYSTEM | 79 | 260 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900533 | MORTON'S WARM SPRINGS / SONOMA SPRINGS | 21 | 59 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900536 | OCCIDENTAL COMMUNITY SERVICES DISTRICT | 109 | 383 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900543 | SONOMA COUNTY CSA 41-SALMON CREEK | 99 | 427 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900546 | HAWKINS WATER CO-CAL WATER SERVICE (PUC) | 51 | 127 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900551 | MELITA HEIGHTS MUTUAL WATER COMPANY | 25 | 64 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900561 | WILLOWSIDE MUTUAL WATER COMPANY | 160 | 350 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900568 | VALLEY FORD WATER ASSOCIATION | 23 | 61 | 3 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900577 | RIO LINDO ADVENTIST ACADEMY | 54 | 358 | 3 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900584 | TIMBER COVE COUNTY WATER DISTRICT | 189 | 271 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900587 | BRAND WATER COMPANY | 34 | 112 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900599 | RANDAL'S RANCHETTE MUTUAL WATER COMPANY | 29 | 100 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900600 | RINCON VALLEY MOBILE ESTATES | 230 | 460 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900603 | RIEBLI MUTUAL WATER COMPANY | 47 | 150 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900605 | MARK WEST ACRES MWC | 22 | 61 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900608 | SIX ACRES WATER COMPANY | 22 | 66 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900637 | MAGIC MOUNTAIN MUTUAL WATER COMPANY | 67 | 100 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900640 | SONOMA COUNTY MUTUAL WATER COMPANY | 18 | 40 | 1 |  | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900641 | SUNRISE MOUNTAIN MUTUAL WATER COMPANY | 51 | 100 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900646 | ALEXANDER VALLEY ACRES WATER COMPANY | 16 | 37 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900665 | RUSSIAN RIVER MUTUAL WATER CO. | 30 | 84 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900667 | COLLEGE PARK MUTUAL WATER COMPANY | 72 | 237 | 3 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900669 | WENDELL LANE MUTUAL WATER COMPANY | 25 | 82 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900673 | ATHENA TERRACE MUTUAL WATER COMPANY | 23 | 74 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900674 | PINE HILL TERRACE MOBILE HOME PARK | 23 | 27 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900675 | ROSELAND MOBILE HOME PARK | 70 | 130 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900679 | FORT ROSS SCHOOL DISTRICT | 2 | 100 | 1 |  | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900693 | BELLEVUE UNION SCH DIST-BELLEVUE SCHOOL | 2 | 591 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900694 | WRIGHT ELEMENTARY SCHOOL | 11 | 500 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900695 | NORTHWEST PREP | 1 | 325 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900699 | OLIVET ELEMENTARY SCHOOL | 6 | 400 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900703 | OAK GROVE SCHOOL | 7 | 500 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900704 | ALEXANDER VALLEY UNION SCHOOL DISTRICT | 5 | 200 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900705 | GEYSERVILLE NEWTECH ACADEMY | 1 | 200 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900707 | TWIN HILLS SCHOOL DIST-TWIN HILLS SCHOOL | 2 | 400 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900708 | GRAVENSTEIN SCHOOL DISTRICT-GRAVENSTEIN | 7 | 398 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900711 | GRAVENSTEIN SCHOOL DISTRICT-HILLCREST | 1 | 289 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900714 | LIBERTY SCHOOL | 3 | 225 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900719 | WEST SIDE UNION SCHOOL DISTRICT | 5 | 200 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900720 | MOBILE HOME ESTATES | 150 | 210 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900721 | COLONIAL PARK | 194 | 342 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900723 | SHAMROCK MOBILE HOME PARK | 127 | 188 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900728 | EVERGREEN MOBILE ESTATES | 23 | 70 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900739 | DUNHAM SCHOOL | 2 | 200 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900785 | NOEL HEIGHTS-CAL WATER SERVICE (PUC) | 50 | 137 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900787 | PLAZA MOBILE HOME PARK | 71 | 125 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900788 | EL CRYSTAL MOBILE HOME PARK | 57 | 130 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900789 | BLUE SPRUCE MOBILE HOME PARK | 56 | 90 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900792 | WAYSIDE GARDENS MOBILE HOME PARK | 50 | 75 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900793 | VINEHILL VISTAS MUTUAL WATER COMPANY | 29 | 42 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900794 | SUNSET PARK COMMUNITY | 42 | 141 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900795 | STONEGATE MOBILE HOME PARK | 75 | 100 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900796 | SANTA ROSA MOBILE ESTATES | 141 | 420 | 3 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900797 | NORTH STAR MOBILE HOME PARK | 79 | 75 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900799 | EL PORTAL MOBILE ESTATES | 122 | 200 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900843 | SONOMA RANCH MUTUAL WATER COMPANY | 54 | 178 | 4 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900846 | ROLLING OAKS ROAD ASSOCIATION | 16 | 25 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900850 | BODEGA WATER COMPANY | 38 | 77 | 3 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900901 | SOBRE VISTA WATER COMPANY | 26 | 80 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900905 | MARK WEST MEADOWS MUTUAL WATER | 15 | 25 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900907 | SUMMERFIELD WALDORF SCHOOL | 13 | 299 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900913 | ROBIN WAY WATER SYSTEM | 20 | 66 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900943 | ALLIANCE REDWOODS CONFERENCE GROUNDS | 73 | 418 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4900945 | PRESENTATION SCHOOL | 4 | 200 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4901071 | BOULEVARD HEIGHTS MUTUAL WATER | 18 | 60 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4901156 | WILLOWSIDE SCHOOL | 5 | 460 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4901168 | SALMON CREEK MIDDLE SCHOOL | 14 | 300 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4901190 | LIETO WATER SYSTEM (REACH CHARTR SCHOOL) | 2 | 134 | 1 |  | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4901215 | PLUMFIELD ACADEMY (OCCIDENTAL RD.) | 1 | 30 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4901221 | GRATON MUTUAL (GREEN VALLEY HOA) | 16 | 50 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4901246 | DOWNTOWN GRATON MUTUAL WATER SYSTEM | 24 | 118 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4901309 | HILTON MUTUAL WATER COMPANY | 16 | 100 | 1 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4901346 | DELORES LANE WATER SYSTEM | 17 | 56 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4901355 | TERRACE VIEW WATER SYSTEM | 16 | 60 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4901381 | LICHAU HYLANDS MUTUAL WATER COMPANY | 20 | 56 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4901445 | JAMES COURT WATER SYSTEM | 40 | 205 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4910018 | ARMSTRONG VALLEY-CAL WATER SERVICE (PUC) | 269 | 424 | 2 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA4910026 | ODD FELLOWS RECREATION CLUB | 268 | 309 | 3 | No | SONOMA | 0.3 | 1700 | 2210 | 2313.87
CA5000013 | OID #45 | 51 | 144 | 2 |  | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000014 | OID #46 - SUNSET OAKS | 79 | 269 | 2 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000015 | OID #22 - WILLIAMS TRACT | 53 | 150 | 1 |  | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000016 | OID #41 - MOUNTAIN VIEW | 42 | 147 | 2 |  | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000019 | RIVERDALE PARK TRACT CSD | 182 | 610 | 1 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000048 | LAZY B MOBILEHOME PARK | 49 | 125 | 2 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000054 | MORNINGSIDE MOBILEHOME PARK | 49 | 67 | 2 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000055 | OLIVE LANE MOBILEHOME PARK | 51 | 153 | 2 |  | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000058 | FISHERMAN'S BEND MHP | 66 | 120 | 1 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000061 | MARTIN'S MOBILE HOME COURT | 20 | 60 | 1 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000067 | TULLY MOBILE ESTATES | 15 | 40 | 1 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000071 | TWIN CYPRESS MOBILE HOME PARK | 45 | 112 | 1 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000080 | COUNTRY WESTERN MOBILE HOME PARK | 55 | 90 | 1 |  | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000095 | SUNRISE VILLAGE MHP | 103 | 339 | 3 |  | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000099 | DEL RIO EAST HOA WATER SYSTEM | 55 | 110 | 2 |  | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000101 | CHATOM SCHOOL (EH) | 1 | 500 | 1 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000109 | CERES UNIFIED/WESTPORT SCHOOL | 1 | 450 | 1 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000133 | HART- RANSOM UNION SCHOOL & DISTRICT | 4 | 650 | 1 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000155 | ROBERTS FERRY SCHOOL CAFETERIA | 2 | 100 | 1 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000218 | COUNTRY VILLA APTS | 23 | 60 | 1 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000255 | MOUNTAIN VIEW ELEMENTARY SCHOOL | 1 | 364 | 2 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000274 | PARADISE SCHOOL | 4 | 152 | 1 |  | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000295 | SHILOH SCHOOL DISTRICT | 7 | 105 | 1 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000313 | BUEHNER WATER SYSTEM | 50 | 150 | 2 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000317 | OID #51 - SUNSET OAKS #10 | 82 | 287 | 2 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000433 | OID-OAKDALE RURAL WATER SYSTEM #1 | 476 | 1570 | 8 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5000584 | MESA ELEMENTARY SCHOOL | 5 | 860 | 1 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5010006 | CITY OF WATERFORD | 2065 | 8788 | 5 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5010026 | WATERFORD - HICKMAN | 180 | 597 | 2 | No | STANISLAUS | 0 | 1700 | 1700 | 1779.9
CA5100107 | SUTTER CO. WWD#1 (ROBBINS) | 94 | 339 | 2 | No | SUTTER | 0 | 1700 | 1700 | 1779.9
CA5100112 | TIERRA BUENA MHP #1 | 17 | 50 | 1 | No | SUTTER | 0 | 1700 | 1700 | 1779.9
CA5100136 | EAST NICOLAUS JOINT UNION HIGH SCHOOL | 1 | 338 | 1 | No | SUTTER | 0 | 1700 | 1700 | 1779.9
CA5100138 | BROWNS ELEMENTARY SCHOOL | 1 | 160 | 1 | No | SUTTER | 0 | 1700 | 1700 | 1779.9
CA5100140 | MARCUM ILLINOIS ELEMENTARY SCHOOL | 7 | 185 | 1 | No | SUTTER | 0 | 1700 | 1700 | 1779.9
CA5100142 | NUESTRO SCHOOL | 1 | 120 | 1 | No | SUTTER | 0 | 1700 | 1700 | 1779.9
CA5100143 | PLEASANT GROVE ELEM. SCHOOL | 1 | 185 | 1 | No | SUTTER | 0 | 1700 | 1700 | 1779.9
CA5100145 | WINSHIP ELEMENTARY SCHOOL | 2 | 38 | 2 | No | SUTTER | 0 | 1700 | 1700 | 1779.9
CA5100149 | BARRY ELEMENTARY SCHOOL | 1 | 650 | 1 | No | SUTTER | 0 | 1700 | 1700 | 1779.9
CA5100172 | ENCINAL ELEMENTARY SCHOOL | 1 | 128 | 1 | No | SUTTER | 0 | 1700 | 1700 | 1779.9
CA5101009 | WILDEWOOD EAST MUTUAL | 48 | 350 | 2 | No | SUTTER | 0 | 1700 | 1700 | 1779.9
CA5110001 | CITY OF LIVE OAK | 2407 | 8912 | 5 | No | SUTTER | 0 | 1700 | 1700 | 1779.9
CA5200007 | HOWELL'S LAKESIDE WATER CO. | 55 | 75 | 2 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200008 | BREESE SUBDIVISION 2 | 30 | 75 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200010 | WOODSON BRIDGE RV PARK | 46 | 45 | 2 | NULL | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200012 | VISTA GRANDE WATER SYSTEM | 141 | 400 | 2 | NULL | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200013 | WOMACK SUBDIVISION M.W.C. | 16 | 40 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200014 | WILSON ACRES MUTUAL WATER | 28 | 75 | 1 |  | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200255 | CORNING RV PARK | 40 | 112 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200502 | LAS FLORES WATER WORKS | 63 | 191 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200504 | CITY OF TEHAMA | 195 | 445 | 2 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200506 | PLUM VALLEY ELEM SCHOOL (NEW SCHOOL) | 1 | 70 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200507 | BERRENDOS SCHOOL | 4 | 325 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200508 | RIO VISTA MOBILE HOME PARK | 195 | 543 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200510 | RIVER RANCH MOBILE HOME PARK | 109 | 305 | 2 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200511 | BEND ELEMENTARY SCHOOL | 5 | 100 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200512 | BEND MOBILEHOME & RV PARK | 42 | 99 | 2 |  | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200513 | EVERGREEN UNION SCHOOL DISTRICT | 8 | 1100 | 2 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200514 | GOLDEN ACRES TRAILER PARK | 16 | 81 | 1 | NULL | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200518 | FLOURNOY SCHOOL | 2 | 32 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200519 | GERBER UNION ELEMENTARY SCHOOL DISTRICT | 1 | 625 | 1 |  | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200520 | KIRKWOOD ELEMENTARY SCHOOL | 4 | 111 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200521 | ANTELOPE CREEK MHP | 60 | 175 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200526 | HIDDEN HARBOR MARINA & RVP | 70 | 70 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200527 | HUNTER'S FISHING RESORT | 47 | 50 | 2 |  | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200531 | RIVER POINTE LANDING MHP | 40 | 104 | 1 | NULL | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200535 | LIVE OAK ACRES MWC INC. | 40 | 80 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200538 | LASSEN VIEW UNION ELEMENTARY SCHOOL DIST | 4 | 350 | 1 | NULL | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200539 | FRIENDLY ACRES MHP | 51 | 75 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200540 | REEDS CREEK SCHOOL | 7 | 196 | 1 |  | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200544 | VINA ELEMENTARY SCHOOL | 2 | 90 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200545 | MODERN VILLAGE MWC | 19 | 85 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200546 | ANTELOPE-HOMEWOOD MHP | 24 | 140 | 1 | NULL | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200547 | GATEWAY MOBILE HOME PARK | 32 | 75 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200548 | LASSEN VIEW WATER DISTRICT | 30 | 85 | 1 | NULL | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200551 | WOODSON BRIDGE MHP | 104 | 158 | 1 |  | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200555 | RIO RANCH COMMUNITY SVCS DIST | 30 | 44 | 1 |  | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200556 | MAYWOOD MOBILE HOME PARK | 50 | 140 | 1 |  | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200558 | RIVER VIEW MHC LLC | 55 | 100 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200559 | ABBEY OF NEW CLAIRVAUX | 22 | 25 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200560 | MIRA MONTE WATER CO. | 41 | 142 | 1 | NULL | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200562 | SKY VIEW COUNTY WATER | 85 | 412 | 1 |  | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200565 | RICHFIELD ELEMENTARY SCHOOL | 9 | 280 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200570 | SURREY VILLAGE WATER CO. INC. | 75 | 145 | 2 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200571 | MOUNTAIN VALLEY APTS & RVP | 47 | 131 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200584 | LITTLE AVENUE WATER SYSTEM | 16 | 53 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200600 | GURNSEY AVENUE MUTUAL WATER SYSTEM | 15 | 25 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200645 | SADDLEBACK MUTUAL WATER CO. | 38 | 90 | 2 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200657 | NORCAL WATER WORKS | 17 | 45 | 1 | NULL | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5200864 | R-WILD HORSE RANCH | 17 | 55 | 2 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5201147 | GOLDEN MEADOWS CSD | 49 | 102 | 1 |  | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5205007 | RANCHO TEHAMA ELEM SCHOOL | 5 | 90 | 1 | No | TEHAMA | 0 | 1700 | 1700 | 1779.9
CA5301001 | BUCKTAIL MUTUAL WATER COMPANY | 42 | 61 | 3 | No | TRINITY | 0 | 1700 | 1700 | 1779.9
CA5301002 | LEWISTON COMMUNITY SERVICES DISTRICT | 231 | 701 | 3 | No | TRINITY | 0 | 1700 | 1700 | 1779.9
CA5301102 | TRINITY KNOLLS MUTUAL WATER COMPANY | 66 | 338 | 7 | No | TRINITY | 0 | 1700 | 1700 | 1779.9
CA5301103 | COVINGTON MILL - A | 42 | 60 | 1 | No | TRINITY | 0 | 1700 | 1700 | 1779.9
CA5301104 | COVINGTON MILL MWC-DIVISION B | 99 | 99 | 3 | No | TRINITY | 0 | 1700 | 1700 | 1779.9
CA5304105 | BURNT RANCH SCHOOL | 2 | 125 | 1 |  | TRINITY | 0 | 1700 | 1700 | 1779.9
CA5305107 | SO TRINITY UNIFIED SCHOOL DIST. | 6 | 100 | 1 |  | TRINITY | 0 | 1700 | 1700 | 1779.9
CA5400506 | NORTH KAWEAH MWC | 71 | 560 | 3 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400519 | PALO VERDE SCHOOL | 26 | 500 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400529 | SHADY GROVE MHP, LLC | 42 | 95 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400537 | LINDYS LANDING | 177 | 49 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400538 | ACCELERATED CHARTER HIGH SCHOOL | 10 | 172 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400550 | SEVILLE WATER COMPANY | 90 | 691 | 2 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400556 | RIVER RETREAT MUTUAL | 25 | 53 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400567 | TOOLEVILLE MUTUAL NON PROFIT WATER ASSOC | 77 | 340 | 2 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400602 | EAGLE'S NEST RESORT | 78 | 279 | 1 |  | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400616 | LEMON COVE WATER CO | 60 | 109 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400620 | GRAND VIEW SCHOOL | 9 | 400 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400624 | KINGS RIVER ELEMENTARY SCHOOL | 9 | 550 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400636 | OROSI HIGH SCHOOL | 8 | 1200 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400647 | YOKOHL MUTUAL WATER CO | 32 | 95 | 2 |  | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400655 | CENTRAL MUTUAL WATER CO | 41 | 119 | 1 |  | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400709 | SEQUOIA UNION ELEMENTARY SCHOOL | 26 | 400 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400710 | BADGER HILL ESTATES | 98 | 272 | 2 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400714 | SUNDALE UNION SCHOOL | 11 | 827 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400728 | GRIER MUTUAL WATER COMPANY | 99 | 94 | 1 | N/A | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400732 | PIERPOINT SPRINGS WATER CO. | 84 | 35 | 2 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400735 | RODRIGUEZ LABOR CAMP | 35 | 110 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400744 | EAST THREE RIVERS MUTUAL WATER CORP | 15 | 40 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400754 | SOUTH KAWEAH MUTUAL WATER COMPANY | 138 | 384 | 2 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400816 | BEDEL MUTUAL WATER CO | 66 | 155 | 2 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400819 | MOUNTAIN VIEW MHP | 24 | 44 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400844 | ELBOW CREEK SCHOOL | 11 | 530 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400846 | ELBOW SCHOOL | 3 | 95 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400850 | PACKWOOD SCHOOL | 2 | 105 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400873 | UNION SCHOOL | 1 | 330 | 1 |  | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400880 | THE LAKES ASSOCIATION | 161 | 495 | 2 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400881 | SUNRISE MUTUAL WATER CO. | 39 | 80 | 2 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400886 | COLUMBINE SCHOOL | 8 | 250 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400903 | TRACT 92 CSD | 93 | 500 | 2 |  | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400940 | SIERRA KING HOMEOWNERS ASSN | 49 | 200 | 2 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5400972 | OUTSIDE CREEK SCHOOL | 2 | 125 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5401003 | EAST OROSI CSD | 103 | 932 | 2 |  | TULARE | 0 | 1700 | 1700 | 1779.9
CA5401026 | DEER MEADOW MUTUAL WATER COMPANY | 25 | 67 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5402008 | HOT SPRINGS SCHOOL | 1 | 42 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5402036 | R-RANCH IN THE SEQUOIAS | 115 | 330 | 2 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5402038 | PATTERSON TRACT CSD | 153 | 550 | 2 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5403043 | YETTEM WATER SYSTEM | 66 | 350 | 2 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5403084 | FAIRWAY MUTUAL WATER CO | 45 | 126 | 2 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5403110 | SIERRA MUTUAL WATER CO | 16 | 43 | 2 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5403113 | SOUTH FORK ESTATES MUTUAL WATER CO | 39 | 92 | 3 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5403130 | ELEANOR ROOSEVELT COMM LEARNING CTR | 5 | 295 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5403212 | MONSON WATER SYSTEM | 32 | 140 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5403217 | OKIEVILLE HIGHLAND ACRES MWC | 72 | 300 | 1 |  | TULARE | 0 | 1700 | 1700 | 1779.9
CA5410009 | PIXLEY PUBLIC UTIL DIST | 840 | 2772 | 4 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5410026 | POPLAR COMM SERVICE DIST | 597 | 2200 | 2 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5410503 | NPS-WOLVERTON | 125 | 2940 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5410513 | NPS-ASH MOUNTAIN | 45 | 2930 | 1 | No | TULARE | 0 | 1700 | 1700 | 1779.9
CA5500041 | ALPINE ACRES MUTUAL WATER CO | 55 | 59 | 2 | NULL | TUOLUMNE | 0 | 1700 | 1700 | 1779.9
CA5500053 | LEISURE PINES MUTUAL WATER CO | 103 | 340 | 3 | No | TUOLUMNE | 0 | 1700 | 1700 | 1779.9
CA5500092 | PONDEROSA MOBILE HOME PARK | 58 | 52 | 2 |  | TUOLUMNE | 0 | 1700 | 1700 | 1779.9
CA5500115 | SUGAR PINE RV RESORT | 87 | 244 | 1 | No | TUOLUMNE | 0 | 1700 | 1700 | 1779.9
CA5500120 | 49ER TRAILER RANCH | 80 | 121 | 1 | No | TUOLUMNE | 0 | 1700 | 1700 | 1779.9
CA5500125 | MOTHER LODE MOBILE ESTATES | 75 | 210 | 1 |  | TUOLUMNE | 0 | 1700 | 1700 | 1779.9
CA5500149 | COLUMBIA MOBILE HOME PARK | 63 | 88 | 1 | No | TUOLUMNE | 0 | 1700 | 1700 | 1779.9
CA5500152 | CURTIS CREEK ELEMENTARY SCHOOL | 1 | 546 | 1 |  | TUOLUMNE | 0 | 1700 | 1700 | 1779.9
CA5500171 | SIERRA OUTDOOR SCHOOL | 19 | 283 | 2 | No | TUOLUMNE | 0 | 1700 | 1700 | 1779.9
CA5500193 | TAMARRON MOBILE HOME PARK | 100 | 225 | 1 | No | TUOLUMNE | 0 | 1700 | 1700 | 1779.9
CA5500221 | PINECREST ELEMENTARY SCHOOL | 10 | 25 | 1 | NULL | TUOLUMNE | 0 | 1700 | 1700 | 1779.9
CA5500242 | SIERRA WALDORF SCHOOL | 17 | 132 | 1 |  | TUOLUMNE | 0 | 1700 | 1700 | 1779.9
CA5500353 | SIERRA VILLAGE MOBILE HOME PARK | 30 | 30 | 1 | No | TUOLUMNE | 0 | 1700 | 1700 | 1779.9
CA5510004 | PINECREST PERMITTEES ASSN | 390 | 1253 | 2 | No | TUOLUMNE | 0 | 1700 | 1700 | 1779.9
CA5510011 | COLD SPRINGS WATER CO | 535 | 153 | 1 | No | TUOLUMNE | 0 | 1700 | 1700 | 1779.9
CA5510503 | YOSEMITE NPS-HODGDON MEADOW | 51 | 51 | 1 | No | TUOLUMNE | 0 | 1700 | 1700 | 1779.9
CA5601106 | ALTURAS FILLMORE MHP | 33 | 99 | 1 | No | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5601117 | SENIOR CANYON MUTUAL WATER CO | 218 | 800 | 1 | No | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5601119 | SIETE ROBLES MUTUAL WATER CO | 95 | 323 | 1 | No | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5601125 | COMMUNITY MUTUAL WATER CO | 36 | 53 | 2 | No | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5601141 | SOUTH MOUNTAIN MUTUAL WATER CO | 27 | 58 | 2 | No | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5601144 | RANCHO SESPE WORKERS IMP ASSOC | 109 | 600 | 1 | No | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5601405 | SANTA CLARA SCHOOL | 1 | 39 | 1 | No | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5602101 | ESTERINA PROPERTIES | 16 | 50 | 2 | No | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5602109 | GLENVIEW MOBILE PARK | 26 | 160 | 1 | No | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5602110 | NAVALAIR MOBILE HOME PARK | 52 | 160 | 2 | No | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5602403 | LAGUNA VISTA SCHOOL/OCEANVIEW SCHOOL DIS | 1 | 600 | 1 |  | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5610001 | DEMPSEY ROAD MUTUAL WATER CO | 301 | 990 | 1 | N/A | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5610035 | RIO MANOR MUTUAL WATER CO | 295 | 983 | 2 | No | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5610056 | VINEYARD AVE ESTATES MWC | 342 | 1200 | 2 | No | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5610068 | CLOVERDALE MUTUAL WATER CO. | 150 | 455 | 3 |  | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5610701 | NAVAL BASE VENTURA COUNTY, PORT HUENEME | 609 | 3500 | 1 |  | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5610702 | U.S.N., SAN NICOLAS ISLAND | 106 | 187 | 1 |  | VENTURA | 0.32 | 1700 | 2244 | 2349.468
CA5700509 | CLARKSBURG MIDDLE SCHOOL | 3 | 460 | 1 | No | YOLO | 0 | 1700 | 1700 | 1779.9
CA5700510 | DELTA HIGH SCHOOL | 7 | 250 | 1 | No | YOLO | 0 | 1700 | 1700 | 1779.9
CA5700554 | CAMPERS INN - RV & GOLF COURSE | 68 | 120 | 1 | No | YOLO | 0 | 1700 | 1700 | 1779.9
CA5700623 | DAVIS JUSD - FAIRFIELD SCHOOL | 1 | 65 | 1 | No | YOLO | 0 | 1700 | 1700 | 1779.9
CA5700643 | PLAINFIELD ELEM SCHOOL - WATER | 17 | 400 | 1 | No | YOLO | 0 | 1700 | 1700 | 1779.9
CA5800006 | YES CHARTER ACADEMY | 1 | 125 | 1 | No | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800572 | FAIRWAY DOWNS MUTUAL WATER CO | 27 | 100 | 1 | No | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800803 | LOMA RICA WATER COMPANY | 70 | 200 | 1 | No | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800805 | LAKE FRANCIS MUTUAL WATER COMPANY | 19 | 60 | 2 | No | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800820 | RIVER HIGHLANDS CSD | 84 | 200 | 3 | No | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800821 | HERITAGE PARK | 20 | 26 | 1 |  | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800823 | COUNTRY AIR MOBILE HOME PARK | 35 | 100 | 2 | No | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800824 | COUNTRY VILLAGE MOBILE HOME PARK | 45 | 50 | 1 | No | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800827 | WHISPERING PINES MOBILE HOME PARK | 19 | 25 | 1 | No | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800828 | COUNTRYSIDE MOBILE HOME PARK | 86 | 185 | 1 | No | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800832 | CASTLEWOOD MOBILE HOME PARK | 88 | 200 | 1 | No | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800840 | MJUSD CORDUA SCHOOL | 3 | 110 | 1 | No | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800843 | MJUSD FOOTHILL INTERMEDIATE SCHOOL | 2 | 325 | 1 | No | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800844 | MJUSD BROWNS VALLEY SCHOOL | 5 | 155 | 1 | No | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800845 | MJUSD DOBBINS SCHOOL | 3 | 85 | 1 | No | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800847 | MJUSD LOMA RICA SCHOOL | 6 | 150 | 1 | No | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800850 | REBEL RIDGE VILLAGE | 41 | 60 | 1 | No | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800863 | FELLOWSHIP OF FRIENDS | 30 | 325 | 2 |  | YUBA | 0 | 1700 | 1700 | 1779.9
CA5800924 | CAMPTONVILLE COMMUNITY SERV DIST | 85 | 180 | 2 | No | YUBA | 0 | 1700 | 1700 | 1779.9
Total | [9 empty] | 2453414.16

## Basic Info (hidden)
Number | Agency | State Type | Service Area
CA0103040 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0103041 | DISTRICT 04 - SAN FRANCISCO | C | R - MOBILE HOME PARK
CA0105002 | DISTRICT 04 - SAN FRANCISCO | NC | T - RECREATION AREA
CA0105008 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0105009 | DISTRICT 04 - SAN FRANCISCO | NTNC | NT - SCHOOL
CA0105010 | DISTRICT 04 - SAN FRANCISCO | NC | T - RECREATION AREA
CA0105012 | DISTRICT 04 - SAN FRANCISCO | NC | T - RECREATION AREA
CA0105013 | DISTRICT 04 - SAN FRANCISCO | NC | T - RECREATION AREA
CA0105016 | DISTRICT 04 - SAN FRANCISCO | NC | T - RESTAURANT
CA0105017 | DISTRICT 04 - SAN FRANCISCO | NC | T - SUMMER CAMP
CA0105018 | DISTRICT 04 - SAN FRANCISCO | NC | T - HOTEL/MOTEL
CA0105019 | DISTRICT 04 - SAN FRANCISCO | NC | T - SERVICE STATION
CA0105020 | DISTRICT 04 - SAN FRANCISCO | NTNC | T - RECREATION AREA
CA0110001 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0110003 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0110005 | DISTRICT 04 - SAN FRANCISCO | C | R - MUNICIPALITY
CA0110006 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0110008 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0110009 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0110010 | DISTRICT 04 - SAN FRANCISCO | C | O - WHOLESALER (SELLS WATER)
CA0110011 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0110012 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0110016 | DISTRICT 04 - SAN FRANCISCO | C | O - OTHER AREA
CA0110018 | DISTRICT 04 - SAN FRANCISCO | C | O - WHOLESALER (SELLS WATER)
CA0110019 | DISTRICT 04 - SAN FRANCISCO | NC | T - OTHER TRANSIENT AREA
CA0110650 | DISTRICT 04 - SAN FRANCISCO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0110701 | DISTRICT 04 - SAN FRANCISCO | NTNC | NT - INSTITUTION
CA0202501 | LPA32 - ALPINE COUNTY | NTNC | NT - SCHOOL
CA0202502 | LPA32 - ALPINE COUNTY | NC | T - RESTAURANT
CA0202503 | LPA32 - ALPINE COUNTY | C | R - RESIDENTIAL AREA
CA0202504 | LPA32 - ALPINE COUNTY | C | R - RESIDENTIAL AREA
CA0202505 | LPA32 - ALPINE COUNTY | NC | T - SUMMER CAMP
CA0202506 | LPA32 - ALPINE COUNTY | NC | T - RESTAURANT
CA0202508 | LPA32 - ALPINE COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA0202509 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202512 | LPA32 - ALPINE COUNTY | NC | T - HOTEL/MOTEL
CA0202513 | LPA32 - ALPINE COUNTY | NC | R - RESIDENTIAL AREA
CA0202515 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202516 | LPA32 - ALPINE COUNTY | NC | R - RESIDENTIAL AREA
CA0202517 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202519 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202520 | LPA32 - ALPINE COUNTY | NC | T - RESTAURANT
CA0202522 | LPA32 - ALPINE COUNTY | C | R - MOBILE HOME PARK
CA0202523 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202524 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202525 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202529 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202530 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202532 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202542 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202543 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202546 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202547 | LPA32 - ALPINE COUNTY | NC | T - SUMMER CAMP
CA0202548 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202549 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202550 | LPA32 - ALPINE COUNTY | NC | NT - INSTITUTION
CA0202552 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202554 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202556 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202557 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202562 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202563 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202564 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202565 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202566 | LPA32 - ALPINE COUNTY | NC | T - RECREATION AREA
CA0202570 | LPA32 - ALPINE COUNTY | NC | T - RESTAURANT
CA0202599 | LPA32 - ALPINE COUNTY | NTNC | NT - SCHOOL
CA0205425 | LPA32 - ALPINE COUNTY | NTNC | T - RECREATION AREA
CA0210001 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0210002 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA0210300 | DISTRICT 09 - SACRAMENTO | NC | T - RECREATION AREA
CA0300006 | DISTRICT 10 - STOCKTON | NC | T - SUMMER CAMP
CA0300007 | DISTRICT 10 - STOCKTON | NC | T - SUMMER CAMP
CA0300010 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0300011 | DISTRICT 10 - STOCKTON | C | R - MOBILE HOME PARK
CA0300016 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0300019 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0300022 | DISTRICT 10 - STOCKTON | NC | T - SUMMER CAMP
CA0300024 | DISTRICT 10 - STOCKTON | C | R - MOBILE HOME PARK
CA0300025 | DISTRICT 10 - STOCKTON | NC | T - RESTAURANT
CA0300028 | DISTRICT 10 - STOCKTON | NC | T - RESTAURANT
CA0300032 | DISTRICT 10 - STOCKTON | NC | T - RECREATION AREA
CA0300033 | DISTRICT 10 - STOCKTON | NC | T - RECREATION AREA
CA0300034 | DISTRICT 10 - STOCKTON | NC | T - RECREATION AREA
CA0300036 | DISTRICT 10 - STOCKTON | NC | T - RECREATION AREA
CA0300037 | DISTRICT 10 - STOCKTON | C | R - MOBILE HOME PARK
CA0300043 | DISTRICT 10 - STOCKTON | NC | R - MOBILE HOME PARK
CA0300048 | DISTRICT 10 - STOCKTON | NC | T - RESTAURANT
CA0300049 | DISTRICT 10 - STOCKTON | NC | T - RECREATION AREA
CA0300051 | DISTRICT 10 - STOCKTON | NC | T - HOTEL/MOTEL
CA0300052 | DISTRICT 10 - STOCKTON | NC | T - RESTAURANT
CA0300053 | DISTRICT 10 - STOCKTON | C | R - MOBILE HOME PARK
CA0300055 | DISTRICT 10 - STOCKTON | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0300060 | DISTRICT 10 - STOCKTON | NC | T - RESTAURANT
CA0300062 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0300065 | DISTRICT 10 - STOCKTON | NC | R - OTHER RESIDENTIAL AREA
CA0300070 | DISTRICT 10 - STOCKTON | NC | R - OTHER RESIDENTIAL AREA
CA0300073 | DISTRICT 10 - STOCKTON | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0300074 | DISTRICT 10 - STOCKTON | NC | R - OTHER RESIDENTIAL AREA
CA0300076 | DISTRICT 10 - STOCKTON | NC | T - RECREATION AREA
CA0300077 | DISTRICT 10 - STOCKTON | NC | T - RESTAURANT
CA0300078 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0300080 | DISTRICT 10 - STOCKTON | NC | T - RECREATION AREA
CA0300081 | DISTRICT 10 - STOCKTON | NC | T - RESTAURANT
CA0300083 | DISTRICT 10 - STOCKTON | NC | T - RESTAURANT
CA0300085 | DISTRICT 10 - STOCKTON | NC | T - RESTAURANT
CA0300086 | DISTRICT 10 - STOCKTON | NC | T - OTHER TRANSIENT AREA
CA0300087 | DISTRICT 10 - STOCKTON | NC | T - RESTAURANT
CA0300088 | DISTRICT 10 - STOCKTON | NC | T - RECREATION AREA
CA0300089 | DISTRICT 10 - STOCKTON | NC | NT - INDUSTRIAL/AGRICULTURAL
CA0300090 | DISTRICT 10 - STOCKTON | NC | NT - INDUSTRIAL/AGRICULTURAL
CA0300091 | DISTRICT 10 - STOCKTON | NC | NT - INDUSTRIAL/AGRICULTURAL
CA0300092 | DISTRICT 10 - STOCKTON | NC | NT - INDUSTRIAL/AGRICULTURAL
CA0300095 | DISTRICT 10 - STOCKTON | NC | T - OTHER TRANSIENT AREA
CA0300096 | DISTRICT 10 - STOCKTON | NC | NT - INDUSTRIAL/AGRICULTURAL
CA0300097 | DISTRICT 10 - STOCKTON | NC | NT - INDUSTRIAL/AGRICULTURAL
CA0300099 | DISTRICT 10 - STOCKTON | NC | NT - INDUSTRIAL/AGRICULTURAL
CA0300101 | DISTRICT 10 - STOCKTON | NC | T - RESTAURANT
CA0300102 | DISTRICT 10 - STOCKTON | NC | NT - INDUSTRIAL/AGRICULTURAL
CA0300104 | DISTRICT 10 - STOCKTON | NC | T - OTHER TRANSIENT AREA
CA0300107 | DISTRICT 10 - STOCKTON | NC | T - OTHER TRANSIENT AREA
CA0300108 | DISTRICT 10 - STOCKTON | NC | T - OTHER TRANSIENT AREA
CA0300110 | DISTRICT 10 - STOCKTON | NC | T - OTHER TRANSIENT AREA
CA0300112 | DISTRICT 10 - STOCKTON | NC | T - OTHER TRANSIENT AREA
CA0300113 | DISTRICT 10 - STOCKTON | NC | T - OTHER TRANSIENT AREA
CA0300448 | DISTRICT 10 - STOCKTON | NTNC | O - OTHER AREA
CA0300524 | DISTRICT 10 - STOCKTON | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0300667 | DISTRICT 10 - STOCKTON | NC | T - SUMMER CAMP
CA0301038 | DISTRICT 10 - STOCKTON | NTNC | T - RECREATION AREA
CA0310001 | DISTRICT 10 - STOCKTON | C | O - OTHER AREA
CA0310002 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0310003 | DISTRICT 10 - STOCKTON | C | O - WHOLESALER (SELLS WATER)
CA0310004 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0310005 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0310006 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0310008 | DISTRICT 10 - STOCKTON | C | T - RECREATION AREA
CA0310011 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0310012 | DISTRICT 10 - STOCKTON | C | O - WHOLESALER (SELLS WATER)
CA0310018 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0310019 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0310021 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0310300 | DISTRICT 10 - STOCKTON | NC | T - RECREATION AREA
CA0310803 | DISTRICT 10 - STOCKTON | NC | T - RESTAURANT
CA0310804 | DISTRICT 10 - STOCKTON | NC | T - RESTAURANT
CA0400001 | LPA34 - BUTTE COUNTY | C | NT - INSTITUTION
CA0400003 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0400004 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0400007 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0400008 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0400010 | LPA34 - BUTTE COUNTY | NC | T - SUMMER CAMP
CA0400012 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0400013 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0400014 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0400016 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0400019 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK
CA0400020 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK
CA0400021 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK
CA0400023 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK
CA0400026 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK
CA0400027 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK
CA0400030 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK
CA0400040 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK
CA0400041 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK
CA0400042 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK
CA0400051 | LPA34 - BUTTE COUNTY | C | R - MOBILE HOME PARK
CA0400060 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL
CA0400062 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL
CA0400063 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL
CA0400064 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL
CA0400065 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL
CA0400067 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL
CA0400068 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL
CA0400070 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL
CA0400073 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL
CA0400078 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0400079 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL
CA0400081 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0400090 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0400091 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0400093 | LPA34 - BUTTE COUNTY | NC | T - OTHER TRANSIENT AREA
CA0400103 | LPA34 - BUTTE COUNTY | NC | T - RECREATION AREA
CA0400105 | LPA34 - BUTTE COUNTY | NC | T - RECREATION AREA
CA0400106 | LPA34 - BUTTE COUNTY | NC | T - OTHER TRANSIENT AREA
CA0400111 | LPA34 - BUTTE COUNTY | NC | T - RECREATION AREA
CA0400117 | LPA34 - BUTTE COUNTY | NC | T - OTHER TRANSIENT AREA
CA0400120 | LPA34 - BUTTE COUNTY | NC | T - RECREATION AREA
CA0400123 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0400132 | LPA34 - BUTTE COUNTY | NC | T - RECREATION AREA
CA0400133 | LPA34 - BUTTE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0400135 | LPA34 - BUTTE COUNTY | NC | T - RECREATION AREA
CA0400137 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA0400138 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA0400140 | LPA34 - BUTTE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0400141 | LPA34 - BUTTE COUNTY | NTNC | R - RESIDENTIAL AREA
CA0400142 | LPA34 - BUTTE COUNTY | NC | T - RECREATION AREA
CA0400143 | LPA34 - BUTTE COUNTY | NC | T - RECREATION AREA
CA0400144 | LPA34 - BUTTE COUNTY | NC | T - RECREATION AREA
CA0400149 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0400150 | LPA34 - BUTTE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0400151 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0400154 | LPA34 - BUTTE COUNTY | NTNC | NT - OTHER NON-TRANSIENT AREA
CA0400155 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0400158 | LPA34 - BUTTE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0400160 | LPA34 - BUTTE COUNTY | NC | T - RECREATION AREA
CA0400161 | LPA34 - BUTTE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0400162 | LPA34 - BUTTE COUNTY | NTNC | NT - SCHOOL
CA0400166 | LPA34 - BUTTE COUNTY | NC | T - RECREATION AREA
CA0400169 | LPA34 - BUTTE COUNTY | NC | T - RESTAURANT
CA0405001 | DISTRICT 21 - VALLEY | C | T - RECREATION AREA
CA0405002 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA0405003 | DISTRICT 21 - VALLEY | NTNC | T - OTHER TRANSIENT AREA
CA0409177 | LPA34 - BUTTE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0409179 | LPA34 - BUTTE COUNTY | NC | T - RECREATION AREA
CA0409181 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0409183 | LPA34 - BUTTE COUNTY | C | R - RESIDENTIAL AREA
CA0409184 | LPA34 - BUTTE COUNTY | NC | O - OTHER AREA
CA0409187 | LPA34 - BUTTE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0409188 | LPA34 - BUTTE COUNTY | NTNC | R - OTHER RESIDENTIAL AREA
CA0409189 | LPA34 - BUTTE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0409190 | LPA34 - BUTTE COUNTY | NC | T - RESTAURANT
CA0409192 | LPA34 - BUTTE COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA0409193 | LPA34 - BUTTE COUNTY | NC | O - OTHER AREA
CA0409194 | LPA34 - BUTTE COUNTY | NTNC | NT - OTHER NON-TRANSIENT AREA
CA0409195 | LPA34 - BUTTE COUNTY | NC | T - RECREATION AREA
CA0409196 | LPA34 - BUTTE COUNTY | NC | T - OTHER TRANSIENT AREA
CA0409197 | LPA34 - BUTTE COUNTY | NTNC | O - OTHER AREA
CA0410001 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0410002 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0410003 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0410004 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0410005 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0410006 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0410007 | DISTRICT 21 - VALLEY | C | R - MUNICIPALITY
CA0410008 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0410009 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0410011 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0410012 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0410018 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0500003 | LPA35 - CALAVERAS COUNTY | NC | T - RECREATION AREA
CA0500007 | LPA35 - CALAVERAS COUNTY | NC | T - RECREATION AREA
CA0500009 | LPA35 - CALAVERAS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0500016 | LPA35 - CALAVERAS COUNTY | NC | T - SECONDARY RESIDENCES
CA0500019 | LPA35 - CALAVERAS COUNTY | C | R - RESIDENTIAL AREA
CA0500021 | LPA35 - CALAVERAS COUNTY | NC | R - RESIDENTIAL AREA
CA0500022 | LPA35 - CALAVERAS COUNTY | NC | T - SUMMER CAMP
CA0500023 | LPA35 - CALAVERAS COUNTY | NC | R - RESIDENTIAL AREA
CA0500026 | LPA35 - CALAVERAS COUNTY | NC | T - SUMMER CAMP
CA0500027 | LPA35 - CALAVERAS COUNTY | C | R - RESIDENTIAL AREA
CA0500028 | LPA35 - CALAVERAS COUNTY | NC | R - RESIDENTIAL AREA
CA0500029 | LPA35 - CALAVERAS COUNTY | NC | R - RESIDENTIAL AREA
CA0500032 | LPA35 - CALAVERAS COUNTY | NC | T - RECREATION AREA
CA0500039 | LPA35 - CALAVERAS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0500043 | LPA35 - CALAVERAS COUNTY | NC | T - RECREATION AREA
CA0500044 | LPA35 - CALAVERAS COUNTY | NC | T - RECREATION AREA
CA0500050 | LPA35 - CALAVERAS COUNTY | NC | T - RECREATION AREA
CA0500053 | DISTRICT 10 - STOCKTON | NTNC | T - SECONDARY RESIDENCES
CA0500055 | LPA35 - CALAVERAS COUNTY | NC | T - SUMMER CAMP
CA0500057 | LPA35 - CALAVERAS COUNTY | NC | T - RECREATION AREA
CA0500068 | LPA35 - CALAVERAS COUNTY | C | R - MOBILE HOME PARK
CA0500069 | LPA35 - CALAVERAS COUNTY | NC | T - RESTAURANT
CA0500075 | LPA35 - CALAVERAS COUNTY | C | R - MOBILE HOME PARK
CA0500082 | LPA35 - CALAVERAS COUNTY | NC | T - RECREATION AREA
CA0500084 | LPA35 - CALAVERAS COUNTY | NC | T - SUMMER CAMP
CA0500085 | LPA35 - CALAVERAS COUNTY | NTNC | NT - SCHOOL
CA0500088 | LPA35 - CALAVERAS COUNTY | NC | T - RECREATION AREA
CA0500090 | LPA35 - CALAVERAS COUNTY | NC | T - RESTAURANT
CA0500091 | LPA35 - CALAVERAS COUNTY | C | NT - SCHOOL
CA0500095 | LPA35 - CALAVERAS COUNTY | NTNC | NT - SCHOOL
CA0500096 | LPA35 - CALAVERAS COUNTY | SSWS | T - RESTAURANT
CA0500097 | LPA35 - CALAVERAS COUNTY | NTNC | O - OTHER AREA
CA0500099 | LPA35 - CALAVERAS COUNTY | NC | NT - INSTITUTION
CA0500102 | LPA35 - CALAVERAS COUNTY | NC | T - RECREATION AREA
CA0500103 | LPA35 - CALAVERAS COUNTY | NC | T - OTHER TRANSIENT AREA
CA0500104 | LPA35 - CALAVERAS COUNTY | NC | T - OTHER TRANSIENT AREA
CA0500105 | LPA35 - CALAVERAS COUNTY | NC | NT - INSTITUTION
CA0500106 | LPA35 - CALAVERAS COUNTY | NC | T - RECREATION AREA
CA0500107 | LPA35 - CALAVERAS COUNTY | NC | NT - MEDICAL FACILITY
CA0510001 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0510002 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0510003 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0510004 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0510004 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0510005 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0510006 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0510009 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0510010 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0510011 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0510012 | DISTRICT 10 - STOCKTON | C | T - RECREATION AREA
CA0510016 | DISTRICT 10 - STOCKTON | C | O - WHOLESALER (SELLS WATER)
CA0510017 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0510019 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA0600001 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA0600003 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA0600005 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0600008 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0600009 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA0600012 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0600012 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0600013 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0600016 | DISTRICT 21 - VALLEY | NC | T - HOTEL/MOTEL
CA0600027 | DISTRICT 21 - VALLEY | NC | R - MOBILE HOME PARK
CA0600032 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA0600033 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA0600042 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA0600050 | DISTRICT 21 - VALLEY | NC | T - HIGHWAY REST AREA
CA0600056 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA0600065 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0600076 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA0605002 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0605004 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0605005 | DISTRICT 21 - VALLEY | NC | T - OTHER TRANSIENT AREA
CA0605006 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA0605007 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0605011 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0605012 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0605013 | DISTRICT 21 - VALLEY | NC | T - OTHER TRANSIENT AREA
CA0605015 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA0610001 | DISTRICT 21 - VALLEY | C | O - OTHER AREA
CA0610002 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0610003 | DISTRICT 21 - VALLEY | C | O - OTHER AREA
CA0610004 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA0701706 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0701707 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0706000 | LPA37 - CONTRA COSTA COUNTY | NP | NT - INDUSTRIAL/AGRICULTURAL
CA0706004 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0706005 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0706007 | LPA37 - CONTRA COSTA COUNTY | SSWS | R - RESIDENTIAL AREA
CA0706014 | LPA37 - CONTRA COSTA COUNTY | NC | R - RESIDENTIAL AREA
CA0706015 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0706018 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0706022 | LPA37 - CONTRA COSTA COUNTY | NC | O - OTHER AREA
CA0706023 | LPA37 - CONTRA COSTA COUNTY | SSWS | R - RESIDENTIAL AREA
CA0706027 | LPA37 - CONTRA COSTA COUNTY | NTNC | NT - SCHOOL
CA0706028 | LPA37 - CONTRA COSTA COUNTY | NTNC | NT - SCHOOL
CA0706029 | LPA37 - CONTRA COSTA COUNTY | NTNC | NT - SCHOOL
CA0706030 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0706031 | LPA37 - CONTRA COSTA COUNTY | NC | T - RESTAURANT
CA0706032 | LPA37 - CONTRA COSTA COUNTY | NC | O - OTHER AREA
CA0706034 | LPA37 - CONTRA COSTA COUNTY | NC | R - RESIDENTIAL AREA
CA0706037 | LPA37 - CONTRA COSTA COUNTY | NC | O - OTHER AREA
CA0706042 | LPA37 - CONTRA COSTA COUNTY | NC | T - RESTAURANT
CA0706045 | LPA37 - CONTRA COSTA COUNTY | NC | T - RESTAURANT
CA0706049 | LPA37 - CONTRA COSTA COUNTY | NC | T - RESTAURANT
CA0706050 | LPA37 - CONTRA COSTA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0706054 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0706055 | LPA37 - CONTRA COSTA COUNTY | NC | T - RESTAURANT
CA0706056 | LPA37 - CONTRA COSTA COUNTY | NC | T - RESTAURANT
CA0706059 | LPA37 - CONTRA COSTA COUNTY | NC | T - RESTAURANT
CA0706102 | LPA37 - CONTRA COSTA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0706110 | LPA37 - CONTRA COSTA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA0706111 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0706112 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0707501 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707502 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0707503 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0707504 | LPA37 - CONTRA COSTA COUNTY | SSWS | R - RESIDENTIAL AREA
CA0707507 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707509 | LPA37 - CONTRA COSTA COUNTY | NC | T - RESTAURANT
CA0707511 | LPA37 - CONTRA COSTA COUNTY | SSWS | R - RESIDENTIAL AREA
CA0707517 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707519 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707521 | LPA37 - CONTRA COSTA COUNTY | NC | T - RESTAURANT
CA0707523 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707528 | LPA37 - CONTRA COSTA COUNTY | SSWS | R - RESIDENTIAL AREA
CA0707532 | LPA37 - CONTRA COSTA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA0707534 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0707542 | LPA37 - CONTRA COSTA COUNTY | NC | R - RESIDENTIAL AREA
CA0707545 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707546 | LPA37 - CONTRA COSTA COUNTY | SSWS | R - RESIDENTIAL AREA
CA0707547 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707550 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0707553 | LPA37 - CONTRA COSTA COUNTY | C | R - MOBILE HOME PARK
CA0707556 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707562 | LPA37 - CONTRA COSTA COUNTY | SSWS | R - RESIDENTIAL AREA
CA0707564 | LPA37 - CONTRA COSTA COUNTY | NC | T - RESTAURANT
CA0707568 | LPA37 - CONTRA COSTA COUNTY | NC | T - RESTAURANT
CA0707569 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707570 | LPA37 - CONTRA COSTA COUNTY | NC | T - RESTAURANT
CA0707572 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707573 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707574 | DISTRICT 04 - SAN FRANCISCO | C | R - MOBILE HOME PARK
CA0707575 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707576 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707577 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707580 | LPA37 - CONTRA COSTA COUNTY | SSWS | R - RESIDENTIAL AREA
CA0707581 | LPA37 - CONTRA COSTA COUNTY | SSWS | T - OTHER TRANSIENT AREA
CA0707585 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707588 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707589 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707591 | LPA37 - CONTRA COSTA COUNTY | SSWS | R - RESIDENTIAL AREA
CA0707592 | LPA37 - CONTRA COSTA COUNTY | NC | T - RESTAURANT
CA0707594 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707595 | LPA37 - CONTRA COSTA COUNTY | NC | T - RESTAURANT
CA0707597 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707598 | LPA37 - CONTRA COSTA COUNTY | C | R - MOBILE HOME PARK
CA0707601 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707603 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707608 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707613 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707615 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707617 | LPA37 - CONTRA COSTA COUNTY | NC | T - RESTAURANT
CA0707620 | LPA37 - CONTRA COSTA COUNTY | NTNC | NT - SCHOOL
CA0707623 | LPA37 - CONTRA COSTA COUNTY | C | R - RESIDENTIAL AREA
CA0707625 | LPA37 - CONTRA COSTA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0707630 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0707637 | LPA37 - CONTRA COSTA COUNTY | SSWS | R - RESIDENTIAL AREA
CA0707639 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0707643 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0707644 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0707645 | LPA37 - CONTRA COSTA COUNTY | LSS | R - RESIDENTIAL AREA
CA0707800 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0707900 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0707901 | LPA37 - CONTRA COSTA COUNTY | NC | T - RESTAURANT
CA0707915 | LPA37 - CONTRA COSTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA0708000 | LPA37 - CONTRA COSTA COUNTY | NC | T - RECREATION AREA
CA0710001 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0710002 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0710003 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0710004 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0710006 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0710007 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0710008 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0710009 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA0710010 | DISTRICT 04 - SAN FRANCISCO | C | O - WHOLESALER (SELLS WATER)
CA0710011 | DISTRICT 04 - SAN FRANCISCO | C | O - WHOLESALER (SELLS WATER)
CA0710300 | DISTRICT 04 - SAN FRANCISCO | NC | T - RECREATION AREA
CA0710800 | DISTRICT 04 - SAN FRANCISCO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA0710995 | LPA37 - CONTRA COSTA COUNTY | SSWS | R - RESIDENTIAL AREA
CA0711146 | LPA37 - CONTRA COSTA COUNTY | SSWS | R - RESIDENTIAL AREA
CA0800526 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA0800532 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA0800542 | DISTRICT 01 - KLAMATH | NC | T - HOTEL/MOTEL
CA0800548 | DISTRICT 01 - KLAMATH | C | T - SECONDARY RESIDENCES
CA0800552 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK
CA0800555 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA0800556 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA0800557 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA0800603 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK
CA0800605 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK
CA0800608 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA0800613 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA0800615 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA0800622 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA0800627 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA0800632 | DISTRICT 01 - KLAMATH | NC | R - MOBILE HOME PARK
CA0800635 | DISTRICT 01 - KLAMATH | NC | R - MOBILE HOME PARK
CA0800647 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA0800649 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA0800661 | DISTRICT 01 - KLAMATH | NC | T - HIGHWAY REST AREA
CA0800700 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK
CA0800800 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK
CA0800825 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA0800850 | DISTRICT 01 - KLAMATH | NC | T - RESTAURANT
CA0800861 | DISTRICT 01 - KLAMATH | C | NT - INDUSTRIAL/AGRICULTURAL
CA0810001 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA0810002 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA0810003 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA
CA0810300 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA0810303 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA0810500 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA0810800 | DISTRICT 01 - KLAMATH | NTNC | NT - INSTITUTION
CA0900100 | LPA39 - EL DORADO COUNTY | NC | T - OTHER TRANSIENT AREA
CA0900102 | LPA39 - EL DORADO COUNTY | C | R - MOBILE HOME PARK
CA0900103 | LPA39 - EL DORADO COUNTY | NC | T - RESTAURANT
CA0900104 | LPA39 - EL DORADO COUNTY | NC | T - SECONDARY RESIDENCES
CA0900105 | LPA39 - EL DORADO COUNTY | NC | T - RESTAURANT
CA0900106 | LPA39 - EL DORADO COUNTY | SSWS | NT - SCHOOL
CA0900107 | LPA39 - EL DORADO COUNTY | NC | T - OTHER TRANSIENT AREA
CA0900109 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900111 | LPA39 - EL DORADO COUNTY | NTNC | NT - SCHOOL
CA0900112 | LPA39 - EL DORADO COUNTY | C | R - MOBILE HOME PARK
CA0900113 | LPA39 - EL DORADO COUNTY | NC | T - OTHER TRANSIENT AREA
CA0900116 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900117 | LPA39 - EL DORADO COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA0900119 | LPA39 - EL DORADO COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA0900120 | LPA39 - EL DORADO COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA0900204 | LPA39 - EL DORADO COUNTY | NC | T - OTHER TRANSIENT AREA
CA0900205 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900206 | LPA39 - EL DORADO COUNTY | NC | T - OTHER TRANSIENT AREA
CA0900208 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900210 | LPA39 - EL DORADO COUNTY | NTNC | NT - SCHOOL
CA0900212 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900213 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900214 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900216 | LPA39 - EL DORADO COUNTY | NC | T - RESTAURANT
CA0900219 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900300 | LPA39 - EL DORADO COUNTY | C | R - RESIDENTIAL AREA
CA0900301 | LPA39 - EL DORADO COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA0900303 | LPA39 - EL DORADO COUNTY | NC | R - RESIDENTIAL AREA
CA0900304 | LPA39 - EL DORADO COUNTY | NTNC | NT - SCHOOL
CA0900306 | LPA39 - EL DORADO COUNTY | NC | T - SUMMER CAMP
CA0900307 | LPA39 - EL DORADO COUNTY | NC | T - RESTAURANT
CA0900308 | LPA39 - EL DORADO COUNTY | C | R - RESIDENTIAL AREA
CA0900309 | LPA39 - EL DORADO COUNTY | NTNC | NT - SCHOOL
CA0900311 | LPA39 - EL DORADO COUNTY | NC | T - SUMMER CAMP
CA0900313 | LPA39 - EL DORADO COUNTY | NP | T - SUMMER CAMP
CA0900314 | LPA39 - EL DORADO COUNTY | NC | T - OTHER TRANSIENT AREA
CA0900316 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900317 | LPA39 - EL DORADO COUNTY | NC | R - RESIDENTIAL AREA
CA0900319 | LPA39 - EL DORADO COUNTY | NC | T - OTHER TRANSIENT AREA
CA0900401 | LPA39 - EL DORADO COUNTY | NC | T - OTHER TRANSIENT AREA
CA0900404 | LPA39 - EL DORADO COUNTY | C | R - MOBILE HOME PARK
CA0900410 | LPA39 - EL DORADO COUNTY | NTNC | NT - SCHOOL
CA0900411 | LPA39 - EL DORADO COUNTY | NC | T - RESTAURANT
CA0900417 | LPA39 - EL DORADO COUNTY | NP | T - RECREATION AREA
CA0900419 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900420 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900422 | LPA39 - EL DORADO COUNTY | C | R - MOBILE HOME PARK
CA0900423 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900502 | LPA39 - EL DORADO COUNTY | NC | T - OTHER TRANSIENT AREA
CA0900505 | LPA39 - EL DORADO COUNTY | NC | T - SUMMER CAMP
CA0900506 | LPA39 - EL DORADO COUNTY | NC | R - RESIDENTIAL AREA
CA0900507 | LPA39 - EL DORADO COUNTY | NC | T - SUMMER CAMP
CA0900511 | LPA39 - EL DORADO COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA0900515 | LPA39 - EL DORADO COUNTY | NC | T - OTHER TRANSIENT AREA
CA0900516 | LPA39 - EL DORADO COUNTY | NC | T - SUMMER CAMP
CA0900523 | LPA39 - EL DORADO COUNTY | NC | R - RESIDENTIAL AREA
CA0900525 | LPA39 - EL DORADO COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA0900529 | LPA39 - EL DORADO COUNTY | NTNC | T - HOTEL/MOTEL
CA0900535 | LPA39 - EL DORADO COUNTY | NC | T - HOTEL/MOTEL
CA0900536 | LPA39 - EL DORADO COUNTY | NC | T - HOTEL/MOTEL
CA0900549 | LPA39 - EL DORADO COUNTY | NC | R - RESIDENTIAL AREA
CA0900551 | LPA39 - EL DORADO COUNTY | NC | T - HOTEL/MOTEL
CA0900553 | LPA39 - EL DORADO COUNTY | NC | T - HOTEL/MOTEL
CA0900554 | LPA39 - EL DORADO COUNTY | NC | T - HOTEL/MOTEL
CA0900557 | LPA39 - EL DORADO COUNTY | SSWS | T - HOTEL/MOTEL
CA0900560 | LPA39 - EL DORADO COUNTY | NC | R - RESIDENTIAL AREA
CA0900562 | LPA39 - EL DORADO COUNTY | NC | R - RESIDENTIAL AREA
CA0900564 | LPA39 - EL DORADO COUNTY | NC | R - RESIDENTIAL AREA
CA0900565 | LPA39 - EL DORADO COUNTY | NC | T - HOTEL/MOTEL
CA0900566 | LPA39 - EL DORADO COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA0900576 | LPA39 - EL DORADO COUNTY | NC | T - HOTEL/MOTEL
CA0900578 | LPA39 - EL DORADO COUNTY | NC | T - HOTEL/MOTEL
CA0900582 | LPA39 - EL DORADO COUNTY | NC | T - HOTEL/MOTEL
CA0900585 | LPA39 - EL DORADO COUNTY | NC | T - HOTEL/MOTEL
CA0900587 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900591 | LPA39 - EL DORADO COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA0900592 | LPA39 - EL DORADO COUNTY | NC | T - HOTEL/MOTEL
CA0900595 | LPA39 - EL DORADO COUNTY | SSWS | R - RESIDENTIAL AREA
CA0900603 | LPA39 - EL DORADO COUNTY | NC | R - RESIDENTIAL AREA
CA0900615 | LPA39 - EL DORADO COUNTY | SSWS | R - RESIDENTIAL AREA
CA0900616 | LPA39 - EL DORADO COUNTY | SSWS | R - RESIDENTIAL AREA
CA0900618 | LPA39 - EL DORADO COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA0900621 | LPA39 - EL DORADO COUNTY | NC | R - RESIDENTIAL AREA
CA0900623 | LPA39 - EL DORADO COUNTY | NC | T - HOTEL/MOTEL
CA0900624 | LPA39 - EL DORADO COUNTY | NC | R - RESIDENTIAL AREA
CA0900629 | LPA39 - EL DORADO COUNTY | NC | R - RESIDENTIAL AREA
CA0900631 | LPA39 - EL DORADO COUNTY | NC | T - SUMMER CAMP
CA0900637 | LPA39 - EL DORADO COUNTY | SSWS | R - RESIDENTIAL AREA
CA0900641 | LPA39 - EL DORADO COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA0900643 | LPA39 - EL DORADO COUNTY | NC | R - RESIDENTIAL AREA
CA0900649 | LPA39 - EL DORADO COUNTY | NTNC | T - RECREATION AREA
CA0900650 | LPA39 - EL DORADO COUNTY | NC | T - SUMMER CAMP
CA0900651 | LPA39 - EL DORADO COUNTY | NC | T - SUMMER CAMP
CA0900652 | LPA39 - EL DORADO COUNTY | NC | T - OTHER TRANSIENT AREA
CA0900654 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900656 | LPA39 - EL DORADO COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA0900658 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900659 | LPA39 - EL DORADO COUNTY | NTNC | T - RECREATION AREA
CA0900660 | LPA39 - EL DORADO COUNTY | NTNC | T - RECREATION AREA
CA0900663 | LPA39 - EL DORADO COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA0900664 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900665 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0900667 | LPA39 - EL DORADO COUNTY | SSWS | R - MOBILE HOME PARK
CA0900669 | LPA39 - EL DORADO COUNTY | SSWS | T - SECONDARY RESIDENCES
CA0900672 | LPA39 - EL DORADO COUNTY | SSWS | R - MOBILE HOME PARK
CA0901217 | LPA39 - EL DORADO COUNTY | C | R - RESIDENTIAL AREA
CA0901219 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0901222 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0901223 | LPA39 - EL DORADO COUNTY | NC | T - HIGHWAY REST AREA
CA0901228 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0901229 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0901230 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0901232 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0901239 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0901243 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0901244 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0901246 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0901247 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0901248 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0901249 | LPA39 - EL DORADO COUNTY | NC | T - RECREATION AREA
CA0901250 | LPA39 - EL DORADO COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA0901260 | LPA39 - EL DORADO COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA0901281 | LPA39 - EL DORADO COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA0901282 | LPA39 - EL DORADO COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA0901285 | LPA39 - EL DORADO COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA0910001 | DISTRICT 09 - SACRAMENTO | C | O - WHOLESALER (SELLS WATER)
CA0910002 | DISTRICT 09 - SACRAMENTO | C | O - WHOLESALER (SELLS WATER)
CA0910003 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA0910006 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA0910007 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA0910012 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA0910013 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA0910015 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA0910017 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA0910018 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA0910019 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA0910024 | DISTRICT 02 - LASSEN | NC | R - RESIDENTIAL AREA
CA0910300 | DISTRICT 09 - SACRAMENTO | NC | T - RECREATION AREA
CA0910301 | DISTRICT 09 - SACRAMENTO | NC | T - RECREATION AREA
CA0910302 | DISTRICT 09 - SACRAMENTO | NC | T - RECREATION AREA
CA0910303 | DISTRICT 09 - SACRAMENTO | NC | T - RECREATION AREA
CA0910305 | DISTRICT 09 - SACRAMENTO | NC | T - RECREATION AREA
CA1000003 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000004 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000005 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000007 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000010 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000012 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000013 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000014 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000015 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000016 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000017 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000018 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000019 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000020 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000021 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000023 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000024 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000039 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000040 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000041 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000042 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000049 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000050 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000051 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000053 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000054 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000056 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000057 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000058 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000059 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000060 | DISTRICT 23 - FRESNO | NTNC | R - RESIDENTIAL AREA
CA1000061 | DISTRICT 23 - FRESNO | NTNC | R - RESIDENTIAL AREA
CA1000063 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000067 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000069 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000071 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000072 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000075 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000076 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000078 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000080 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000083 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000085 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000094 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000096 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000097 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000104 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000105 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000111 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000116 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000122 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000126 | DISTRICT 23 - FRESNO | NC | T - SUMMER CAMP
CA1000128 | DISTRICT 23 - FRESNO | NC | T - SUMMER CAMP
CA1000129 | DISTRICT 23 - FRESNO | NC | T - SUMMER CAMP
CA1000130 | DISTRICT 23 - FRESNO | NC | T - SUMMER CAMP
CA1000134 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000135 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000136 | DISTRICT 23 - FRESNO | NTNC | T - SECONDARY RESIDENCES
CA1000137 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000140 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000141 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000143 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000145 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000147 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000148 | DISTRICT 23 - FRESNO | NTNC | T - RECREATION AREA
CA1000151 | DISTRICT 23 - FRESNO | NC | T - SUMMER CAMP
CA1000156 | DISTRICT 23 - FRESNO | NC | T - SUMMER CAMP
CA1000165 | DISTRICT 23 - FRESNO | NC | T - SUMMER CAMP
CA1000170 | DISTRICT 23 - FRESNO | NC | T - SUMMER CAMP
CA1000171 | DISTRICT 23 - FRESNO | NC | T - RESTAURANT
CA1000176 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000177 | DISTRICT 23 - FRESNO | NTNC | T - HIGHWAY REST AREA
CA1000178 | DISTRICT 23 - FRESNO | NTNC | T - HIGHWAY REST AREA
CA1000180 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000181 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000182 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000184 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000185 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000186 | DISTRICT 23 - FRESNO | C | NT - SCHOOL
CA1000187 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000189 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000190 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000192 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000193 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000194 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000196 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000198 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000199 | DISTRICT 23 - FRESNO | C | NT - INSTITUTION
CA1000200 | DISTRICT 23 - FRESNO | C | T - SECONDARY RESIDENCES
CA1000201 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000204 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000206 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000208 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000213 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1000214 | DISTRICT 23 - FRESNO | NTNC | T - RESTAURANT
CA1000217 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000221 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000223 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000229 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK
CA1000230 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000238 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK
CA1000244 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK
CA1000247 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK
CA1000249 | DISTRICT 23 - FRESNO | NC | R - MOBILE HOME PARK
CA1000257 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK
CA1000258 | DISTRICT 23 - FRESNO | NC | R - MOBILE HOME PARK
CA1000259 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK
CA1000260 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK
CA1000261 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000264 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000265 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK
CA1000267 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK
CA1000270 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000277 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000279 | DISTRICT 23 - FRESNO | NTNC | T - OTHER TRANSIENT AREA
CA1000280 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000282 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000295 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000298 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK
CA1000299 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK
CA1000304 | DISTRICT 23 - FRESNO | NC | T - HOTEL/MOTEL
CA1000305 | DISTRICT 23 - FRESNO | NC | T - HOTEL/MOTEL
CA1000308 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000310 | DISTRICT 23 - FRESNO | NC | O - OTHER AREA
CA1000315 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000316 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000317 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000318 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000319 | DISTRICT 23 - FRESNO | NC | T - RESTAURANT
CA1000324 | DISTRICT 23 - FRESNO | C | NT - INSTITUTION
CA1000345 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1000359 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000361 | DISTRICT 23 - FRESNO | NTNC | O - OTHER AREA
CA1000362 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000365 | DISTRICT 23 - FRESNO | NC | R - MOBILE HOME PARK
CA1000366 | DISTRICT 23 - FRESNO | C | NT - MEDICAL FACILITY
CA1000367 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000369 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1000377 | DISTRICT 23 - FRESNO | C | T - SUMMER CAMP
CA1000378 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK
CA1000381 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000383 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000389 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000393 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000399 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000405 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK
CA1000406 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000411 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000416 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000424 | DISTRICT 23 - FRESNO | NTNC | T - SECONDARY RESIDENCES
CA1000426 | DISTRICT 23 - FRESNO | C | R - MOBILE HOME PARK
CA1000430 | DISTRICT 23 - FRESNO | C | NT - INSTITUTION
CA1000439 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000440 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000442 | DISTRICT 23 - FRESNO | NC | O - OTHER AREA
CA1000443 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000447 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000453 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000454 | DISTRICT 23 - FRESNO | NC | R - MOBILE HOME PARK
CA1000457 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000459 | DISTRICT 23 - FRESNO | NC | O - OTHER AREA
CA1000460 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000461 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000462 | DISTRICT 23 - FRESNO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1000467 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000468 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000471 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000472 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1000473 | DISTRICT 23 - FRESNO | NTNC | R - RESIDENTIAL AREA
CA1000474 | DISTRICT 23 - FRESNO | NC | NT - INSTITUTION
CA1000476 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000478 | DISTRICT 23 - FRESNO | NC | T - RESTAURANT
CA1000479 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000480 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000482 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000483 | DISTRICT 23 - FRESNO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1000484 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000485 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000486 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000487 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000488 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000490 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000492 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000495 | DISTRICT 23 - FRESNO | NTNC | T - OTHER TRANSIENT AREA
CA1000497 | DISTRICT 23 - FRESNO | NC | NT - MEDICAL FACILITY
CA1000501 | DISTRICT 23 - FRESNO | NC | T - RESTAURANT
CA1000502 | DISTRICT 23 - FRESNO | NC | NT - INSTITUTION
CA1000507 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000508 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000511 | DISTRICT 23 - FRESNO | NC | NT - INSTITUTION
CA1000513 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000514 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000515 | DISTRICT 23 - FRESNO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1000517 | DISTRICT 23 - FRESNO | NC | T - RESTAURANT
CA1000519 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000520 | DISTRICT 23 - FRESNO | NC | T - RESTAURANT
CA1000524 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000525 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000526 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000528 | DISTRICT 23 - FRESNO | NC | T - RESTAURANT
CA1000529 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000533 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000534 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000537 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000540 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000541 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000544 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000545 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000546 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000548 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000549 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000550 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000551 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000552 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000553 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000554 | DISTRICT 23 - FRESNO | C | O - OTHER AREA
CA1000555 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000557 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000560 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000561 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000562 | DISTRICT 23 - FRESNO | NTNC | T - SECONDARY RESIDENCES
CA1000564 | DISTRICT 23 - FRESNO | NTNC | NT - OTHER NON-TRANSIENT AREA
CA1000565 | DISTRICT 23 - FRESNO | NTNC | O - OTHER AREA
CA1000566 | DISTRICT 23 - FRESNO | NTNC | O - OTHER AREA
CA1000568 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000569 | DISTRICT 23 - FRESNO | NC | O - OTHER AREA
CA1000570 | DISTRICT 23 - FRESNO | C | O - OTHER AREA
CA1000571 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000573 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000575 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000576 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000577 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000578 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000579 | DISTRICT 23 - FRESNO | NC | T - SECONDARY RESIDENCES
CA1000580 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000583 | DISTRICT 23 - FRESNO | NTNC | NT - SCHOOL
CA1000584 | DISTRICT 23 - FRESNO | NTNC | O - OTHER AREA
CA1000585 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1000586 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000587 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000588 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1000589 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000590 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000592 | DISTRICT 23 - FRESNO | NC | O - OTHER AREA
CA1000593 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000596 | DISTRICT 23 - FRESNO | NTNC | NT - OTHER NON-TRANSIENT AREA
CA1000599 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000600 | DISTRICT 23 - FRESNO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1000601 | DISTRICT 23 - FRESNO | NC | T - RESTAURANT
CA1000602 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000606 | DISTRICT 23 - FRESNO | NC | T - RESTAURANT
CA1000607 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000608 | DISTRICT 23 - FRESNO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1000609 | DISTRICT 23 - FRESNO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1000611 | DISTRICT 23 - FRESNO | NC | T - RETAIL EMPLOYEES
CA1000613 | DISTRICT 23 - FRESNO | NC | T - SUMMER CAMP
CA1000614 | DISTRICT 23 - FRESNO | NC | O - OTHER AREA
CA1000619 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000619 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000620 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000621 | DISTRICT 23 - FRESNO | NC | T - RESTAURANT
CA1000625 | DISTRICT 23 - FRESNO | NC | T - RESTAURANT
CA1000626 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000627 | DISTRICT 23 - FRESNO | C | NT - OTHER NON-TRANSIENT AREA
CA1000629 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000630 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000634 | DISTRICT 23 - FRESNO | NC | T - RESTAURANT
CA1000635 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000637 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000639 | DISTRICT 23 - FRESNO | NTNC | T - OTHER TRANSIENT AREA
CA1000641 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000643 | DISTRICT 23 - FRESNO | NTNC | NT - OTHER NON-TRANSIENT AREA
CA1000644 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000645 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000647 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000648 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000649 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000650 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000652 | DISTRICT 23 - FRESNO | NC | T - SERVICE STATION
CA1000654 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000664 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1000665 | DISTRICT 23 - FRESNO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1000666 | DISTRICT 23 - FRESNO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1000667 | DISTRICT 23 - FRESNO | NC | T - OTHER TRANSIENT AREA
CA1000670 | DISTRICT 23 - FRESNO | NC | T - RESTAURANT
CA1000671 | DISTRICT 23 - FRESNO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1009020 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1009023 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1009027 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1009028 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1009039 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1009051 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1009078 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1009091 | DISTRICT 23 - FRESNO | NTNC | R - OTHER RESIDENTIAL AREA
CA1009111 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1009120 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1009129 | DISTRICT 23 - FRESNO | NC | R - RESIDENTIAL AREA
CA1009147 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1009179 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1009214 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1009222 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1009232 | DISTRICT 23 - FRESNO | C | R - OTHER RESIDENTIAL AREA
CA1009256 | DISTRICT 23 - FRESNO | NC | R - OTHER RESIDENTIAL AREA
CA1010001 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1010003 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1010004 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010005 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010006 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010007 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA1010013 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010017 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010018 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010019 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010020 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010021 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010023 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010024 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1010025 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010026 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1010027 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010028 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010029 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010030 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010034 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010035 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010039 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010042 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1010044 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010049 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010051 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010052 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010053 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010055 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010057 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1010060 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA1010062 | DISTRICT 23 - FRESNO | C | R - RESIDENTIAL AREA
CA1010339 | DISTRICT 12 - VISALIA | C | NT - SCHOOL
CA1010500 | DISTRICT 23 - FRESNO | NC | T - RECREATION AREA
CA1010501 | DISTRICT 23 - FRESNO | C | T - RECREATION AREA
CA1010800 | DISTRICT 23 - FRESNO | C | NT - INSTITUTION
CA1100101 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1100102 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1100103 | DISTRICT 21 - VALLEY | NC | T - OTHER TRANSIENT AREA
CA1100104 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL
CA1100203 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA1100206 | DISTRICT 21 - VALLEY | NC | T - HOTEL/MOTEL
CA1100221 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA1100229 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA1100232 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1100237 | DISTRICT 21 - VALLEY | C | R - MOBILE HOME PARK
CA1100250 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA1100254 | DISTRICT 21 - VALLEY | C | T - RECREATION AREA
CA1100257 | DISTRICT 21 - VALLEY | NC | T - HIGHWAY REST AREA
CA1100258 | DISTRICT 21 - VALLEY | NC | T - HIGHWAY REST AREA
CA1100404 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA1100413 | DISTRICT 21 - VALLEY | C | R - MOBILE HOME PARK
CA1100436 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA1100439 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA1100440 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL
CA1100443 | DISTRICT 21 - VALLEY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1100444 | DISTRICT 21 - VALLEY | C | R - MOBILE HOME PARK
CA1100445 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA1100448 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL
CA1100452 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA1100527 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL
CA1100616 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA1100642 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA1100711 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA1100749 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL
CA1105001 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1105003 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1105004 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1105005 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1105006 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1105007 | DISTRICT 21 - VALLEY | NC | T - OTHER TRANSIENT AREA
CA1110001 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA1110002 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA1110003 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA1110300 | DISTRICT 21 - VALLEY | NC | T - SECONDARY RESIDENCES
CA1110800 | DISTRICT 21 - VALLEY | NTNC | NT - INSTITUTION
CA1200500 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1200501 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200501 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200509 | DISTRICT 01 - KLAMATH | NC | NT - MEDICAL FACILITY
CA1200518 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200522 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA1200538 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200541 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200544 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200546 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA1200547 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200553 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200566 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200579 | DISTRICT 01 - KLAMATH | NTNC | R - RESIDENTIAL AREA
CA1200587 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200588 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200590 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200591 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200592 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200597 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA1200600 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1200637 | DISTRICT 01 - KLAMATH | NC | T - HOTEL/MOTEL
CA1200643 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK
CA1200648 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA1200671 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200681 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA1200684 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA1200687 | DISTRICT 01 - KLAMATH | C | T - OTHER TRANSIENT AREA
CA1200689 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA1200701 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200704 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1200705 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1200706 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK
CA1200707 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200710 | DISTRICT 01 - KLAMATH | NC | T - HOTEL/MOTEL
CA1200715 | DISTRICT 01 - KLAMATH | C | R - OTHER RESIDENTIAL AREA
CA1200718 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200728 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA1200729 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1200733 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1200754 | DISTRICT 01 - KLAMATH | NC | T - HIGHWAY REST AREA
CA1200772 | DISTRICT 01 - KLAMATH | NC | T - HOTEL/MOTEL
CA1200773 | DISTRICT 01 - KLAMATH | NC | T - SUMMER CAMP
CA1200776 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1200778 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA1200793 | DISTRICT 01 - KLAMATH | NC | T - RESTAURANT
CA1200798 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1200817 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA1200823 | DISTRICT 01 - KLAMATH | NC | T - RESTAURANT
CA1200831 | DISTRICT 01 - KLAMATH | NC | T - RESTAURANT
CA1206001 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA1206002 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1206004 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1206005 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1206011 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1206012 | DISTRICT 01 - KLAMATH | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1206013 | DISTRICT 01 - KLAMATH | NC | T - SUMMER CAMP
CA1206014 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA1206015 | DISTRICT 01 - KLAMATH | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1206016 | DISTRICT 01 - KLAMATH | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1210001 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1210002 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA
CA1210004 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1210006 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1210007 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1210008 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1210009 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1210010 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA
CA1210011 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1210012 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA
CA1210013 | DISTRICT 01 - KLAMATH | C | O - WHOLESALER (SELLS WATER)
CA1210015 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1210016 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA
CA1210017 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA
CA1210018 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1210019 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA
CA1210020 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1210021 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA
CA1210022 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1210023 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA1210024 | DISTRICT 01 - KLAMATH | C | O - OTHER AREA
CA1210307 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1210308 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1210312 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA1210314 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1210319 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1210320 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1210321 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1210322 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1210324 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA1210800 | DISTRICT 01 - KLAMATH | C | NT - INSTITUTION
CA1210801 | DISTRICT 01 - KLAMATH | C | NT - INSTITUTION
CA1300009 | LPA43 - IMPERIAL COUNTY | C | R - RESIDENTIAL AREA
CA1300018 | LPA43 - IMPERIAL COUNTY | C | T - SECONDARY RESIDENCES
CA1300513 | LPA43 - IMPERIAL COUNTY | C | R - RESIDENTIAL AREA
CA1300514 | LPA43 - IMPERIAL COUNTY | C | R - RESIDENTIAL AREA
CA1300517 | LPA43 - IMPERIAL COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1300540 | LPA43 - IMPERIAL COUNTY | NC | R - MOBILE HOME PARK
CA1300544 | LPA43 - IMPERIAL COUNTY | SSWS | O - OTHER AREA
CA1300546 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK
CA1300549 | LPA43 - IMPERIAL COUNTY | NTNC | NT - SCHOOL
CA1300550 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK
CA1300553 | LPA43 - IMPERIAL COUNTY | NTNC | NT - SCHOOL
CA1300554 | LPA43 - IMPERIAL COUNTY | NTNC | NT - SCHOOL
CA1300555 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK
CA1300556 | LPA43 - IMPERIAL COUNTY | NTNC | NT - SCHOOL
CA1300559 | LPA43 - IMPERIAL COUNTY | NC | R - MOBILE HOME PARK
CA1300560 | LPA43 - IMPERIAL COUNTY | NTNC | NT - SCHOOL
CA1300561 | LPA43 - IMPERIAL COUNTY | NC | T - RECREATION AREA
CA1300564 | LPA43 - IMPERIAL COUNTY | NC | R - MOBILE HOME PARK
CA1300571 | DISTRICT 14 - SAN DIEGO | NTNC | NT - INSTITUTION
CA1300572 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK
CA1300574 | LPA43 - IMPERIAL COUNTY | NC | R - MOBILE HOME PARK
CA1300575 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK
CA1300579 | LPA43 - IMPERIAL COUNTY | NTNC | NT - SCHOOL
CA1300583 | DISTRICT 14 - SAN DIEGO | NC | T - HIGHWAY REST AREA
CA1300588 | LPA43 - IMPERIAL COUNTY | C | R - RESIDENTIAL AREA
CA1300591 | LPA43 - IMPERIAL COUNTY | C | R - RESIDENTIAL AREA
CA1300614 | LPA43 - IMPERIAL COUNTY | NC | T - RECREATION AREA
CA1300616 | LPA43 - IMPERIAL COUNTY | C | R - RESIDENTIAL AREA
CA1300617 | LPA43 - IMPERIAL COUNTY | NC | T - RECREATION AREA
CA1300620 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK
CA1300622 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK
CA1300624 | LPA43 - IMPERIAL COUNTY | NC | R - MOBILE HOME PARK
CA1300626 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK
CA1300627 | LPA43 - IMPERIAL COUNTY | NC | R - RESIDENTIAL AREA
CA1300628 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK
CA1300629 | LPA43 - IMPERIAL COUNTY | C | R - MOBILE HOME PARK
CA1300632 | LPA43 - IMPERIAL COUNTY | NC | T - RESTAURANT
CA1300635 | LPA43 - IMPERIAL COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1300637 | LPA43 - IMPERIAL COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1300638 | LPA43 - IMPERIAL COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1300642 | LPA43 - IMPERIAL COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1300643 | LPA43 - IMPERIAL COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1300644 | LPA43 - IMPERIAL COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1300652 | LPA43 - IMPERIAL COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1300653 | LPA43 - IMPERIAL COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1300654 | LPA43 - IMPERIAL COUNTY | NC | O - INTERSTATE CARRIER
CA1300655 | LPA43 - IMPERIAL COUNTY | NC | T - RESTAURANT
CA1300656 | LPA43 - IMPERIAL COUNTY | NC | T - RESTAURANT
CA1300657 | LPA43 - IMPERIAL COUNTY | NC | R - MOBILE HOME PARK
CA1300661 | LPA43 - IMPERIAL COUNTY | NTNC | NT - INSTITUTION
CA1300662 | LPA43 - IMPERIAL COUNTY | NC | R - MOBILE HOME PARK
CA1300664 | LPA43 - IMPERIAL COUNTY | C | O - OTHER AREA
CA1300667 | LPA43 - IMPERIAL COUNTY | NC | T - OTHER TRANSIENT AREA
CA1300668 | LPA43 - IMPERIAL COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1300669 | LPA43 - IMPERIAL COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1300676 | LPA43 - IMPERIAL COUNTY | NTNC | O - OTHER AREA
CA1300678 | LPA43 - IMPERIAL COUNTY | NC | T - RECREATION AREA
CA1300679 | LPA43 - IMPERIAL COUNTY | NTNC | O - OTHER AREA
CA1300682 | LPA43 - IMPERIAL COUNTY | NC | O - OTHER AREA
CA1300683 | LPA43 - IMPERIAL COUNTY | NC | T - SERVICE STATION
CA1300685 | LPA43 - IMPERIAL COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1300686 | LPA43 - IMPERIAL COUNTY | NC | T - SERVICE STATION
CA1300687 | LPA43 - IMPERIAL COUNTY | NC | T - RESTAURANT
CA1310001 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA1310002 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA1310003 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA
CA1310004 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA1310005 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA
CA1310006 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA1310007 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA1310008 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA1310013 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA
CA1310014 | DISTRICT 14 - SAN DIEGO | NP | O - WHOLESALER (SELLS WATER)
CA1310016 | DISTRICT 14 - SAN DIEGO | NTNC | T - OTHER TRANSIENT AREA
CA1310019 | DISTRICT 14 - SAN DIEGO | NTNC | NT - INSTITUTION
CA1310300 | DISTRICT 14 - SAN DIEGO | NC | T - RECREATION AREA
CA1310301 | DISTRICT 14 - SAN DIEGO | NC | T - RECREATION AREA
CA1310302 | DISTRICT 14 - SAN DIEGO | NC | T - RECREATION AREA
CA1310700 | DISTRICT 14 - SAN DIEGO | C | T - SECONDARY RESIDENCES
CA1310800 | DISTRICT 14 - SAN DIEGO | C | NT - INSTITUTION
CA1310801 | DISTRICT 14 - SAN DIEGO | C | NT - INSTITUTION
CA1400002 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400004 | DISTRICT 13 - SAN BERNARDINO | C | T - SECONDARY RESIDENCES
CA1400005 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400006 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400007 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400009 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400010 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400011 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400012 | DISTRICT 13 - SAN BERNARDINO | NC | T - SERVICE STATION
CA1400013 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400014 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400015 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400019 | DISTRICT 13 - SAN BERNARDINO | NTNC | NT - SCHOOL
CA1400020 | DISTRICT 13 - SAN BERNARDINO | C | R - MOBILE HOME PARK
CA1400024 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400025 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400026 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400027 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400030 | DISTRICT 13 - SAN BERNARDINO | C | R - MOBILE HOME PARK
CA1400031 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400034 | DISTRICT 13 - SAN BERNARDINO | C | R - MOBILE HOME PARK
CA1400035 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400036 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400037 | DISTRICT 13 - SAN BERNARDINO | C | R - MOBILE HOME PARK
CA1400040 | DISTRICT 13 - SAN BERNARDINO | NC | T - SECONDARY RESIDENCES
CA1400043 | DISTRICT 13 - SAN BERNARDINO | NC | T - RESTAURANT
CA1400044 | DISTRICT 13 - SAN BERNARDINO | NC | T - HOTEL/MOTEL
CA1400045 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400046 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400047 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400049 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400051 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400055 | DISTRICT 13 - SAN BERNARDINO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1400056 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400058 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400059 | DISTRICT 13 - SAN BERNARDINO | C | R - MOBILE HOME PARK
CA1400064 | DISTRICT 13 - SAN BERNARDINO | NTNC | NT - SCHOOL
CA1400066 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400067 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400068 | DISTRICT 13 - SAN BERNARDINO | NTNC | NT - SCHOOL
CA1400069 | DISTRICT 13 - SAN BERNARDINO | NC | T - HOTEL/MOTEL
CA1400070 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400072 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400078 | DISTRICT 13 - SAN BERNARDINO | C | R - OTHER RESIDENTIAL AREA
CA1400088 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400096 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400098 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400099 | DISTRICT 13 - SAN BERNARDINO | C | R - MOBILE HOME PARK
CA1400102 | DISTRICT 13 - SAN BERNARDINO | NTNC | O - WHOLESALER (SELLS WATER)
CA1400109 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400110 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400111 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400114 | DISTRICT 13 - SAN BERNARDINO | NC | T - OTHER TRANSIENT AREA
CA1400115 | DISTRICT 13 - SAN BERNARDINO | NC | T - OTHER TRANSIENT AREA
CA1400131 | DISTRICT 13 - SAN BERNARDINO | NC | T - RESTAURANT
CA1400133 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400135 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400136 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400144 | DISTRICT 13 - SAN BERNARDINO | C | R - MOBILE HOME PARK
CA1400147 | DISTRICT 13 - SAN BERNARDINO | NC | T - RESTAURANT
CA1400155 | DISTRICT 13 - SAN BERNARDINO | C | R - OTHER RESIDENTIAL AREA
CA1400161 | DISTRICT 13 - SAN BERNARDINO | NC | NT - SCHOOL
CA1400181 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400182 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400183 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400184 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400185 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400186 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400191 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400192 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400193 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400194 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400195 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400500 | DISTRICT 13 - SAN BERNARDINO | NC | T - HOTEL/MOTEL
CA1400503 | DISTRICT 13 - SAN BERNARDINO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1400504 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400505 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400506 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400511 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400516 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400518 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1400522 | DISTRICT 13 - SAN BERNARDINO | NTNC | NT - SCHOOL
CA1400524 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400525 | DISTRICT 13 - SAN BERNARDINO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1400526 | DISTRICT 13 - SAN BERNARDINO | NTNC | NT - SCHOOL
CA1400527 | DISTRICT 13 - SAN BERNARDINO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1400528 | DISTRICT 13 - SAN BERNARDINO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1400529 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400531 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400532 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1400534 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1410001 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1410002 | DISTRICT 13 - SAN BERNARDINO | C | O - WHOLESALER (SELLS WATER)
CA1410003 | DISTRICT 13 - SAN BERNARDINO | C | O - WHOLESALER (SELLS WATER)
CA1410004 | DISTRICT 13 - SAN BERNARDINO | C | O - WHOLESALER (SELLS WATER)
CA1410005 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1410006 | DISTRICT 13 - SAN BERNARDINO | C | R - MUNICIPALITY
CA1410007 | DISTRICT 13 - SAN BERNARDINO | C | R - MOBILE HOME PARK
CA1410008 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1410009 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA1410500 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1410502 | DISTRICT 13 - SAN BERNARDINO | C | T - RECREATION AREA
CA1410503 | DISTRICT 13 - SAN BERNARDINO | C | R - OTHER RESIDENTIAL AREA
CA1410504 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1410505 | DISTRICT 13 - SAN BERNARDINO | C | T - RECREATION AREA
CA1410506 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1410507 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1410509 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1410510 | DISTRICT 13 - SAN BERNARDINO | C | O - WHOLESALER (SELLS WATER)
CA1410511 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA1410800 | DISTRICT 13 - SAN BERNARDINO | C | NT - INSTITUTION
CA1500050 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1500090 | DISTRICT 12 - VISALIA | NC | T - HOTEL/MOTEL
CA1500096 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500152 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500209 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500211 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500216 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500231 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500251 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500252 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500289 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500290 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500296 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500314 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500324 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500327 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500333 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500336 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500340 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500341 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500344 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500349 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500364 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500371 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500374 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500378 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500380 | DISTRICT 12 - VISALIA | C | R - MOBILE HOME PARK
CA1500393 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500396 | DISTRICT 19 - TEHACHAPI | NC | R - MOBILE HOME PARK
CA1500398 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500401 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500404 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500405 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500406 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500407 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500409 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500413 | DISTRICT 19 - TEHACHAPI | C | T - OTHER TRANSIENT AREA
CA1500415 | DISTRICT 19 - TEHACHAPI | NTNC | T - HIGHWAY REST AREA
CA1500424 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500426 | DISTRICT 19 - TEHACHAPI | C | R - OTHER RESIDENTIAL AREA
CA1500436 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500442 | DISTRICT 19 - TEHACHAPI | C | R - OTHER RESIDENTIAL AREA
CA1500443 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500447 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500448 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500449 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500452 | DISTRICT 12 - VISALIA | C | R - MOBILE HOME PARK
CA1500455 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500458 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500459 | DISTRICT 19 - TEHACHAPI | C | R - MOBILE HOME PARK
CA1500461 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500464 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1500465 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500466 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500475 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500478 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500481 | DISTRICT 19 - TEHACHAPI | C | R - MOBILE HOME PARK
CA1500483 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500485 | DISTRICT 19 - TEHACHAPI | C | R - MOBILE HOME PARK
CA1500489 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500491 | DISTRICT 12 - VISALIA | NTNC | T - HIGHWAY REST AREA
CA1500493 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500494 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500495 | DISTRICT 12 - VISALIA | NTNC | R - RESIDENTIAL AREA
CA1500507 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500516 | DISTRICT 12 - VISALIA | C | R - OTHER RESIDENTIAL AREA
CA1500517 | DISTRICT 12 - VISALIA | NTNC | R - RESIDENTIAL AREA
CA1500518 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500525 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500535 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500540 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500542 | DISTRICT 19 - TEHACHAPI | C | R - MOBILE HOME PARK
CA1500543 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500544 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500546 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500550 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500553 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500554 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500555 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500556 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500557 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500560 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500561 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500563 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500564 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500566 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500569 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500571 | DISTRICT 19 - TEHACHAPI | C | R - MOBILE HOME PARK
CA1500574 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1500575 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500578 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500579 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500584 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500585 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500588 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500591 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1500593 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500597 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1500599 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1500600 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1502012 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1502029 | DISTRICT 12 - VISALIA | NC | T - HIGHWAY REST AREA
CA1502034 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1502042 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502044 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502056 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1502066 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1502068 | DISTRICT 19 - TEHACHAPI | NTNC | NT - SCHOOL
CA1502073 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502074 | DISTRICT 19 - TEHACHAPI | NTNC | NT - SCHOOL
CA1502093 | DISTRICT 19 - TEHACHAPI | NC | T - RESTAURANT
CA1502133 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1502134 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502154 | DISTRICT 12 - VISALIA | NTNC | NT - SCHOOL
CA1502164 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1502194 | DISTRICT 19 - TEHACHAPI | NC | R - MOBILE HOME PARK
CA1502213 | DISTRICT 19 - TEHACHAPI | NC | T - HOTEL/MOTEL
CA1502217 | DISTRICT 19 - TEHACHAPI | NC | T - OTHER TRANSIENT AREA
CA1502221 | DISTRICT 12 - VISALIA | NTNC | NT - SCHOOL
CA1502223 | DISTRICT 19 - TEHACHAPI | NC | T - OTHER TRANSIENT AREA
CA1502225 | DISTRICT 19 - TEHACHAPI | NC | T - HOTEL/MOTEL
CA1502229 | DISTRICT 12 - VISALIA | NTNC | NT - SCHOOL
CA1502231 | DISTRICT 19 - TEHACHAPI | NTNC | NT - SCHOOL
CA1502232 | DISTRICT 19 - TEHACHAPI | C | R - MOBILE HOME PARK
CA1502247 | DISTRICT 19 - TEHACHAPI | C | R - MOBILE HOME PARK
CA1502249 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502260 | DISTRICT 19 - TEHACHAPI | NTNC | NT - SCHOOL
CA1502277 | DISTRICT 19 - TEHACHAPI | NC | T - OTHER TRANSIENT AREA
CA1502315 | DISTRICT 19 - TEHACHAPI | C | NT - INSTITUTION
CA1502317 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502319 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502320 | DISTRICT 12 - VISALIA | C | NT - INSTITUTION
CA1502323 | DISTRICT 12 - VISALIA | NC | T - RECREATION AREA
CA1502325 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502327 | DISTRICT 19 - TEHACHAPI | NC | T - OTHER TRANSIENT AREA
CA1502383 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1502398 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1502418 | DISTRICT 19 - TEHACHAPI | NC | T - HOTEL/MOTEL
CA1502422 | DISTRICT 19 - TEHACHAPI | NC | T - HIGHWAY REST AREA
CA1502449 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1502465 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1502524 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502545 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1502561 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1502564 | DISTRICT 19 - TEHACHAPI | C | R - MOBILE HOME PARK
CA1502569 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1502572 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502575 | DISTRICT 19 - TEHACHAPI | NC | T - SECONDARY RESIDENCES
CA1502580 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1502581 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1502595 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1502600 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1502607 | DISTRICT 19 - TEHACHAPI | NTNC | NT - SCHOOL
CA1502608 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1502615 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1502619 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1502620 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1502622 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1502629 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1502645 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1502653 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1502659 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1502663 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1502667 | DISTRICT 19 - TEHACHAPI | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1502670 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1502673 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502680 | DISTRICT 19 - TEHACHAPI | NC | R - MOBILE HOME PARK
CA1502682 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502683 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502686 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502687 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502688 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502689 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502690 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1502691 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1502695 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1502697 | DISTRICT 19 - TEHACHAPI | NTNC | R - RESIDENTIAL AREA
CA1502699 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1502717 | DISTRICT 19 - TEHACHAPI | NC | T - OTHER TRANSIENT AREA
CA1502744 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1502750 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1502753 | DISTRICT 19 - TEHACHAPI | NTNC | T - OTHER TRANSIENT AREA
CA1502757 | DISTRICT 19 - TEHACHAPI | NC | R - OTHER RESIDENTIAL AREA
CA1502759 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1502763 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1502771 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1502799 | DISTRICT 19 - TEHACHAPI | NC | T - HIGHWAY REST AREA
CA1502820 | DISTRICT 12 - VISALIA | NTNC | T - HIGHWAY REST AREA
CA1502826 | DISTRICT 12 - VISALIA | NC | T - OTHER TRANSIENT AREA
CA1503093 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503104 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503105 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1503140 | DISTRICT 19 - TEHACHAPI | NTNC | NT - SCHOOL
CA1503182 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503194 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503206 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1503209 | DISTRICT 12 - VISALIA | NTNC | T - SECONDARY RESIDENCES
CA1503215 | DISTRICT 12 - VISALIA | NC | T - RECREATION AREA
CA1503219 | DISTRICT 19 - TEHACHAPI | NC | T - RESTAURANT
CA1503226 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1503230 | DISTRICT 19 - TEHACHAPI | NC | T - OTHER TRANSIENT AREA
CA1503231 | DISTRICT 12 - VISALIA | NC | T - OTHER TRANSIENT AREA
CA1503232 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503243 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503249 | DISTRICT 12 - VISALIA | NC | T - OTHER TRANSIENT AREA
CA1503270 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1503275 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503290 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503292 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503305 | DISTRICT 12 - VISALIA | NC | T - RESTAURANT
CA1503310 | DISTRICT 12 - VISALIA | NC | T - SECONDARY RESIDENCES
CA1503319 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1503329 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1503330 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503336 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503341 | DISTRICT 19 - TEHACHAPI | NTNC | T - HIGHWAY REST AREA
CA1503349 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503350 | DISTRICT 19 - TEHACHAPI | NC | NT - INSTITUTION
CA1503360 | DISTRICT 19 - TEHACHAPI | NTNC | T - RESTAURANT
CA1503368 | DISTRICT 19 - TEHACHAPI | NTNC | NT - SCHOOL
CA1503373 | DISTRICT 19 - TEHACHAPI | NC | T - OTHER TRANSIENT AREA
CA1503374 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503378 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1503380 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503384 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503392 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1503397 | DISTRICT 19 - TEHACHAPI | NC | T - OTHER TRANSIENT AREA
CA1503398 | DISTRICT 12 - VISALIA | NC | T - SERVICE STATION
CA1503440 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503475 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1503509 | DISTRICT 12 - VISALIA | C | R - OTHER RESIDENTIAL AREA
CA1503515 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503521 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503526 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1503536 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1503537 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503543 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503558 | DISTRICT 19 - TEHACHAPI | NC | NT - INSTITUTION
CA1503565 | DISTRICT 19 - TEHACHAPI | NC | T - OTHER TRANSIENT AREA
CA1503570 | DISTRICT 19 - TEHACHAPI | NC | T - OTHER TRANSIENT AREA
CA1503576 | DISTRICT 19 - TEHACHAPI | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1503578 | DISTRICT 12 - VISALIA | NC | T - HIGHWAY REST AREA
CA1503623 | DISTRICT 12 - VISALIA | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1503629 | DISTRICT 19 - TEHACHAPI | NC | T - OTHER TRANSIENT AREA
CA1503642 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503645 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503646 | DISTRICT 19 - TEHACHAPI | NC | T - SECONDARY RESIDENCES
CA1503648 | DISTRICT 12 - VISALIA | NC | O - OTHER AREA
CA1503649 | DISTRICT 12 - VISALIA | NC | O - OTHER AREA
CA1503650 | DISTRICT 12 - VISALIA | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1503651 | DISTRICT 19 - TEHACHAPI | NC | T - OTHER TRANSIENT AREA
CA1503652 | DISTRICT 12 - VISALIA | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1503653 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503654 | DISTRICT 12 - VISALIA | NC | T - SERVICE STATION
CA1503655 | DISTRICT 19 - TEHACHAPI | NC | T - OTHER TRANSIENT AREA
CA1503656 | DISTRICT 19 - TEHACHAPI | NC | T - OTHER TRANSIENT AREA
CA1503657 | DISTRICT 12 - VISALIA | NC | R - RESIDENTIAL AREA
CA1503658 | DISTRICT 12 - VISALIA | NC | O - OTHER AREA
CA1503660 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503661 | DISTRICT 19 - TEHACHAPI | NC | NT - OTHER NON-TRANSIENT AREA
CA1503662 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503663 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503664 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503666 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503667 | DISTRICT 12 - VISALIA | NC | O - OTHER AREA
CA1503668 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1503669 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1503671 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503672 | DISTRICT 19 - TEHACHAPI | NC | T - HIGHWAY REST AREA
CA1503676 | DISTRICT 12 - VISALIA | NC | T - RESTAURANT
CA1503677 | DISTRICT 19 - TEHACHAPI | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1503678 | DISTRICT 19 - TEHACHAPI | NTNC | NT - OTHER NON-TRANSIENT AREA
CA1503679 | DISTRICT 19 - TEHACHAPI | NC | T - OTHER TRANSIENT AREA
CA1503680 | DISTRICT 19 - TEHACHAPI | NC | T - OTHER TRANSIENT AREA
CA1503681 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503682 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503683 | DISTRICT 19 - TEHACHAPI | NTNC | NT - SCHOOL
CA1503684 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1503685 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503686 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1503687 | DISTRICT 19 - TEHACHAPI | NC | T - SERVICE STATION
CA1503688 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1504000 | DISTRICT 12 - VISALIA | NTNC | NT - OTHER NON-TRANSIENT AREA
CA1504001 | DISTRICT 12 - VISALIA | NTNC | T - OTHER TRANSIENT AREA
CA1504002 | DISTRICT 12 - VISALIA | NC | T - OTHER TRANSIENT AREA
CA1504003 | DISTRICT 12 - VISALIA | NTNC | NT - OTHER NON-TRANSIENT AREA
CA1504004 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1504005 | DISTRICT 12 - VISALIA | NTNC | NT - OTHER NON-TRANSIENT AREA
CA1504006 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1504007 | DISTRICT 12 - VISALIA | NTNC | T - OTHER TRANSIENT AREA
CA1504008 | DISTRICT 12 - VISALIA | NTNC | NT - OTHER NON-TRANSIENT AREA
CA1504009 | DISTRICT 12 - VISALIA | NC | T - SERVICE STATION
CA1510001 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1510002 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510003 | DISTRICT 12 - VISALIA | C | O - WHOLESALER (SELLS WATER)
CA1510004 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1510005 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1510006 | DISTRICT 12 - VISALIA | C | O - WHOLESALER (SELLS WATER)
CA1510007 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510009 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510011 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1510012 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1510013 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1510014 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510015 | DISTRICT 12 - VISALIA | C | O - WHOLESALER (SELLS WATER)
CA1510016 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510017 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510018 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510019 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1510020 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510021 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1510022 | DISTRICT 12 - VISALIA | C | O - WHOLESALER (SELLS WATER)
CA1510023 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510024 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1510025 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510026 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510027 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510028 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510029 | DISTRICT 12 - VISALIA | C | O - WHOLESALER (SELLS WATER)
CA1510031 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1510032 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510033 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510036 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510038 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510039 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510040 | DISTRICT 12 - VISALIA | C | O - WHOLESALER (SELLS WATER)
CA1510042 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510043 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510045 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510046 | DISTRICT 12 - VISALIA | C | O - WHOLESALER (SELLS WATER)
CA1510049 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510051 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510052 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510053 | DISTRICT 19 - TEHACHAPI | C | O - WHOLESALER (SELLS WATER)
CA1510054 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510055 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1510056 | DISTRICT 19 - TEHACHAPI | C | R - RESIDENTIAL AREA
CA1510300 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1510301 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1510302 | DISTRICT 19 - TEHACHAPI | NC | T - RECREATION AREA
CA1510701 | DISTRICT 19 - TEHACHAPI | C | NT - INSTITUTION
CA1510702 | DISTRICT 19 - TEHACHAPI | NTNC | NT - INSTITUTION
CA1510703 | DISTRICT 19 - TEHACHAPI | C | NT - INSTITUTION
CA1510800 | DISTRICT 19 - TEHACHAPI | C | NT - INSTITUTION
CA1510801 | DISTRICT 12 - VISALIA | C | NT - INSTITUTION
CA1510802 | DISTRICT 12 - VISALIA | C | NT - INSTITUTION
CA1600002 | LPA46 - KINGS COUNTY | C | R - MOBILE HOME PARK
CA1600007 | LPA46 - KINGS COUNTY | SSWS | R - RESIDENTIAL AREA
CA1600009 | LPA46 - KINGS COUNTY | NTNC | NT - SCHOOL
CA1600011 | LPA46 - KINGS COUNTY | NTNC | NT - SCHOOL
CA1600013 | LPA46 - KINGS COUNTY | NTNC | NT - SCHOOL
CA1600015 | LPA46 - KINGS COUNTY | NTNC | NT - SCHOOL
CA1600017 | LPA46 - KINGS COUNTY | NTNC | NT - SCHOOL
CA1600018 | LPA46 - KINGS COUNTY | SSWS | R - RESIDENTIAL AREA
CA1600022 | LPA46 - KINGS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1600023 | DISTRICT 12 - VISALIA | C | R - OTHER RESIDENTIAL AREA
CA1600029 | LPA46 - KINGS COUNTY | NC | T - RECREATION AREA
CA1600032 | LPA46 - KINGS COUNTY | NC | T - HOTEL/MOTEL
CA1600050 | LPA46 - KINGS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1600232 | LPA46 - KINGS COUNTY | SSWS | R - RESIDENTIAL AREA
CA1600249 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1600256 | LPA46 - KINGS COUNTY | SSWS | T - SECONDARY RESIDENCES
CA1600265 | LPA46 - KINGS COUNTY | NC | T - RECREATION AREA
CA1600270 | LPA46 - KINGS COUNTY | NC | T - RECREATION AREA
CA1600285 | LPA46 - KINGS COUNTY | SSWS | NT - SCHOOL
CA1600288 | LPA46 - KINGS COUNTY | SSWS | T - SECONDARY RESIDENCES
CA1600293 | LPA46 - KINGS COUNTY | C | T - SECONDARY RESIDENCES
CA1600303 | DISTRICT 12 - VISALIA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1600507 | LPA46 - KINGS COUNTY | C | R - RESIDENTIAL AREA
CA1600602 | LPA46 - KINGS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1600603 | LPA46 - KINGS COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1600604 | LPA46 - KINGS COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1600605 | LPA46 - KINGS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1600607 | LPA46 - KINGS COUNTY | NC | NT - INSTITUTION
CA1600608 | LPA46 - KINGS COUNTY | NC | T - RECREATION AREA
CA1600609 | LPA46 - KINGS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1610001 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1610002 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1610003 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1610004 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1610005 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1610006 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1610007 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1610009 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA1610700 | DISTRICT 12 - VISALIA | C | T - OTHER TRANSIENT AREA
CA1700502 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700508 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700510 | DISTRICT 03 - MENDOCINO | NC | R - RESIDENTIAL AREA
CA1700511 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA1700518 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700519 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700527 | DISTRICT 03 - MENDOCINO | C | R - OTHER RESIDENTIAL AREA
CA1700533 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA1700536 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700546 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK
CA1700549 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700554 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700561 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700568 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700579 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700580 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700584 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK
CA1700589 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK
CA1700592 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700595 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700596 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700597 | DISTRICT 03 - MENDOCINO | NC | R - RESIDENTIAL AREA
CA1700599 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA1700601 | DISTRICT 03 - MENDOCINO | NC | R - OTHER RESIDENTIAL AREA
CA1700603 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA1700604 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA1700606 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700609 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK
CA1700610 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK
CA1700617 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA1700627 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA1700628 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA1700630 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700633 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA1700634 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA1700638 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA1700650 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA1700657 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700659 | DISTRICT 03 - MENDOCINO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1700670 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA1700674 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700676 | DISTRICT 03 - MENDOCINO | NC | T - SUMMER CAMP
CA1700677 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA1700685 | DISTRICT 03 - MENDOCINO | NC | T - RESTAURANT
CA1700695 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA1700698 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA1700702 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1700704 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA1700710 | DISTRICT 03 - MENDOCINO | NC | T - SERVICE STATION
CA1700712 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA1700713 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA1700715 | DISTRICT 03 - MENDOCINO | NC | T - RESTAURANT
CA1700716 | DISTRICT 03 - MENDOCINO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA1700725 | DISTRICT 03 - MENDOCINO | NC | T - RESTAURANT
CA1700727 | DISTRICT 03 - MENDOCINO | NC | T - SERVICE STATION
CA1700728 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA1700730 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA1700731 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA1700733 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA1700734 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA1700736 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA1700738 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA1700739 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA1710001 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES
CA1710002 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES
CA1710003 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES
CA1710004 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1710005 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES
CA1710006 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES
CA1710007 | DISTRICT 03 - MENDOCINO | C | O - WHOLESALER (SELLS WATER)
CA1710008 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES
CA1710009 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES
CA1710010 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES
CA1710011 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1710012 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1710013 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1710014 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1710015 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1710016 | DISTRICT 03 - MENDOCINO | NTNC | T - RECREATION AREA
CA1710018 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1710021 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1710022 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA1710800 | DISTRICT 03 - MENDOCINO | C | T - SECONDARY RESIDENCES
CA1800010 | DISTRICT 02 - LASSEN | NC | NT - INSTITUTION
CA1800028 | DISTRICT 02 - LASSEN | NC | T - RESTAURANT
CA1800202 | DISTRICT 02 - LASSEN | NTNC | NT - SCHOOL
CA1800503 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA1800511 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA1800512 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA1800514 | DISTRICT 02 - LASSEN | NC | R - RESIDENTIAL AREA
CA1800515 | DISTRICT 02 - LASSEN | NC | R - OTHER RESIDENTIAL AREA
CA1800516 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA1800522 | DISTRICT 02 - LASSEN | C | T - SUMMER CAMP
CA1800523 | DISTRICT 02 - LASSEN | C | R - MOBILE HOME PARK
CA1800524 | DISTRICT 02 - LASSEN | C | R - MOBILE HOME PARK
CA1800528 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA1800529 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA1800531 | DISTRICT 02 - LASSEN | NC | T - HIGHWAY REST AREA
CA1800534 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA1800557 | DISTRICT 02 - LASSEN | NC | NT - INSTITUTION
CA1800569 | DISTRICT 02 - LASSEN | NTNC | T - OTHER TRANSIENT AREA
CA1800573 | DISTRICT 02 - LASSEN | NTNC | NT - SCHOOL
CA1800574 | DISTRICT 02 - LASSEN | NTNC | NT - SCHOOL
CA1800575 | DISTRICT 02 - LASSEN | NTNC | NT - SCHOOL
CA1800576 | DISTRICT 02 - LASSEN | NTNC | NT - SCHOOL
CA1800577 | DISTRICT 02 - LASSEN | NTNC | NT - SCHOOL
CA1800585 | DISTRICT 02 - LASSEN | NTNC | NT - SCHOOL
CA1800589 | DISTRICT 02 - LASSEN | NC | T - HIGHWAY REST AREA
CA1800601 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA1800632 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA1800801 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA1805001 | DISTRICT 02 - LASSEN | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1805004 | DISTRICT 02 - LASSEN | C | NT - INSTITUTION
CA1805005 | DISTRICT 02 - LASSEN | NTNC | R - MOBILE HOME PARK
CA1805006 | DISTRICT 02 - LASSEN | NC | R - MOBILE HOME PARK
CA1805007 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA1805010 | DISTRICT 02 - LASSEN | NC | T - RETAIL EMPLOYEES
CA1805011 | DISTRICT 02 - LASSEN | NTNC | NT - OTHER NON-TRANSIENT AREA
CA1810001 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA1810002 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA1810003 | DISTRICT 02 - LASSEN | C | O - OTHER AREA
CA1810004 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA1810700 | DISTRICT 02 - LASSEN | NTNC | O - OTHER AREA
CA1810801 | DISTRICT 02 - LASSEN | NTNC | NT - INSTITUTION
CA1900007 | DISTRICT 16 - CENTRAL | C | NT - INSTITUTION
CA1900008 | LPA49 - LA COUNTY | NC | T - SUMMER CAMP
CA1900011 | LPA49 - LA COUNTY | NTNC | NT - INSTITUTION
CA1900018 | LPA49 - LA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1900020 | LPA49 - LA COUNTY | NC | T - RECREATION AREA
CA1900035 | LPA49 - LA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1900038 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900045 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900046 | DISTRICT 22 - ANGELES | C | NT - INSTITUTION
CA1900055 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900057 | LPA49 - LA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA1900058 | LPA49 - LA COUNTY | NC | T - RECREATION AREA
CA1900061 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900062 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900074 | LPA49 - LA COUNTY | C | T - OTHER TRANSIENT AREA
CA1900075 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900077 | LPA49 - LA COUNTY | NC | T - RECREATION AREA
CA1900078 | LPA49 - LA COUNTY | NC | T - RECREATION AREA
CA1900080 | LPA49 - LA COUNTY | NC | T - SUMMER CAMP
CA1900081 | LPA49 - LA COUNTY | NC | T - RESTAURANT
CA1900089 | LPA49 - LA COUNTY | NTNC | NT - INSTITUTION
CA1900092 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900100 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900102 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900130 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900143 | LPA49 - LA COUNTY | NC | T - RECREATION AREA
CA1900145 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900146 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900154 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900155 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900158 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900162 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900239 | LPA49 - LA COUNTY | NC | T - RECREATION AREA
CA1900244 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900301 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900303 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900304 | LPA49 - LA COUNTY | NC | T - RESTAURANT
CA1900509 | LPA49 - LA COUNTY | SSWS | R - RESIDENTIAL AREA
CA1900512 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900520 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900523 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1900527 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900529 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900537 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900541 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900542 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1900552 | LPA49 - LA COUNTY | NC | T - SUMMER CAMP
CA1900555 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1900556 | DISTRICT 15 - METROPOLITAN | NC | T - RECREATION AREA
CA1900563 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1900569 | DISTRICT 22 - ANGELES | NC | T - OTHER TRANSIENT AREA
CA1900571 | LPA49 - LA COUNTY | NC | O - WHOLESALER (SELLS WATER)
CA1900576 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900581 | LPA49 - LA COUNTY | NC | T - RECREATION AREA
CA1900583 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900586 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900588 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900594 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900599 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900603 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900612 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900616 | LPA49 - LA COUNTY | C | R - OTHER RESIDENTIAL AREA
CA1900636 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900649 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900679 | LPA49 - LA COUNTY | NTNC | NT - MEDICAL FACILITY
CA1900693 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900699 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900707 | LPA49 - LA COUNTY | NTNC | NT - SCHOOL
CA1900715 | LPA49 - LA COUNTY | NC | T - RESTAURANT
CA1900717 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900721 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900741 | LPA49 - LA COUNTY | NC | R - MOBILE HOME PARK
CA1900750 | LPA49 - LA COUNTY | NTNC | NT - SCHOOL
CA1900751 | LPA49 - LA COUNTY | NTNC | NT - SCHOOL
CA1900752 | LPA49 - LA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA1900761 | LPA49 - LA COUNTY | NC | T - RECREATION AREA
CA1900764 | DISTRICT 16 - CENTRAL | NC | T - RECREATION AREA
CA1900767 | LPA49 - LA COUNTY | C | T - OTHER TRANSIENT AREA
CA1900768 | LPA49 - LA COUNTY | NC | T - RESTAURANT
CA1900785 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900791 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900794 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900801 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900803 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1900804 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900808 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900809 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900817 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900820 | LPA49 - LA COUNTY | NC | T - RESTAURANT
CA1900843 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900849 | LPA49 - LA COUNTY | C | O - WHOLESALER (SELLS WATER)
CA1900868 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900886 | LPA49 - LA COUNTY | NTNC | NT - SCHOOL
CA1900894 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900901 | DISTRICT 16 - CENTRAL | C | T - OTHER TRANSIENT AREA
CA1900903 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900904 | DISTRICT 16 - CENTRAL | NTNC | T - OTHER TRANSIENT AREA
CA1900907 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900913 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900914 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900922 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900929 | LPA49 - LA COUNTY | NTNC | NT - MEDICAL FACILITY
CA1900936 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1900937 | DISTRICT 22 - ANGELES | NC | T - OTHER TRANSIENT AREA
CA1900942 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900952 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900961 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900974 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1900975 | LPA49 - LA COUNTY | C | R - MOBILE HOME PARK
CA1900976 | LPA49 - LA COUNTY | C | R - OTHER RESIDENTIAL AREA
CA1901000 | LPA49 - LA COUNTY | NTNC | R - RESIDENTIAL AREA
CA1901002 | LPA49 - LA COUNTY | NC | NT - INSTITUTION
CA1907004 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1907011 | LPA49 - LA COUNTY | NTNC | T - HOTEL/MOTEL
CA1907013 | LPA49 - LA COUNTY | NC | T - RESTAURANT
CA1907014 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1907015 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1907016 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1907018 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1907019 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1907024 | LPA49 - LA COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA1907028 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1907029 | LPA49 - LA COUNTY | NC | T - RECREATION AREA
CA1907031 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1907032 | LPA49 - LA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA1909006 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1909627 | LPA49 - LA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA1909644 | DISTRICT 15 - METROPOLITAN | NC | T - RESTAURANT
CA1909645 | LPA49 - LA COUNTY | NC | T - RECREATION AREA
CA1909646 | LPA49 - LA COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA1909647 | LPA49 - LA COUNTY | NC | T - OTHER TRANSIENT AREA
CA1910001 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910002 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910003 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910004 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910005 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910006 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910007 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910009 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910010 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910011 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910012 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910013 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910017 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910018 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910019 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910020 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910021 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910022 | DISTRICT 22 - ANGELES | C | NT - SCHOOL
CA1910023 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910024 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910025 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910026 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910027 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910028 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910029 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910030 | DISTRICT 15 - METROPOLITAN | C | R - OTHER RESIDENTIAL AREA
CA1910032 | DISTRICT 07 - HOLLYWOOD | C | O - WHOLESALER (SELLS WATER)
CA1910033 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910034 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910035 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910036 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910038 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910039 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910040 | DISTRICT 15 - METROPOLITAN | C | O - OTHER AREA
CA1910041 | DISTRICT 07 - HOLLYWOOD | C | O - WHOLESALER (SELLS WATER)
CA1910042 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910043 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910044 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910045 | DISTRICT 16 - CENTRAL | C | O - WHOLESALER (SELLS WATER)
CA1910046 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910047 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910048 | DISTRICT 22 - ANGELES | C | O - WHOLESALER (SELLS WATER)
CA1910049 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910050 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910051 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910052 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910053 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910054 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910056 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910059 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910060 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910061 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910062 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910063 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910064 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910065 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910066 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910067 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910070 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910072 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910073 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910075 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910077 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910079 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910081 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910083 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910084 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910085 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910086 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910087 | DISTRICT 16 - CENTRAL | C | O - WHOLESALER (SELLS WATER)
CA1910090 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910091 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910092 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910096 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910097 | DISTRICT 22 - ANGELES | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1910098 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910099 | DISTRICT 15 - METROPOLITAN | C | R - MOBILE HOME PARK
CA1910101 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910102 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910103 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910104 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910105 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910108 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910117 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910124 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910125 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910126 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910127 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910128 | DISTRICT 15 - METROPOLITAN | C | O - WHOLESALER (SELLS WATER)
CA1910130 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910134 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910137 | DISTRICT 07 - HOLLYWOOD | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1910138 | DISTRICT 07 - HOLLYWOOD | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1910139 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910140 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910142 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910143 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910144 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910146 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910147 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910148 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910149 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910152 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910153 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910154 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910155 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910156 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910157 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910158 | LPA49 - LA COUNTY | C | R - RESIDENTIAL AREA
CA1910159 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910160 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910161 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910163 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910165 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910166 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910167 | DISTRICT 15 - METROPOLITAN | C | NT - INDUSTRIAL/AGRICULTURAL
CA1910169 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910173 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910174 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910179 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910185 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910186 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910189 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910191 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910194 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910195 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910199 | DISTRICT 15 - METROPOLITAN | C | O - WHOLESALER (SELLS WATER)
CA1910200 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910203 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910204 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910205 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910211 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910212 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910213 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910218 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910223 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910225 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910234 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910238 | DISTRICT 22 - ANGELES | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1910239 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910240 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910241 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910242 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910243 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910244 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910245 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910246 | DISTRICT 07 - HOLLYWOOD | C | R - RESIDENTIAL AREA
CA1910247 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910248 | DISTRICT 16 - CENTRAL | C | R - RESIDENTIAL AREA
CA1910249 | DISTRICT 22 - ANGELES | C | R - RESIDENTIAL AREA
CA1910250 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910253 | DISTRICT 15 - METROPOLITAN | C | O - WHOLESALER (SELLS WATER)
CA1910254 | DISTRICT 22 - ANGELES | NTNC | T - RECREATION AREA
CA1910255 | DISTRICT 15 - METROPOLITAN | C | R - RESIDENTIAL AREA
CA1910301 | DISTRICT 16 - CENTRAL | NC | T - RECREATION AREA
CA1910303 | DISTRICT 16 - CENTRAL | NC | T - RECREATION AREA
CA1910305 | DISTRICT 22 - ANGELES | NC | T - RECREATION AREA
CA1910443 | DISTRICT 15 - METROPOLITAN | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA1910604 | DISTRICT 22 - ANGELES | NC | T - HIGHWAY REST AREA
CA1910801 | DISTRICT 15 - METROPOLITAN | C | NT - INSTITUTION
CA2000048 | LPA50 - MADERA COUNTY | NC | T - SUMMER CAMP
CA2000150 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000195 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2000202 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000206 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000207 | LPA50 - MADERA COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA2000220 | LPA50 - MADERA COUNTY | NC | R - RESIDENTIAL AREA
CA2000245 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000251 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000259 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000260 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000275 | LPA50 - MADERA COUNTY | NTNC | NT - MEDICAL FACILITY
CA2000286 | LPA50 - MADERA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2000293 | LPA50 - MADERA COUNTY | C | T - RECREATION AREA
CA2000294 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000315 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000320 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000352 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000370 | LPA50 - MADERA COUNTY | NTNC | T - SERVICE STATION
CA2000379 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2000380 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2000384 | LPA50 - MADERA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2000385 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000501 | LPA50 - MADERA COUNTY | C | R - OTHER RESIDENTIAL AREA
CA2000502 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000503 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000504 | LPA50 - MADERA COUNTY | NTNC | R - OTHER RESIDENTIAL AREA
CA2000505 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000506 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000507 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000508 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000509 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000511 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000512 | LPA50 - MADERA COUNTY | C | NT - INDUSTRIAL/AGRICULTURAL
CA2000517 | LPA50 - MADERA COUNTY | NC | T - SECONDARY RESIDENCES
CA2000521 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2000524 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000526 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000527 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000529 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000530 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000531 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000533 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000534 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000535 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000536 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000537 | LPA50 - MADERA COUNTY | NC | T - SERVICE STATION
CA2000538 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000542 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2000544 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2000545 | LPA50 - MADERA COUNTY | NC | T - HOTEL/MOTEL
CA2000547 | LPA50 - MADERA COUNTY | NC | T - HOTEL/MOTEL
CA2000548 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000549 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000550 | LPA50 - MADERA COUNTY | NC | R - RESIDENTIAL AREA
CA2000551 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000552 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000553 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000554 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000556 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000557 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000558 | LPA50 - MADERA COUNTY | NTNC | T - RESTAURANT
CA2000560 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000561 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000562 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000563 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000564 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000565 | LPA50 - MADERA COUNTY | SSWS | R - RESIDENTIAL AREA
CA2000567 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000568 | LPA50 - MADERA COUNTY | NC | NT - MEDICAL FACILITY
CA2000571 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000573 | LPA50 - MADERA COUNTY | C | R - OTHER RESIDENTIAL AREA
CA2000577 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000581 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000587 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000589 | LPA50 - MADERA COUNTY | C | R - MOBILE HOME PARK
CA2000592 | LPA50 - MADERA COUNTY | C | R - MOBILE HOME PARK
CA2000593 | LPA50 - MADERA COUNTY | C | R - MOBILE HOME PARK
CA2000594 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000595 | LPA50 - MADERA COUNTY | C | R - MOBILE HOME PARK
CA2000597 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000598 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000600 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000601 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000602 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000605 | LPA50 - MADERA COUNTY | C | R - MOBILE HOME PARK
CA2000607 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000608 | LPA50 - MADERA COUNTY | C | R - MOBILE HOME PARK
CA2000609 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000611 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000612 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000616 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000618 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000619 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000627 | LPA50 - MADERA COUNTY | NC | T - HOTEL/MOTEL
CA2000629 | LPA50 - MADERA COUNTY | NC | T - HOTEL/MOTEL
CA2000636 | LPA50 - MADERA COUNTY | NC | T - HOTEL/MOTEL
CA2000637 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000641 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000647 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000653 | LPA50 - MADERA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2000655 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000659 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000660 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000665 | LPA50 - MADERA COUNTY | SSWS | NT - INDUSTRIAL/AGRICULTURAL
CA2000670 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000672 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000681 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000682 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000684 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000688 | LPA50 - MADERA COUNTY | C | R - OTHER RESIDENTIAL AREA
CA2000690 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000692 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000695 | LPA50 - MADERA COUNTY | NTNC | NT - INSTITUTION
CA2000714 | LPA50 - MADERA COUNTY | SSWS | R - RESIDENTIAL AREA
CA2000716 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000724 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000727 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000728 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000729 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2000733 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000735 | LPA50 - MADERA COUNTY | SSWS | R - RESIDENTIAL AREA
CA2000737 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000745 | LPA50 - MADERA COUNTY | NC | R - RESIDENTIAL AREA
CA2000749 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2000757 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000760 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000770 | LPA50 - MADERA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2000775 | LPA50 - MADERA COUNTY | C | R - MOBILE HOME PARK
CA2000780 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000785 | LPA50 - MADERA COUNTY | C | T - SECONDARY RESIDENCES
CA2000790 | LPA50 - MADERA COUNTY | NC | T - SERVICE STATION
CA2000794 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000800 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000806 | LPA50 - MADERA COUNTY | NC | R - RESIDENTIAL AREA
CA2000807 | LPA50 - MADERA COUNTY | NC | NT - INSTITUTION
CA2000808 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000810 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000811 | LPA50 - MADERA COUNTY | NC | T - SERVICE STATION
CA2000815 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000817 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000821 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000823 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000824 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000825 | LPA50 - MADERA COUNTY | NC | T - RECREATION AREA
CA2000827 | LPA50 - MADERA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2000828 | LPA50 - MADERA COUNTY | C | R - MOBILE HOME PARK
CA2000829 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000830 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000832 | DISTRICT 11 - MERCED | C | T - RECREATION AREA
CA2000834 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000840 | LPA50 - MADERA COUNTY | NTNC | NT - DAY CARE CENTER
CA2000843 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000844 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000846 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000848 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000849 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000850 | LPA50 - MADERA COUNTY | NC | T - SERVICE STATION
CA2000851 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000855 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000864 | LPA50 - MADERA COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA2000865 | LPA50 - MADERA COUNTY | C | R - RESIDENTIAL AREA
CA2000866 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000880 | LPA50 - MADERA COUNTY | NC | T - SUMMER CAMP
CA2000885 | LPA50 - MADERA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2000890 | LPA50 - MADERA COUNTY | NC | T - HOTEL/MOTEL
CA2000920 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000930 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000931 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000932 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000938 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000940 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000941 | LPA50 - MADERA COUNTY | SSWS | R - MOBILE HOME PARK
CA2000942 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000943 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000944 | LPA50 - MADERA COUNTY | NC | T - RESTAURANT
CA2000945 | LPA50 - MADERA COUNTY | SSWS | R - RESIDENTIAL AREA
CA2000946 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000947 | LPA50 - MADERA COUNTY | NTNC | NT - SCHOOL
CA2000950 | LPA50 - MADERA COUNTY | NC | O - OTHER AREA
CA2000951 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000952 | LPA50 - MADERA COUNTY | NC | O - OTHER AREA
CA2000953 | LPA50 - MADERA COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA2000955 | LPA50 - MADERA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2000956 | LPA50 - MADERA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2000957 | LPA50 - MADERA COUNTY | NC | NT - SCHOOL
CA2000961 | LPA50 - MADERA COUNTY | NTNC | NT - OTHER NON-TRANSIENT AREA
CA2000962 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000963 | LPA50 - MADERA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2000965 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000966 | LPA50 - MADERA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2000968 | LPA50 - MADERA COUNTY | NC | T - SERVICE STATION
CA2000969 | LPA50 - MADERA COUNTY | NC | NT - INSTITUTION
CA2010001 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2010002 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2010003 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2010003 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2010004 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2010005 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2010006 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2010007 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2010008 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2010009 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2010010 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2010011 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2010012 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2010013 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2010014 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2010015 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2010016 | DISTRICT 11 - MERCED | C | R - SUBDIVISION
CA2010017 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2010300 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2010500 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2010501 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA2010800 | DISTRICT 11 - MERCED | C | NT - INSTITUTION
CA2010801 | DISTRICT 11 - MERCED | C | NT - INSTITUTION
CA2100508 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA
CA2100519 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA
CA2100527 | DISTRICT 25 - MARIN | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2100531 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA2100538 | DISTRICT 25 - MARIN | NTNC | NT - SCHOOL
CA2100545 | DISTRICT 25 - MARIN | NTNC | NT - SCHOOL
CA2100549 | DISTRICT 25 - MARIN | C | R - OTHER RESIDENTIAL AREA
CA2100551 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA2100552 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA2100553 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA2100557 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA2100560 | DISTRICT 25 - MARIN | NTNC | NT - SCHOOL
CA2100564 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA2100565 | DISTRICT 25 - MARIN | C | R - OTHER RESIDENTIAL AREA
CA2100566 | DISTRICT 25 - MARIN | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2100568 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA2100576 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA2100577 | DISTRICT 25 - MARIN | NC | T - SERVICE STATION
CA2100578 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA2100579 | DISTRICT 25 - MARIN | C | R - OTHER RESIDENTIAL AREA
CA2100580 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA2100581 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA2100582 | DISTRICT 25 - MARIN | NTNC | NT - SCHOOL
CA2100584 | DISTRICT 25 - MARIN | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2100585 | DISTRICT 25 - MARIN | NC | R - RESIDENTIAL AREA
CA2100586 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA2100587 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA2110001 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA
CA2110002 | DISTRICT 25 - MARIN | C | O - WHOLESALER (SELLS WATER)
CA2110003 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA
CA2110004 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA
CA2110005 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA
CA2110005 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA
CA2110006 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA
CA2110007 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA
CA2110007 | DISTRICT 25 - MARIN | C | R - RESIDENTIAL AREA
CA2110008 | DISTRICT 25 - MARIN | C | R - OTHER RESIDENTIAL AREA
CA2110009 | DISTRICT 25 - MARIN | NC | T - SECONDARY RESIDENCES
CA2110010 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA2110300 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA2110301 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA2110302 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA2110303 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA2110304 | DISTRICT 25 - MARIN | NC | T - HOTEL/MOTEL
CA2110305 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA2110350 | DISTRICT 25 - MARIN | C | T - RECREATION AREA
CA2110500 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA2110501 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA2110502 | DISTRICT 25 - MARIN | C | T - RECREATION AREA
CA2110503 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA2110505 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA2201070 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2202036 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2202131 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2203021 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2203023 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2203024 | DISTRICT 11 - MERCED | NC | T - HOTEL/MOTEL
CA2203051 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2203059 | DISTRICT 11 - MERCED | NC | NT - SCHOOL
CA2203069 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2204054 | DISTRICT 11 - MERCED | NTNC | T - RECREATION AREA
CA2204101 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2207070 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2207094 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2208033 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2208034 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2208056 | DISTRICT 11 - MERCED | NC | T - HOTEL/MOTEL
CA2208067 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2208107 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2209035 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2209063 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2209065 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2210001 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2210002 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2210003 | DISTRICT 11 - MERCED | NTNC | T - HOTEL/MOTEL
CA2210503 | DISTRICT 11 - MERCED | C | T - RECREATION AREA
CA2210508 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2210510 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2210511 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2210512 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2210513 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2210515 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2210516 | DISTRICT 11 - MERCED | NC | R - RESIDENTIAL AREA
CA2210851 | DISTRICT 11 - MERCED | C | NT - INSTITUTION
CA2210900 | DISTRICT 11 - MERCED | C | T - HOTEL/MOTEL
CA2210901 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2210903 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2210905 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA2210906 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2210907 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2210908 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2210909 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2210910 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2210911 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2210912 | DISTRICT 11 - MERCED | NC | R - RESIDENTIAL AREA
CA2210913 | DISTRICT 11 - MERCED | NC | R - RESIDENTIAL AREA
CA2210915 | DISTRICT 11 - MERCED | NC | R - RESIDENTIAL AREA
CA2210917 | DISTRICT 11 - MERCED | NC | R - MOBILE HOME PARK
CA2210918 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2210920 | DISTRICT 11 - MERCED | NC | R - MOBILE HOME PARK
CA2210921 | DISTRICT 11 - MERCED | C | R - OTHER RESIDENTIAL AREA
CA2210922 | DISTRICT 11 - MERCED | NC | R - RESIDENTIAL AREA
CA2210923 | DISTRICT 11 - MERCED | NC | R - RESIDENTIAL AREA
CA2210924 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2210925 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA2210926 | DISTRICT 11 - MERCED | NTNC | T - HOTEL/MOTEL
CA2210927 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2210928 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2210930 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2210931 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2210932 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2210933 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2210934 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2210937 | DISTRICT 11 - MERCED | NTNC | NT - INSTITUTION
CA2210939 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2210942 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2210943 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2300502 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300506 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300507 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300509 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2300511 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA2300512 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA2300514 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300515 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA2300516 | DISTRICT 03 - MENDOCINO | NC | T - SERVICE STATION
CA2300517 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2300518 | DISTRICT 03 - MENDOCINO | NTNC | NT - OTHER NON-TRANSIENT AREA
CA2300519 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA2300524 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA2300541 | DISTRICT 03 - MENDOCINO | NTNC | T - HOTEL/MOTEL
CA2300545 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300584 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL
CA2300590 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300591 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300596 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300596 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300604 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300605 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300606 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300609 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300610 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300617 | DISTRICT 03 - MENDOCINO | NTNC | T - HOTEL/MOTEL
CA2300619 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2300620 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA2300621 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA2300625 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA2300626 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA2300628 | DISTRICT 03 - MENDOCINO | NTNC | T - HOTEL/MOTEL
CA2300629 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2300633 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA2300634 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK
CA2300635 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2300636 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2300638 | DISTRICT 03 - MENDOCINO | C | T - RECREATION AREA
CA2300642 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2300644 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK
CA2300645 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA2300646 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK
CA2300653 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2300663 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300667 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300668 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK
CA2300668 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK
CA2300705 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK
CA2300708 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300717 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK,PRINC. RES.
CA2300730 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300731 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300735 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300736 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2300740 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA2300743 | DISTRICT 03 - MENDOCINO | C | R - OTHER RESIDENTIAL AREA
CA2300746 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA2300755 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL
CA2300757 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA2300760 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2300764 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL
CA2300770 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL
CA2300775 | DISTRICT 03 - MENDOCINO | NC | R - MOBILE HOME PARK
CA2300785 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL
CA2300788 | DISTRICT 03 - MENDOCINO | NC | R - RESIDENTIAL AREA
CA2300789 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2300802 | DISTRICT 03 - MENDOCINO | NTNC | T - SECONDARY RESIDENCES
CA2300804 | DISTRICT 03 - MENDOCINO | NTNC | T - OTHER TRANSIENT AREA
CA2300811 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA2300818 | DISTRICT 03 - MENDOCINO | NC | T - HIGHWAY REST AREA
CA2300819 | DISTRICT 03 - MENDOCINO | NC | T - HIGHWAY REST AREA
CA2300820 | DISTRICT 03 - MENDOCINO | NC | T - HIGHWAY REST AREA
CA2300821 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA2300826 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL
CA2300829 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL
CA2300830 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL
CA2300831 | DISTRICT 03 - MENDOCINO | NC | R - MOBILE HOME PARK
CA2300832 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300837 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2300838 | DISTRICT 03 - MENDOCINO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2300839 | DISTRICT 03 - MENDOCINO | NC | T - SUMMER CAMP
CA2300842 | DISTRICT 03 - MENDOCINO | NC | T - SUMMER CAMP
CA2300845 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA2300846 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL
CA2300847 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL
CA2300852 | DISTRICT 03 - MENDOCINO | NTNC | T - RESTAURANT
CA2300853 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2300854 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2300855 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2300856 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2300858 | DISTRICT 03 - MENDOCINO | NC | T - SUMMER CAMP
CA2300863 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL
CA2300871 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA2300872 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA2300873 | DISTRICT 03 - MENDOCINO | NC | T - SUMMER CAMP
CA2300874 | DISTRICT 03 - MENDOCINO | NTNC | NT - SCHOOL
CA2300877 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA2300878 | DISTRICT 03 - MENDOCINO | NC | T - SERVICE STATION
CA2300879 | DISTRICT 03 - MENDOCINO | NTNC | NT - OTHER NON-TRANSIENT AREA
CA2300892 | DISTRICT 03 - MENDOCINO | C | R - MOBILE HOME PARK
CA2300900 | DISTRICT 03 - MENDOCINO | NC | R - MOBILE HOME PARK
CA2300901 | DISTRICT 03 - MENDOCINO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2300902 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA2300903 | DISTRICT 03 - MENDOCINO | NC | T - RESTAURANT
CA2300905 | DISTRICT 03 - MENDOCINO | NC | NT - OTHER NON-TRANSIENT AREA
CA2300906 | DISTRICT 03 - MENDOCINO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2300907 | DISTRICT 03 - MENDOCINO | NTNC | NT - OTHER NON-TRANSIENT AREA
CA2300908 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA2300950 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2300951 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA2300952 | DISTRICT 03 - MENDOCINO | NC | T - SERVICE STATION
CA2300953 | DISTRICT 03 - MENDOCINO | NC | T - HOTEL/MOTEL
CA2300954 | DISTRICT 03 - MENDOCINO | NC | T - RESTAURANT
CA2300958 | DISTRICT 03 - MENDOCINO | NC | T - OTHER TRANSIENT AREA
CA2300970 | DISTRICT 03 - MENDOCINO | NC | NT - OTHER NON-TRANSIENT AREA
CA2310001 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2310002 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2310003 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2310004 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2310005 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2310005 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2310006 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2310007 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2310008 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2310008 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2310009 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2310010 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2310011 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2310012 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2310013 | DISTRICT 03 - MENDOCINO | C | O - OTHER AREA
CA2310300 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2310301 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2310302 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2310303 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2310304 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2310308 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2310310 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2310312 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2310313 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2310316 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2310317 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2310800 | DISTRICT 03 - MENDOCINO | NTNC | T - SECONDARY RESIDENCES
CA2310801 | DISTRICT 03 - MENDOCINO | NTNC | T - SECONDARY RESIDENCES
CA2400011 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400013 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400014 | DISTRICT 11 - MERCED | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2400028 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2400034 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2400046 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2400051 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400053 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA2400055 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400058 | DISTRICT 11 - MERCED | NC | T - RESTAURANT
CA2400062 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2400064 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2400065 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2400066 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2400071 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2400075 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2400078 | DISTRICT 11 - MERCED | NTNC | T - RECREATION AREA
CA2400079 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2400084 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA2400085 | DISTRICT 11 - MERCED | NC | T - SERVICE STATION
CA2400088 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2400089 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2400091 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2400097 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2400099 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2400113 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2400114 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2400117 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2400119 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2400122 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2400128 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2400134 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2400139 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400140 | DISTRICT 11 - MERCED | NC | T - RESTAURANT
CA2400148 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2400153 | DISTRICT 11 - MERCED | NC | NT - INSTITUTION
CA2400154 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400162 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400165 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400166 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400167 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2400169 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400170 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400172 | DISTRICT 11 - MERCED | C | NT - INSTITUTION
CA2400175 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400196 | DISTRICT 11 - MERCED | NTNC | R - OTHER RESIDENTIAL AREA
CA2400200 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400201 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2400206 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400208 | DISTRICT 11 - MERCED | NC | T - SERVICE STATION
CA2400209 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2400211 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2400216 | DISTRICT 11 - MERCED | NTNC | O - OTHER AREA
CA2400218 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400219 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA2400220 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2400223 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400226 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400227 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2400229 | DISTRICT 11 - MERCED | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2400230 | DISTRICT 11 - MERCED | NC | NT - MEDICAL FACILITY
CA2400231 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400232 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400234 | DISTRICT 11 - MERCED | NC | O - OTHER AREA
CA2400240 | DISTRICT 11 - MERCED | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2400245 | DISTRICT 11 - MERCED | NC | NT - INSTITUTION
CA2400248 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400249 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2400250 | DISTRICT 11 - MERCED | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2400254 | DISTRICT 11 - MERCED | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2400255 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400304 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2400307 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2400315 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2400318 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2400320 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2400322 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2400323 | DISTRICT 11 - MERCED | NC | T - RESTAURANT
CA2400326 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2400327 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2400328 | DISTRICT 11 - MERCED | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2400329 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400330 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400331 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400332 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400333 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400334 | DISTRICT 11 - MERCED | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2400335 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400336 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400337 | DISTRICT 11 - MERCED | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2400338 | DISTRICT 11 - MERCED | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2400339 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400340 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA2400341 | DISTRICT 11 - MERCED | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2400342 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400343 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400345 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400347 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2400348 | DISTRICT 11 - MERCED | NTNC | NT - OTHER NON-TRANSIENT AREA
CA2410001 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2410002 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2410003 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2410004 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2410005 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2410006 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2410007 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2410008 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2410009 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2410010 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2410011 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2410012 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2410018 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA2410021 | DISTRICT 11 - MERCED | NTNC | O - OTHER AREA
CA2410301 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2410302 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2410303 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2410304 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2410305 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA2410700 | DISTRICT 11 - MERCED | C | NT - INDUSTRIAL/AGRICULTURAL
CA2410950 | DISTRICT 11 - MERCED | NTNC | O - OTHER AREA
CA2500503 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA2500538 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA2500547 | DISTRICT 01 - KLAMATH | NTNC | T - SECONDARY RESIDENCES
CA2500801 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA2500811 | DISTRICT 01 - KLAMATH | NC | T - SECONDARY RESIDENCES
CA2500911 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA2510001 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA2510002 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA2510800 | DISTRICT 01 - KLAMATH | NTNC | NT - INSTITUTION
CA2600501 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA
CA2600502 | LPA56 - MONO COUNTY | NC | T - RESTAURANT
CA2600503 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600505 | LPA56 - MONO COUNTY | NC | R - RESIDENTIAL AREA
CA2600509 | LPA56 - MONO COUNTY | NC | R - RESIDENTIAL AREA
CA2600510 | LPA56 - MONO COUNTY | NC | R - RESIDENTIAL AREA
CA2600511 | LPA56 - MONO COUNTY | NC | T - HOTEL/MOTEL
CA2600513 | LPA56 - MONO COUNTY | NC | R - MOBILE HOME PARK
CA2600515 | LPA56 - MONO COUNTY | SSWS | T - HOTEL/MOTEL
CA2600518 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600519 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600520 | LPA56 - MONO COUNTY | SSWS | T - HOTEL/MOTEL
CA2600524 | LPA56 - MONO COUNTY | NC | NT - INSTITUTION
CA2600526 | LPA56 - MONO COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA2600529 | DISTRICT 13 - SAN BERNARDINO | NC | T - RESTAURANT
CA2600530 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA2600532 | LPA56 - MONO COUNTY | C | NT - INDUSTRIAL/AGRICULTURAL
CA2600533 | LPA56 - MONO COUNTY | NC | T - RESTAURANT
CA2600534 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600535 | LPA56 - MONO COUNTY | NC | T - RESTAURANT
CA2600536 | LPA56 - MONO COUNTY | NC | R - MOBILE HOME PARK
CA2600538 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA
CA2600540 | LPA56 - MONO COUNTY | NC | T - SUMMER CAMP
CA2600542 | LPA56 - MONO COUNTY | SSWS | R - MOBILE HOME PARK
CA2600543 | LPA56 - MONO COUNTY | NC | R - MOBILE HOME PARK
CA2600545 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600546 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA
CA2600547 | LPA56 - MONO COUNTY | C | R - MOBILE HOME PARK
CA2600550 | LPA56 - MONO COUNTY | NC | R - MOBILE HOME PARK
CA2600551 | LPA56 - MONO COUNTY | SSWS | R - MOBILE HOME PARK
CA2600552 | LPA56 - MONO COUNTY | NC | T - RESTAURANT
CA2600553 | LPA56 - MONO COUNTY | NC | T - HOTEL/MOTEL
CA2600555 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600556 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600558 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600560 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600561 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600563 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600564 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600567 | LPA56 - MONO COUNTY | NC | T - SUMMER CAMP
CA2600568 | LPA56 - MONO COUNTY | NTNC | NT - SCHOOL
CA2600570 | LPA56 - MONO COUNTY | NTNC | NT - SCHOOL
CA2600571 | LPA56 - MONO COUNTY | NC | T - RESTAURANT
CA2600572 | LPA56 - MONO COUNTY | NC | R - MOBILE HOME PARK
CA2600573 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600574 | LPA56 - MONO COUNTY | NC | R - MOBILE HOME PARK
CA2600576 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600577 | LPA56 - MONO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2600578 | LPA56 - MONO COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA2600581 | LPA56 - MONO COUNTY | NC | T - SUMMER CAMP
CA2600589 | DISTRICT 13 - SAN BERNARDINO | NC | T - HIGHWAY REST AREA
CA2600592 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600596 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600597 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600598 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600599 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600600 | LPA56 - MONO COUNTY | NC | T - OTHER TRANSIENT AREA
CA2600601 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600605 | LPA56 - MONO COUNTY | NC | T - RESTAURANT
CA2600607 | LPA56 - MONO COUNTY | NC | T - RESTAURANT
CA2600608 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600609 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600610 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600614 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600615 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600617 | LPA56 - MONO COUNTY | NC | T - RESTAURANT
CA2600620 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA
CA2600621 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA
CA2600622 | LPA56 - MONO COUNTY | C | R - MOBILE HOME PARK
CA2600624 | LPA56 - MONO COUNTY | NTNC | T - RECREATION AREA
CA2600626 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600627 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600629 | LPA56 - MONO COUNTY | SSWS | R - RESIDENTIAL AREA
CA2600631 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600641 | LPA56 - MONO COUNTY | NC | T - RESTAURANT
CA2600648 | LPA56 - MONO COUNTY | NC | T - RESTAURANT
CA2600649 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600652 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600656 | LPA56 - MONO COUNTY | NC | T - OTHER TRANSIENT AREA
CA2600658 | LPA56 - MONO COUNTY | NC | T - RESTAURANT
CA2600661 | LPA56 - MONO COUNTY | NC | T - SUMMER CAMP
CA2600699 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA
CA2600700 | DISTRICT 13 - SAN BERNARDINO | NC | NT - OTHER NON-TRANSIENT AREA
CA2600708 | LPA56 - MONO COUNTY | NC | T - OTHER TRANSIENT AREA
CA2600714 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA
CA2600718 | LPA56 - MONO COUNTY | NC | T - OTHER TRANSIENT AREA
CA2600725 | LPA56 - MONO COUNTY | NC | T - SERVICE STATION
CA2600727 | DISTRICT 13 - SAN BERNARDINO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2600729 | LPA56 - MONO COUNTY | NC | T - RECREATION AREA
CA2600733 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA
CA2600755 | LPA56 - MONO COUNTY | NC | T - RESTAURANT
CA2610001 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA2610002 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA2610003 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA2610004 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA2610005 | LPA56 - MONO COUNTY | C | R - RESIDENTIAL AREA
CA2610300 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA2610700 | DISTRICT 13 - SAN BERNARDINO | C | R - OTHER RESIDENTIAL AREA
CA2610701 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA2700014 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700032 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700042 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700101 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700147 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700156 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700236 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700360 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700503 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700508 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2700509 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700511 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2700518 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700521 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700522 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK
CA2700523 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700534 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700535 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700536 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700541 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700544 | LPA57 - MONTEREY COUNTY | SSWS | O - OTHER AREA
CA2700547 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700548 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700552 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL
CA2700558 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700575 | LPA57 - MONTEREY COUNTY | NC | T - OTHER TRANSIENT AREA
CA2700577 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL
CA2700579 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700586 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700589 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700592 | LPA57 - MONTEREY COUNTY | NTNC | NT - INSTITUTION
CA2700594 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700606 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK
CA2700612 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700622 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700624 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700629 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700634 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700636 | LPA57 - MONTEREY COUNTY | NC | T - RECREATION AREA
CA2700638 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700656 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700662 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700663 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700665 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700669 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700674 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700678 | LPA57 - MONTEREY COUNTY | C | O - OTHER AREA
CA2700682 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700686 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700687 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700691 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700702 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700703 | LPA57 - MONTEREY COUNTY | NTNC | NT - INSTITUTION
CA2700705 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL
CA2700709 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700713 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700727 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL
CA2700728 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA
CA2700731 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700733 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700738 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700739 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2700740 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700760 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2700766 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700771 | LPA57 - MONTEREY COUNTY | C | T - SECONDARY RESIDENCES
CA2700772 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK
CA2700773 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2700774 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2700775 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700787 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700792 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK
CA2700799 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700802 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2700837 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700838 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700842 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2700843 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2700850 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700851 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700853 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700856 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700875 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700889 | LPA57 - MONTEREY COUNTY | NC | R - RESIDENTIAL AREA
CA2700960 | LPA57 - MONTEREY COUNTY | SSWS | O - OTHER AREA
CA2700964 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL
CA2700970 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK
CA2700983 | DISTRICT 05 - MONTEREY | NC | T - HIGHWAY REST AREA
CA2700984 | DISTRICT 05 - MONTEREY | NC | T - HIGHWAY REST AREA
CA2700992 | LPA57 - MONTEREY COUNTY | C | T - RECREATION AREA
CA2700998 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2700999 | LPA57 - MONTEREY COUNTY | NC | T - RECREATION AREA
CA2701000 | LPA57 - MONTEREY COUNTY | NC | T - RESTAURANT
CA2701001 | LPA57 - MONTEREY COUNTY | NC | T - RECREATION AREA
CA2701009 | LPA57 - MONTEREY COUNTY | NC | T - HOTEL/MOTEL
CA2701034 | LPA57 - MONTEREY COUNTY | C | T - SECONDARY RESIDENCES
CA2701036 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701040 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA
CA2701046 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA
CA2701063 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA
CA2701068 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701109 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701142 | LPA57 - MONTEREY COUNTY | NC | R - RESIDENTIAL AREA
CA2701144 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701151 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701152 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701153 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701166 | LPA57 - MONTEREY COUNTY | NC | T - RECREATION AREA
CA2701171 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701172 | LPA57 - MONTEREY COUNTY | NTNC | T - SECONDARY RESIDENCES
CA2701176 | LPA57 - MONTEREY COUNTY | NC | NT - INSTITUTION
CA2701183 | LPA57 - MONTEREY COUNTY | NC | T - RECREATION AREA
CA2701184 | LPA57 - MONTEREY COUNTY | NC | T - RECREATION AREA
CA2701187 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701202 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2701214 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701221 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL
CA2701229 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2701231 | LPA57 - MONTEREY COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2701232 | LPA57 - MONTEREY COUNTY | NC | NT - INSTITUTION
CA2701235 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2701241 | LPA57 - MONTEREY COUNTY | C | T - SECONDARY RESIDENCES
CA2701254 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701257 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701263 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701273 | LPA57 - MONTEREY COUNTY | NC | T - OTHER TRANSIENT AREA
CA2701278 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701279 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701280 | LPA57 - MONTEREY COUNTY | C | T - RESTAURANT
CA2701284 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2701295 | LPA57 - MONTEREY COUNTY | C | NT - INSTITUTION
CA2701297 | LPA57 - MONTEREY COUNTY | NC | T - OTHER TRANSIENT AREA
CA2701298 | LPA57 - MONTEREY COUNTY | NC | T - RECREATION AREA
CA2701310 | LPA57 - MONTEREY COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA2701325 | LPA57 - MONTEREY COUNTY | NC | T - SECONDARY RESIDENCES
CA2701334 | LPA57 - MONTEREY COUNTY | NC | T - OTHER TRANSIENT AREA
CA2701355 | LPA57 - MONTEREY COUNTY | C | T - RECREATION AREA
CA2701364 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701367 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701403 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701423 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701446 | LPA57 - MONTEREY COUNTY | NC | T - HOTEL/MOTEL
CA2701452 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701474 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2701498 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701503 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701515 | LPA57 - MONTEREY COUNTY | C | T - SECONDARY RESIDENCES
CA2701542 | LPA57 - MONTEREY COUNTY | NC | T - SERVICE STATION
CA2701550 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701553 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701570 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701579 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701589 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701630 | LPA57 - MONTEREY COUNTY | NC | T - SERVICE STATION
CA2701633 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701647 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701658 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701659 | LPA57 - MONTEREY COUNTY | NTNC | R - OTHER RESIDENTIAL AREA
CA2701670 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701676 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA
CA2701679 | LPA57 - MONTEREY COUNTY | NTNC | NT - OTHER NON-TRANSIENT AREA
CA2701681 | LPA57 - MONTEREY COUNTY | NC | T - SERVICE STATION
CA2701683 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701687 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK
CA2701701 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK
CA2701705 | LPA57 - MONTEREY COUNTY | C | NT - INSTITUTION
CA2701726 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701731 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701740 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701742 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA
CA2701789 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701793 | LPA57 - MONTEREY COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2701800 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701814 | LPA57 - MONTEREY COUNTY | NC | T - OTHER TRANSIENT AREA
CA2701820 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701822 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701824 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2701825 | LPA57 - MONTEREY COUNTY | NC | T - HOTEL/MOTEL
CA2701837 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701869 | LPA57 - MONTEREY COUNTY | SSWS | NT - INDUSTRIAL/AGRICULTURAL
CA2701876 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701888 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701897 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701898 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701904 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701906 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK
CA2701912 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701918 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701922 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701926 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701929 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701931 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701935 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701940 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701942 | LPA57 - MONTEREY COUNTY | NC | T - RESTAURANT
CA2701945 | LPA57 - MONTEREY COUNTY | NC | T - RECREATION AREA
CA2701946 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2701951 | LPA57 - MONTEREY COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2701952 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2701956 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701959 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2701964 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702003 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702004 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702007 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702009 | LPA57 - MONTEREY COUNTY | NTNC | T - RECREATION AREA
CA2702021 | LPA57 - MONTEREY COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2702026 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702030 | LPA57 - MONTEREY COUNTY | NC | NT - INSTITUTION
CA2702050 | LPA57 - MONTEREY COUNTY | NTNC | NT - INSTITUTION
CA2702055 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702073 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702094 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702110 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702121 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702135 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702140 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702148 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702163 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702165 | LPA57 - MONTEREY COUNTY | NC | R - RESIDENTIAL AREA
CA2702172 | LPA57 - MONTEREY COUNTY | NTNC | T - SECONDARY RESIDENCES
CA2702180 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL
CA2702198 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702202 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702203 | LPA57 - MONTEREY COUNTY | NC | T - RECREATION AREA
CA2702209 | LPA57 - MONTEREY COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA2702226 | DISTRICT 05 - MONTEREY | NC | T - RECREATION AREA
CA2702229 | LPA57 - MONTEREY COUNTY | NC | T - RECREATION AREA
CA2702254 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL
CA2702255 | LPA57 - MONTEREY COUNTY | NC | T - OTHER TRANSIENT AREA
CA2702256 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK
CA2702259 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702266 | LPA57 - MONTEREY COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA2702268 | LPA57 - MONTEREY COUNTY | C | T - OTHER TRANSIENT AREA
CA2702293 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702296 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702299 | LPA57 - MONTEREY COUNTY | C | T - HOTEL/MOTEL
CA2702315 | LPA57 - MONTEREY COUNTY | NTNC | T - RECREATION AREA
CA2702317 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL
CA2702320 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA
CA2702322 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL
CA2702323 | LPA57 - MONTEREY COUNTY | NTNC | T - HOTEL/MOTEL
CA2702325 | LPA57 - MONTEREY COUNTY | C | T - HOTEL/MOTEL
CA2702327 | LPA57 - MONTEREY COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA2702328 | LPA57 - MONTEREY COUNTY | C | T - HOTEL/MOTEL
CA2702336 | LPA57 - MONTEREY COUNTY | NTNC | R - RESIDENTIAL AREA
CA2702368 | LPA57 - MONTEREY COUNTY | NTNC | O - OTHER AREA
CA2702370 | LPA57 - MONTEREY COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2702373 | LPA57 - MONTEREY COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2702374 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA
CA2702386 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2702388 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702396 | LPA57 - MONTEREY COUNTY | NC | R - RESIDENTIAL AREA
CA2702405 | LPA57 - MONTEREY COUNTY | C | R - MOBILE HOME PARK
CA2702409 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA
CA2702412 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702431 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702439 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702444 | LPA57 - MONTEREY COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2702452 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702453 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702456 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702461 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2702466 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702475 | LPA57 - MONTEREY COUNTY | NC | NT - INSTITUTION
CA2702482 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702484 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702486 | LPA57 - MONTEREY COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2702487 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702490 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL
CA2702495 | LPA57 - MONTEREY COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2702496 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702503 | LPA57 - MONTEREY COUNTY | NC | T - RECREATION AREA
CA2702519 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702520 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702521 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2702537 | LPA57 - MONTEREY COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2702539 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702544 | LPA57 - MONTEREY COUNTY | NC | T - SECONDARY RESIDENCES
CA2702549 | LPA57 - MONTEREY COUNTY | LSS | R - RESIDENTIAL AREA
CA2702550 | LPA57 - MONTEREY COUNTY | NTNC | NT - SCHOOL
CA2702551 | LPA57 - MONTEREY COUNTY | NC | T - HOTEL/MOTEL
CA2702554 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702562 | LPA57 - MONTEREY COUNTY | NC | T - RECREATION AREA
CA2702563 | LPA57 - MONTEREY COUNTY | NC | T - RECREATION AREA
CA2702564 | LPA57 - MONTEREY COUNTY | SSWS | T - RECREATION AREA
CA2702571 | LPA57 - MONTEREY COUNTY | NTNC | NT - MEDICAL FACILITY
CA2702572 | LPA57 - MONTEREY COUNTY | NC | NT - SCHOOL
CA2702575 | LPA57 - MONTEREY COUNTY | NC | T - RECREATION AREA
CA2702583 | LPA57 - MONTEREY COUNTY | LSS | R - RESIDENTIAL AREA
CA2702584 | LPA57 - MONTEREY COUNTY | NTNC | O - OTHER AREA
CA2702586 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2702588 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2702595 | LPA57 - MONTEREY COUNTY | NTNC | R - OTHER RESIDENTIAL AREA
CA2702603 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2702607 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702608 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2702609 | LPA57 - MONTEREY COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2702613 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702615 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702616 | LPA57 - MONTEREY COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2702620 | LPA57 - MONTEREY COUNTY | NTNC | R - OTHER RESIDENTIAL AREA
CA2702625 | LPA57 - MONTEREY COUNTY | SSWS | R - RESIDENTIAL AREA
CA2702641 | LPA57 - MONTEREY COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2702642 | LPA57 - MONTEREY COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2702643 | LPA57 - MONTEREY COUNTY | NTNC | R - OTHER RESIDENTIAL AREA
CA2702652 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702679 | LPA57 - MONTEREY COUNTY | NC | O - OTHER AREA
CA2702681 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702704 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702708 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702736 | LPA57 - MONTEREY COUNTY | NC | NT - INSTITUTION
CA2702739 | LPA57 - MONTEREY COUNTY | NC | T - OTHER TRANSIENT AREA
CA2702799 | LPA57 - MONTEREY COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2702800 | LPA57 - MONTEREY COUNTY | NC | T - RESTAURANT
CA2702802 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702805 | LPA57 - MONTEREY COUNTY | NC | T - RECREATION AREA
CA2702812 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702816 | LPA57 - MONTEREY COUNTY | C | R - OTHER RESIDENTIAL AREA
CA2702830 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2702964 | LPA57 - MONTEREY COUNTY | NC | T - OTHER TRANSIENT AREA
CA2703132 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2704520 | LPA57 - MONTEREY COUNTY | C | R - RESIDENTIAL AREA
CA2704623 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2704785 | LPA57 - MONTEREY COUNTY | SSWS | NT - INDUSTRIAL/AGRICULTURAL
CA2706552 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2708852 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2709830 | LPA57 - MONTEREY COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2710001 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710004 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710005 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710006 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710007 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710008 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710009 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710010 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710011 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710012 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710013 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710016 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710017 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710018 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710019 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710020 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710021 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710022 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710023 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA2710300 | DISTRICT 05 - MONTEREY | C | R - OTHER RESIDENTIAL AREA
CA2710301 | DISTRICT 05 - MONTEREY | NC | T - RECREATION AREA
CA2710302 | DISTRICT 05 - MONTEREY | NC | T - RECREATION AREA
CA2710306 | DISTRICT 05 - MONTEREY | NC | T - RECREATION AREA
CA2710702 | DISTRICT 05 - MONTEREY | C | O - OTHER AREA
CA2710705 | DISTRICT 05 - MONTEREY | NTNC | O - OTHER AREA
CA2710850 | DISTRICT 05 - MONTEREY | C | NT - INSTITUTION
CA2710851 | DISTRICT 05 - MONTEREY | C | NT - INSTITUTION
CA2800008 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800010 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800011 | LPA58 - NAPA COUNTY | LSS | T - OTHER TRANSIENT AREA
CA2800012 | LPA58 - NAPA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2800013 | LPA58 - NAPA COUNTY | NC | O - OTHER AREA
CA2800014 | LPA58 - NAPA COUNTY | NC | O - OTHER AREA
CA2800015 | LPA58 - NAPA COUNTY | NTNC | O - OTHER AREA
CA2800017 | LPA58 - NAPA COUNTY | LSS | O - OTHER AREA
CA2800018 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800019 | LPA58 - NAPA COUNTY | LSS | T - OTHER TRANSIENT AREA
CA2800020 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2800021 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800022 | LPA58 - NAPA COUNTY | LSS | T - OTHER TRANSIENT AREA
CA2800023 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2800024 | LPA58 - NAPA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2800025 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800026 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800027 | LPA58 - NAPA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2800028 | LPA58 - NAPA COUNTY | LSS | T - OTHER TRANSIENT AREA
CA2800030 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800032 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800033 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800034 | LPA58 - NAPA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2800035 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA
CA2800036 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800037 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800038 | LPA58 - NAPA COUNTY | LSS | T - OTHER TRANSIENT AREA
CA2800039 | LPA58 - NAPA COUNTY | C | T - OTHER TRANSIENT AREA
CA2800040 | LPA58 - NAPA COUNTY | C | T - OTHER TRANSIENT AREA
CA2800041 | LPA58 - NAPA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2800042 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800043 | LPA58 - NAPA COUNTY | NTNC | O - OTHER AREA
CA2800044 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800046 | LPA58 - NAPA COUNTY | LSS | T - OTHER TRANSIENT AREA
CA2800047 | LPA58 - NAPA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2800048 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800049 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800050 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800051 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800052 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800054 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800055 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2800057 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800058 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800059 | LPA58 - NAPA COUNTY | NTNC | NT - OTHER NON-TRANSIENT AREA
CA2800060 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800061 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800063 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800064 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800066 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800068 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800070 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800071 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800073 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2800075 | LPA58 - NAPA COUNTY | LSS | NT - INDUSTRIAL/AGRICULTURAL
CA2800077 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800078 | LPA58 - NAPA COUNTY | SSWS | T - OTHER TRANSIENT AREA
CA2800079 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800100 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800101 | LPA58 - NAPA COUNTY | NC | O - OTHER AREA
CA2800103 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2800105 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2800106 | LPA58 - NAPA COUNTY | NC | O - OTHER AREA
CA2800107 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800108 | LPA58 - NAPA COUNTY | LSS | T - OTHER TRANSIENT AREA
CA2800109 | LPA58 - NAPA COUNTY | LSS | T - OTHER TRANSIENT AREA
CA2800110 | LPA58 - NAPA COUNTY | NC | O - OTHER AREA
CA2800111 | LPA58 - NAPA COUNTY | NC | R - RESIDENTIAL AREA
CA2800112 | LPA58 - NAPA COUNTY | NTNC | O - OTHER AREA
CA2800113 | LPA58 - NAPA COUNTY | LSS | O - OTHER AREA
CA2800115 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800129 | LPA58 - NAPA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2800186 | LPA58 - NAPA COUNTY | NC | R - MOBILE HOME PARK
CA2800297 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2800299 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2800301 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2800302 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2800516 | LPA58 - NAPA COUNTY | C | NT - INDUSTRIAL/AGRICULTURAL
CA2800521 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA
CA2800525 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA
CA2800526 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2800527 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA
CA2800528 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA
CA2800530 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA
CA2800531 | LPA58 - NAPA COUNTY | C | R - OTHER RESIDENTIAL AREA
CA2800532 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA
CA2800536 | LPA58 - NAPA COUNTY | NTNC | T - HOTEL/MOTEL
CA2800543 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA
CA2800554 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800555 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2800556 | LPA58 - NAPA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2800561 | LPA58 - NAPA COUNTY | NTNC | T - RESTAURANT
CA2800562 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2800564 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800569 | LPA58 - NAPA COUNTY | NTNC | T - HOTEL/MOTEL
CA2800570 | LPA58 - NAPA COUNTY | SSWS | T - OTHER TRANSIENT AREA
CA2800578 | LPA58 - NAPA COUNTY | NC | T - HOTEL/MOTEL
CA2800580 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2800583 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800584 | LPA58 - NAPA COUNTY | NC | T - SUMMER CAMP
CA2800587 | LPA58 - NAPA COUNTY | NC | T - SECONDARY RESIDENCES
CA2800588 | LPA58 - NAPA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2800589 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2800592 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800593 | LPA58 - NAPA COUNTY | C | T - RECREATION AREA
CA2800594 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800602 | LPA58 - NAPA COUNTY | SSWS | R - MOBILE HOME PARK
CA2800609 | LPA58 - NAPA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2800621 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800625 | DISTRICT 03 - MENDOCINO | C | NT - MEDICAL FACILITY
CA2800648 | LPA58 - NAPA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2800680 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800683 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2800724 | LPA58 - NAPA COUNTY | SSWS | R - RESIDENTIAL AREA
CA2800734 | LPA58 - NAPA COUNTY | SSWS | NT - INDUSTRIAL/AGRICULTURAL
CA2800736 | LPA58 - NAPA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2800740 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800741 | LPA58 - NAPA COUNTY | NTNC | O - OTHER AREA
CA2800742 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800811 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2800812 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800840 | LPA58 - NAPA COUNTY | NTNC | NT - SCHOOL
CA2800847 | LPA58 - NAPA COUNTY | NTNC | NT - SCHOOL
CA2800848 | LPA58 - NAPA COUNTY | NTNC | NT - SCHOOL
CA2800900 | LPA58 - NAPA COUNTY | NC | T - RECREATION AREA
CA2800970 | LPA58 - NAPA COUNTY | NTNC | NT - SCHOOL
CA2800971 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2800972 | LPA58 - NAPA COUNTY | NC | NT - OTHER NON-TRANSIENT AREA
CA2800973 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2801002 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801004 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801006 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801007 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2801008 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801009 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2801010 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2801011 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801012 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801014 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2801015 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801016 | LPA58 - NAPA COUNTY | C | NT - INDUSTRIAL/AGRICULTURAL
CA2801020 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA
CA2801022 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2801024 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801026 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801027 | LPA58 - NAPA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2801028 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801029 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801030 | LPA58 - NAPA COUNTY | NC | T - RECREATION AREA
CA2801031 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801032 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2801033 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801035 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801036 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801037 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801038 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801039 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2801041 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801042 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2801043 | LPA58 - NAPA COUNTY | NC | T - RECREATION AREA
CA2801046 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801047 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801049 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801052 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2801055 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801056 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801057 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2801070 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801073 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2801075 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801076 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801077 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2801080 | LPA58 - NAPA COUNTY | C | R - OTHER RESIDENTIAL AREA
CA2801084 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801086 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801088 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2801089 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2801936 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2802715 | LPA58 - NAPA COUNTY | SSWS | R - RESIDENTIAL AREA
CA2803137 | LPA58 - NAPA COUNTY | SSWS | R - RESIDENTIAL AREA
CA2803657 | LPA58 - NAPA COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA2803697 | LPA58 - NAPA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2803879 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2803886 | LPA58 - NAPA COUNTY | NC | T - HOTEL/MOTEL
CA2803907 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2803911 | LPA58 - NAPA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA2803912 | LPA58 - NAPA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2810001 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2810002 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2810003 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2810004 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2810005 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2810007 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2810007 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2810008 | DISTRICT 03 - MENDOCINO | C | O - WHOLESALER (SELLS WATER)
CA2810009 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA
CA2810011 | LPA58 - NAPA COUNTY | NC | T - RECREATION AREA
CA2810012 | DISTRICT 03 - MENDOCINO | C | NT - SCHOOL
CA2810013 | DISTRICT 03 - MENDOCINO | C | R - RESIDENTIAL AREA
CA2810014 | LPA58 - NAPA COUNTY | C | R - RESIDENTIAL AREA
CA2810300 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2810301 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2810302 | DISTRICT 03 - MENDOCINO | NTNC | NT - OTHER NON-TRANSIENT AREA
CA2810650 | DISTRICT 03 - MENDOCINO | NC | T - RECREATION AREA
CA2900089 | LPA59 - NEVADA COUNTY | NC | T - RESTAURANT
CA2900090 | LPA59 - NEVADA COUNTY | NC | T - HOTEL/MOTEL
CA2900108 | LPA59 - NEVADA COUNTY | NC | T - RESTAURANT
CA2900112 | LPA59 - NEVADA COUNTY | NC | O - OTHER AREA
CA2900115 | LPA59 - NEVADA COUNTY | NC | T - RESTAURANT
CA2900274 | LPA59 - NEVADA COUNTY | NC | T - RESTAURANT
CA2900330 | LPA59 - NEVADA COUNTY | NTNC | NT - MEDICAL FACILITY
CA2900501 | LPA59 - NEVADA COUNTY | NC | T - RESTAURANT
CA2900502 | LPA59 - NEVADA COUNTY | C | R - RESIDENTIAL AREA
CA2900504 | LPA59 - NEVADA COUNTY | NC | T - SERVICE STATION
CA2900507 | LPA59 - NEVADA COUNTY | NTNC | T - RECREATION AREA
CA2900508 | LPA59 - NEVADA COUNTY | NTNC | T - SECONDARY RESIDENCES
CA2900511 | LPA59 - NEVADA COUNTY | C | R - RESIDENTIAL AREA
CA2900513 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2900516 | LPA59 - NEVADA COUNTY | NC | T - SUMMER CAMP
CA2900520 | LPA59 - NEVADA COUNTY | NC | T - SUMMER CAMP
CA2900523 | LPA59 - NEVADA COUNTY | C | R - RESIDENTIAL AREA
CA2900529 | LPA59 - NEVADA COUNTY | C | R - MOBILE HOME PARK
CA2900530 | LPA59 - NEVADA COUNTY | C | R - MOBILE HOME PARK
CA2900531 | LPA59 - NEVADA COUNTY | C | R - MOBILE HOME PARK
CA2900532 | LPA59 - NEVADA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA2900533 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2900534 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2900535 | LPA59 - NEVADA COUNTY | NTNC | NT - SCHOOL
CA2900536 | LPA59 - NEVADA COUNTY | NTNC | NT - SCHOOL
CA2900541 | LPA59 - NEVADA COUNTY | C | R - RESIDENTIAL AREA
CA2900546 | LPA59 - NEVADA COUNTY | C | NT - SCHOOL
CA2900547 | LPA59 - NEVADA COUNTY | NC | T - HOTEL/MOTEL
CA2900548 | LPA59 - NEVADA COUNTY | C | R - MOBILE HOME PARK
CA2900549 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2900550 | LPA59 - NEVADA COUNTY | NC | T - HOTEL/MOTEL
CA2900551 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2900553 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2900554 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2900556 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2900562 | LPA59 - NEVADA COUNTY | C | R - RESIDENTIAL AREA
CA2900563 | LPA59 - NEVADA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2900564 | LPA59 - NEVADA COUNTY | NC | T - RESTAURANT
CA2900567 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2900569 | LPA59 - NEVADA COUNTY | NC | T - SUMMER CAMP
CA2900570 | LPA59 - NEVADA COUNTY | NC | T - RESTAURANT
CA2900571 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2900578 | LPA59 - NEVADA COUNTY | NTNC | NT - SCHOOL
CA2900585 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2900587 | LPA59 - NEVADA COUNTY | NTNC | NT - SCHOOL
CA2900593 | LPA59 - NEVADA COUNTY | NTNC | NT - SCHOOL
CA2900595 | LPA59 - NEVADA COUNTY | NC | T - RESTAURANT
CA2900599 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2900601 | LPA59 - NEVADA COUNTY | NC | NT - SCHOOL
CA2900611 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2900613 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2900618 | LPA59 - NEVADA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2900619 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2900621 | LPA59 - NEVADA COUNTY | NC | T - SUMMER CAMP
CA2900623 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2900626 | LPA59 - NEVADA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA2900644 | LPA59 - NEVADA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2901208 | LPA59 - NEVADA COUNTY | NTNC | NT - SCHOOL
CA2901528 | LPA59 - NEVADA COUNTY | NC | T - RESTAURANT
CA2901551 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2901934 | LPA59 - NEVADA COUNTY | NC | T - SECONDARY RESIDENCES
CA2901994 | LPA59 - NEVADA COUNTY | NC | NT - SCHOOL
CA2902258 | LPA59 - NEVADA COUNTY | NC | T - SUMMER CAMP
CA2902326 | LPA59 - NEVADA COUNTY | NC | T - RESTAURANT
CA2902367 | LPA59 - NEVADA COUNTY | NC | T - RECREATION AREA
CA2902391 | LPA59 - NEVADA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2902392 | LPA59 - NEVADA COUNTY | NC | T - RESTAURANT
CA2903060 | LPA59 - NEVADA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2904010 | LPA59 - NEVADA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2904011 | LPA59 - NEVADA COUNTY | NTNC | NT - SCHOOL
CA2904020 | LPA59 - NEVADA COUNTY | NC | T - OTHER TRANSIENT AREA
CA2905001 | DISTRICT 09 - SACRAMENTO | NC | T - RECREATION AREA
CA2910001 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA2910002 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA2910003 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA2910004 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA2910006 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA2910010 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA2910011 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA2910013 | DISTRICT 09 - SACRAMENTO | C | NT - INSTITUTION
CA2910014 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA2910016 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA2910023 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA2910300 | DISTRICT 09 - SACRAMENTO | NC | T - RECREATION AREA
CA3000519 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3000585 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3000618 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3000734 | DISTRICT 08 - SANTA ANA | NTNC | T - RECREATION AREA
CA3000759 | DISTRICT 08 - SANTA ANA | NTNC | T - RECREATION AREA
CA3000767 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3000778 | DISTRICT 08 - SANTA ANA | NC | T - OTHER TRANSIENT AREA
CA3000819 | DISTRICT 08 - SANTA ANA | NTNC | O - OTHER AREA
CA3000825 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3000940 | DISTRICT 08 - SANTA ANA | NC | T - RECREATION AREA
CA3000980 | DISTRICT 08 - SANTA ANA | NTNC | NT - INSTITUTION
CA3010001 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010002 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010003 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010004 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010008 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010010 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010017 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010018 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010022 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010023 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010027 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010030 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010035 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010036 | DISTRICT 08 - SANTA ANA | C | O - OTHER AREA
CA3010037 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010038 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010041 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010042 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010046 | DISTRICT 08 - SANTA ANA | C | O - OTHER AREA
CA3010047 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010053 | DISTRICT 08 - SANTA ANA | C | O - OTHER AREA
CA3010062 | DISTRICT 08 - SANTA ANA | C | O - OTHER AREA
CA3010064 | DISTRICT 08 - SANTA ANA | C | O - OTHER AREA
CA3010068 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010069 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010071 | DISTRICT 08 - SANTA ANA | C | O - WHOLESALER (SELLS WATER)
CA3010073 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010079 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010082 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010092 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010093 | DISTRICT 08 - SANTA ANA | C | O - WHOLESALER (SELLS WATER)
CA3010094 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010097 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010100 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010101 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3010120 | DISTRICT 08 - SANTA ANA | C | O - WHOLESALER (SELLS WATER)
CA3100008 | LPA61 - PLACER COUNTY | NC | T - OTHER TRANSIENT AREA
CA3100010 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3100011 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA
CA3100014 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA
CA3100019 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA
CA3100023 | LPA61 - PLACER COUNTY | C | R - MOBILE HOME PARK
CA3100027 | LPA61 - PLACER COUNTY | NC | T - HOTEL/MOTEL
CA3100029 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA
CA3100034 | DISTRICT 09 - SACRAMENTO | NC | R - OTHER RESIDENTIAL AREA
CA3100035 | LPA61 - PLACER COUNTY | SSWS | R - RESIDENTIAL AREA
CA3100037 | LPA61 - PLACER COUNTY | SSWS | R - RESIDENTIAL AREA
CA3100038 | LPA61 - PLACER COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3100040 | LPA61 - PLACER COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3100041 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA
CA3100043 | LPA61 - PLACER COUNTY | C | R - MOBILE HOME PARK
CA3100058 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA
CA3100061 | LPA61 - PLACER COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3100062 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3100064 | LPA61 - PLACER COUNTY | SSWS | R - RESIDENTIAL AREA
CA3100067 | LPA61 - PLACER COUNTY | SSWS | R - RESIDENTIAL AREA
CA3100069 | LPA61 - PLACER COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3100072 | LPA61 - PLACER COUNTY | NTNC | NT - SCHOOL
CA3100079 | LPA61 - PLACER COUNTY | NC | NT - SCHOOL
CA3100080 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3100081 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3100082 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3100083 | LPA61 - PLACER COUNTY | NTNC | NT - SCHOOL
CA3100084 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3100085 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3100086 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3100088 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3100102 | LPA61 - PLACER COUNTY | NC | T - HOTEL/MOTEL
CA3100105 | LPA61 - PLACER COUNTY | NTNC | NT - SCHOOL
CA3100106 | LPA61 - PLACER COUNTY | NC | T - OTHER TRANSIENT AREA
CA3100114 | LPA61 - PLACER COUNTY | NC | T - SERVICE STATION
CA3100120 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3100528 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA
CA3100538 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA
CA3103195 | LPA61 - PLACER COUNTY | NC | T - SERVICE STATION
CA3103209 | LPA61 - PLACER COUNTY | NC | T - SUMMER CAMP
CA3103218 | LPA61 - PLACER COUNTY | NC | T - SUMMER CAMP
CA3103234 | LPA61 - PLACER COUNTY | NC | T - RESTAURANT
CA3103247 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3103261 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3103279 | LPA61 - PLACER COUNTY | NC | T - HOTEL/MOTEL
CA3103283 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3103288 | LPA61 - PLACER COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA3103291 | LPA61 - PLACER COUNTY | NTNC | T - RESTAURANT
CA3103294 | LPA61 - PLACER COUNTY | NTNC | T - RECREATION AREA
CA3103297 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3103309 | LPA61 - PLACER COUNTY | NC | R - RESIDENTIAL AREA
CA3103310 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA
CA3103665 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3103666 | LPA61 - PLACER COUNTY | NC | T - SECONDARY RESIDENCES
CA3103835 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA
CA3103836 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA
CA3104449 | LPA61 - PLACER COUNTY | NC | T - SUMMER CAMP
CA3104457 | LPA61 - PLACER COUNTY | NC | T - SUMMER CAMP
CA3104508 | LPA61 - PLACER COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3104519 | DISTRICT 02 - LASSEN | NC | T - OTHER TRANSIENT AREA
CA3105446 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3105779 | LPA61 - PLACER COUNTY | NTNC | T - SECONDARY RESIDENCES
CA3105852 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3105853 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3105886 | LPA61 - PLACER COUNTY | NC | T - OTHER TRANSIENT AREA
CA3106491 | LPA61 - PLACER COUNTY | NC | T - OTHER TRANSIENT AREA
CA3106937 | LPA61 - PLACER COUNTY | NTNC | R - OTHER RESIDENTIAL AREA
CA3107069 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3107084 | LPA61 - PLACER COUNTY | NTNC | T - RECREATION AREA
CA3107310 | LPA61 - PLACER COUNTY | NTNC | NT - MEDICAL FACILITY
CA3107311 | LPA61 - PLACER COUNTY | NC | T - RESTAURANT
CA3107315 | LPA61 - PLACER COUNTY | NC | T - HOTEL/MOTEL
CA3107318 | LPA61 - PLACER COUNTY | NC | T - HOTEL/MOTEL
CA3107320 | LPA61 - PLACER COUNTY | SSWS | R - RESIDENTIAL AREA
CA3107321 | LPA61 - PLACER COUNTY | NC | R - RESIDENTIAL AREA
CA3107322 | LPA61 - PLACER COUNTY | NTNC | T - RESTAURANT
CA3107323 | LPA61 - PLACER COUNTY | NC | T - OTHER TRANSIENT AREA
CA3107324 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3107327 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3107328 | LPA61 - PLACER COUNTY | NC | T - HOTEL/MOTEL
CA3107329 | LPA61 - PLACER COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3107332 | LPA61 - PLACER COUNTY | NC | T - SUMMER CAMP
CA3107334 | LPA61 - PLACER COUNTY | NC | T - RESTAURANT
CA3107337 | LPA61 - PLACER COUNTY | NC | T - RESTAURANT
CA3107338 | LPA61 - PLACER COUNTY | NC | T - RECREATION AREA
CA3107339 | LPA61 - PLACER COUNTY | C | R - RESIDENTIAL AREA
CA3107341 | LPA61 - PLACER COUNTY | NC | T - OTHER TRANSIENT AREA
CA3107342 | LPA61 - PLACER COUNTY | NTNC | NT - SCHOOL
CA3107343 | LPA61 - PLACER COUNTY | NC | T - RESTAURANT
CA3107344 | LPA61 - PLACER COUNTY | NC | T - OTHER TRANSIENT AREA
CA3107345 | LPA61 - PLACER COUNTY | LSS | T - RESTAURANT
CA3107346 | LPA61 - PLACER COUNTY | NC | T - OTHER TRANSIENT AREA
CA3107347 | LPA61 - PLACER COUNTY | LSS | T - RESTAURANT
CA3107348 | LPA61 - PLACER COUNTY | NC | T - OTHER TRANSIENT AREA
CA3107349 | LPA61 - PLACER COUNTY | NC | T - RESTAURANT
CA3107350 | LPA61 - PLACER COUNTY | NC | T - RESTAURANT
CA3110001 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110003 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110004 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110005 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110006 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110008 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110009 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110010 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110011 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110012 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110013 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110015 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110017 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110018 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110019 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110020 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110022 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110023 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110024 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110025 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110026 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3110028 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110029 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110031 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110034 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110035 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110036 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110040 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110041 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110042 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110043 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110044 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110047 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110048 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110049 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110050 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110051 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110124 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3110150 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3200001 | LPA62 - PLUMAS COUNTY | SSWS | T - HOTEL/MOTEL
CA3200006 | LPA62 - PLUMAS COUNTY | NC | T - HOTEL/MOTEL
CA3200007 | LPA62 - PLUMAS COUNTY | LSS | R - RESIDENTIAL AREA
CA3200008 | LPA62 - PLUMAS COUNTY | LSS | T - OTHER TRANSIENT AREA
CA3200009 | DISTRICT 02 - LASSEN | NC | T - HIGHWAY REST AREA
CA3200011 | LPA62 - PLUMAS COUNTY | SSWS | R - MOBILE HOME PARK
CA3200014 | LPA62 - PLUMAS COUNTY | SSWS | T - RECREATION AREA
CA3200015 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200016 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200017 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200019 | LPA62 - PLUMAS COUNTY | NC | T - SUMMER CAMP
CA3200020 | DISTRICT 02 - LASSEN | NC | T - HIGHWAY REST AREA
CA3200021 | LPA62 - PLUMAS COUNTY | LSS | T - RECREATION AREA
CA3200022 | DISTRICT 02 - LASSEN | NC | T - HIGHWAY REST AREA
CA3200024 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200026 | LPA62 - PLUMAS COUNTY | LSS | T - RECREATION AREA
CA3200030 | LPA62 - PLUMAS COUNTY | NC | T - HOTEL/MOTEL
CA3200031 | LPA62 - PLUMAS COUNTY | NC | T - HOTEL/MOTEL
CA3200032 | LPA62 - PLUMAS COUNTY | NC | T - HOTEL/MOTEL
CA3200033 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200034 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200036 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200037 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200038 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200039 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200040 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200044 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200046 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200047 | LPA62 - PLUMAS COUNTY | LSS | T - RECREATION AREA
CA3200048 | LPA62 - PLUMAS COUNTY | NTNC | T - RECREATION AREA
CA3200049 | LPA62 - PLUMAS COUNTY | NC | R - MOBILE HOME PARK
CA3200050 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200051 | LPA62 - PLUMAS COUNTY | NC | T - SUMMER CAMP
CA3200052 | LPA62 - PLUMAS COUNTY | LSS | T - RESTAURANT
CA3200053 | LPA62 - PLUMAS COUNTY | NC | T - HOTEL/MOTEL
CA3200054 | LPA62 - PLUMAS COUNTY | SSWS | R - RESIDENTIAL AREA
CA3200056 | LPA62 - PLUMAS COUNTY | SSWS | R - MOBILE HOME PARK
CA3200057 | LPA62 - PLUMAS COUNTY | SSWS | T - RECREATION AREA
CA3200058 | LPA62 - PLUMAS COUNTY | NC | T - SECONDARY RESIDENCES
CA3200059 | LPA62 - PLUMAS COUNTY | SSWS | R - RESIDENTIAL AREA
CA3200060 | LPA62 - PLUMAS COUNTY | NC | R - RESIDENTIAL AREA
CA3200061 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200062 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200064 | LPA62 - PLUMAS COUNTY | SSWS | T - HOTEL/MOTEL
CA3200065 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200066 | LPA62 - PLUMAS COUNTY | NC | R - MOBILE HOME PARK
CA3200067 | LPA62 - PLUMAS COUNTY | LSS | T - RECREATION AREA
CA3200068 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200069 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200071 | LPA62 - PLUMAS COUNTY | NC | T - HOTEL/MOTEL
CA3200072 | LPA62 - PLUMAS COUNTY | NC | T - HOTEL/MOTEL
CA3200075 | LPA62 - PLUMAS COUNTY | LSS | T - RECREATION AREA
CA3200078 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA
CA3200079 | LPA62 - PLUMAS COUNTY | NTNC | NT - SCHOOL
CA3200080 | LPA62 - PLUMAS COUNTY | SSWS | R - RESIDENTIAL AREA
CA3200083 | LPA62 - PLUMAS COUNTY | NC | R - MOBILE HOME PARK
CA3200084 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200085 | LPA62 - PLUMAS COUNTY | NC | T - RESTAURANT
CA3200094 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200095 | LPA62 - PLUMAS COUNTY | LSS | T - SUMMER CAMP
CA3200097 | LPA62 - PLUMAS COUNTY | NC | T - SUMMER CAMP
CA3200098 | LPA62 - PLUMAS COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3200099 | LPA62 - PLUMAS COUNTY | LSS | R - OTHER RESIDENTIAL AREA
CA3200100 | LPA62 - PLUMAS COUNTY | LSS | T - RECREATION AREA
CA3200101 | LPA62 - PLUMAS COUNTY | SSWS | R - RESIDENTIAL AREA
CA3200102 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3200104 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3200105 | LPA62 - PLUMAS COUNTY | SSWS | R - RESIDENTIAL AREA
CA3200107 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3200109 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200111 | LPA62 - PLUMAS COUNTY | NTNC | NT - SCHOOL
CA3200113 | LPA62 - PLUMAS COUNTY | SSWS | T - RECREATION AREA
CA3200114 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA
CA3200116 | LPA62 - PLUMAS COUNTY | SSWS | T - HOTEL/MOTEL
CA3200117 | LPA62 - PLUMAS COUNTY | LSS | T - RECREATION AREA
CA3200118 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200120 | LPA62 - PLUMAS COUNTY | SSWS | R - RESIDENTIAL AREA
CA3200122 | LPA62 - PLUMAS COUNTY | NC | T - HOTEL/MOTEL
CA3200123 | LPA62 - PLUMAS COUNTY | NC | R - RESIDENTIAL AREA
CA3200126 | LPA62 - PLUMAS COUNTY | NC | T - HOTEL/MOTEL
CA3200127 | LPA62 - PLUMAS COUNTY | C | R - MOBILE HOME PARK
CA3200130 | LPA62 - PLUMAS COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA3200134 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA
CA3200135 | LPA62 - PLUMAS COUNTY | SSWS | R - RESIDENTIAL AREA
CA3200138 | LPA62 - PLUMAS COUNTY | C | R - MOBILE HOME PARK
CA3200139 | LPA62 - PLUMAS COUNTY | NC | R - RESIDENTIAL AREA
CA3200141 | LPA62 - PLUMAS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3200142 | LPA62 - PLUMAS COUNTY | SSWS | R - RESIDENTIAL AREA
CA3200143 | LPA62 - PLUMAS COUNTY | NC | T - HOTEL/MOTEL
CA3200148 | LPA62 - PLUMAS COUNTY | C | R - MOBILE HOME PARK
CA3200151 | LPA62 - PLUMAS COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA3200153 | LPA62 - PLUMAS COUNTY | NC | R - MOBILE HOME PARK
CA3200155 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA
CA3200156 | LPA62 - PLUMAS COUNTY | SSWS | T - HOTEL/MOTEL
CA3200157 | LPA62 - PLUMAS COUNTY | SSWS | T - RECREATION AREA
CA3200162 | LPA62 - PLUMAS COUNTY | LSS | T - RECREATION AREA
CA3200163 | LPA62 - PLUMAS COUNTY | SSWS | R - RESIDENTIAL AREA
CA3200166 | LPA62 - PLUMAS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3200167 | LPA62 - PLUMAS COUNTY | SSWS | R - RESIDENTIAL AREA
CA3200171 | LPA62 - PLUMAS COUNTY | NC | R - MOBILE HOME PARK
CA3200172 | DISTRICT 02 - LASSEN | NC | R - RESIDENTIAL AREA
CA3200173 | LPA62 - PLUMAS COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA3200174 | LPA62 - PLUMAS COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA3200175 | LPA62 - PLUMAS COUNTY | NC | R - RESIDENTIAL AREA
CA3200176 | LPA62 - PLUMAS COUNTY | LSS | T - HOTEL/MOTEL
CA3200177 | LPA62 - PLUMAS COUNTY | NC | R - RESIDENTIAL AREA
CA3200178 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200180 | LPA62 - PLUMAS COUNTY | LSS | T - RECREATION AREA
CA3200185 | LPA62 - PLUMAS COUNTY | NC | T - SUMMER CAMP
CA3200186 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA3200187 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200188 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA
CA3200189 | LPA62 - PLUMAS COUNTY | C | R - MOBILE HOME PARK
CA3200192 | LPA62 - PLUMAS COUNTY | LSS | R - RESIDENTIAL AREA
CA3200193 | LPA62 - PLUMAS COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3200194 | LPA62 - PLUMAS COUNTY | LSS | T - RESTAURANT
CA3200195 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA
CA3200196 | LPA62 - PLUMAS COUNTY | LSS | T - RESTAURANT
CA3200197 | LPA62 - PLUMAS COUNTY | LSS | T - RESTAURANT
CA3200198 | LPA62 - PLUMAS COUNTY | LSS | T - RECREATION AREA
CA3200199 | LPA62 - PLUMAS COUNTY | LSS | T - RECREATION AREA
CA3200200 | LPA62 - PLUMAS COUNTY | SSWS | R - RESIDENTIAL AREA
CA3200203 | LPA62 - PLUMAS COUNTY | LSS | T - RECREATION AREA
CA3200204 | LPA62 - PLUMAS COUNTY | LSS | T - RECREATION AREA
CA3200205 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200206 | LPA62 - PLUMAS COUNTY | SSWS | R - RESIDENTIAL AREA
CA3200207 | LPA62 - PLUMAS COUNTY | NTNC | NT - INSTITUTION
CA3200209 | LPA62 - PLUMAS COUNTY | LSS | T - HOTEL/MOTEL
CA3200212 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200213 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200215 | LPA62 - PLUMAS COUNTY | NTNC | NT - SCHOOL
CA3200219 | LPA62 - PLUMAS COUNTY | NC | T - RESTAURANT
CA3200276 | LPA62 - PLUMAS COUNTY | LSS | T - RESTAURANT
CA3200301 | LPA62 - PLUMAS COUNTY | NC | T - SUMMER CAMP
CA3200406 | LPA62 - PLUMAS COUNTY | SSWS | R - RESIDENTIAL AREA
CA3200505 | DISTRICT 02 - LASSEN | NC | R - RESIDENTIAL AREA
CA3200507 | LPA62 - PLUMAS COUNTY | NC | T - SECONDARY RESIDENCES
CA3200509 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA
CA3200510 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3200610 | LPA62 - PLUMAS COUNTY | SSWS | R - RESIDENTIAL AREA
CA3200611 | LPA62 - PLUMAS COUNTY | SSWS | R - RESIDENTIAL AREA
CA3200612 | LPA62 - PLUMAS COUNTY | LSS | T - RECREATION AREA
CA3200616 | LPA62 - PLUMAS COUNTY | LSS | T - RESTAURANT
CA3200617 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200618 | LPA62 - PLUMAS COUNTY | LSS | T - SERVICE STATION
CA3200704 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3200718 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3205001 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA
CA3205003 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA
CA3205005 | LPA62 - PLUMAS COUNTY | NTNC | T - SUMMER CAMP
CA3205006 | LPA62 - PLUMAS COUNTY | C | R - RESIDENTIAL AREA
CA3205007 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3205009 | LPA62 - PLUMAS COUNTY | NC | R - MOBILE HOME PARK
CA3205011 | LPA62 - PLUMAS COUNTY | NC | T - RECREATION AREA
CA3210001 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3210002 | DISTRICT 02 - LASSEN | C | O - WHOLESALER (SELLS WATER)
CA3210003 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3210004 | DISTRICT 02 - LASSEN | C | O - OTHER AREA
CA3210005 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3210006 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3210007 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3210009 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3210010 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3210010 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3210011 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA3210300 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA3301011 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301018 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301025 | LPA63 - RIVERSIDE COUNTY | NC | T - SUMMER CAMP
CA3301027 | LPA63 - RIVERSIDE COUNTY | SSWS | NT - INDUSTRIAL/AGRICULTURAL
CA3301028 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK
CA3301031 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3301040 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK
CA3301044 | LPA63 - RIVERSIDE COUNTY | NC | T - RECREATION AREA
CA3301045 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK
CA3301055 | LPA63 - RIVERSIDE COUNTY | C | NT - INSTITUTION
CA3301058 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301063 | LPA63 - RIVERSIDE COUNTY | NC | T - SUMMER CAMP
CA3301075 | DISTRICT 20 - RIVERSIDE | NC | T - HIGHWAY REST AREA
CA3301082 | DISTRICT 20 - RIVERSIDE | NC | T - HIGHWAY REST AREA
CA3301097 | LPA63 - RIVERSIDE COUNTY | NC | T - SUMMER CAMP
CA3301099 | LPA63 - RIVERSIDE COUNTY | NC | T - SUMMER CAMP
CA3301100 | LPA63 - RIVERSIDE COUNTY | NC | T - SUMMER CAMP
CA3301107 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301113 | LPA63 - RIVERSIDE COUNTY | NC | NT - SCHOOL
CA3301114 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301115 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301125 | LPA63 - RIVERSIDE COUNTY | NC | T - RESTAURANT
CA3301132 | LPA63 - RIVERSIDE COUNTY | LSS | T - OTHER TRANSIENT AREA
CA3301133 | LPA63 - RIVERSIDE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3301137 | LPA63 - RIVERSIDE COUNTY | NC | T - SERVICE STATION
CA3301140 | LPA63 - RIVERSIDE COUNTY | NC | T - RECREATION AREA
CA3301141 | LPA63 - RIVERSIDE COUNTY | NP | T - RESTAURANT
CA3301143 | LPA63 - RIVERSIDE COUNTY | NTNC | NT - MEDICAL FACILITY
CA3301145 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301146 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301147 | LPA63 - RIVERSIDE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3301148 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301160 | LPA63 - RIVERSIDE COUNTY | NC | T - RECREATION AREA
CA3301161 | LPA63 - RIVERSIDE COUNTY | NC | T - RESTAURANT
CA3301164 | LPA63 - RIVERSIDE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3301169 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK
CA3301171 | LPA63 - RIVERSIDE COUNTY | C | T - OTHER TRANSIENT AREA
CA3301175 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301176 | LPA63 - RIVERSIDE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3301180 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301182 | LPA63 - RIVERSIDE COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3301183 | LPA63 - RIVERSIDE COUNTY | NC | T - RECREATION AREA
CA3301209 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301226 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301227 | LPA63 - RIVERSIDE COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA3301238 | LPA63 - RIVERSIDE COUNTY | NTNC | NT - MEDICAL FACILITY
CA3301245 | LPA63 - RIVERSIDE COUNTY | NC | R - MOBILE HOME PARK
CA3301247 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK
CA3301267 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301275 | LPA63 - RIVERSIDE COUNTY | NC | T - RESTAURANT
CA3301280 | LPA63 - RIVERSIDE COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3301283 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301293 | LPA63 - RIVERSIDE COUNTY | NC | R - RESIDENTIAL AREA
CA3301294 | LPA63 - RIVERSIDE COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3301297 | LPA63 - RIVERSIDE COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA3301305 | LPA63 - RIVERSIDE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3301308 | LPA63 - RIVERSIDE COUNTY | NTNC | NT - SCHOOL
CA3301309 | LPA63 - RIVERSIDE COUNTY | NTNC | NT - SCHOOL
CA3301327 | LPA63 - RIVERSIDE COUNTY | NC | T - SUMMER CAMP
CA3301330 | LPA63 - RIVERSIDE COUNTY | C | T - OTHER TRANSIENT AREA
CA3301350 | LPA63 - RIVERSIDE COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3301351 | LPA63 - RIVERSIDE COUNTY | NC | T - SERVICE STATION
CA3301355 | LPA63 - RIVERSIDE COUNTY | C | T - OTHER TRANSIENT AREA
CA3301359 | LPA63 - RIVERSIDE COUNTY | NC | T - RESTAURANT
CA3301373 | LPA63 - RIVERSIDE COUNTY | NTNC | T - RESTAURANT
CA3301380 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK
CA3301381 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK
CA3301385 | LPA63 - RIVERSIDE COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA3301388 | LPA63 - RIVERSIDE COUNTY | NTNC | T - RECREATION AREA
CA3301396 | LPA63 - RIVERSIDE COUNTY | NC | T - RESTAURANT
CA3301428 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3301482 | LPA63 - RIVERSIDE COUNTY | C | T - RECREATION AREA
CA3301491 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301491 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301494 | LPA63 - RIVERSIDE COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA3301502 | LPA63 - RIVERSIDE COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3301510 | LPA63 - RIVERSIDE COUNTY | NC | T - SUMMER CAMP
CA3301511 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301512 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301512 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301528 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301529 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301529 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301534 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3301535 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301541 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301557 | LPA63 - RIVERSIDE COUNTY | NC | NT - INSTITUTION
CA3301564 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301567 | LPA63 - RIVERSIDE COUNTY | NC | T - SUMMER CAMP
CA3301568 | LPA63 - RIVERSIDE COUNTY | NC | T - RECREATION AREA
CA3301570 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301571 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301577 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301588 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301622 | LPA63 - RIVERSIDE COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA3301630 | DISTRICT 20 - RIVERSIDE | C | R - MOBILE HOME PARK
CA3301631 | LPA63 - RIVERSIDE COUNTY | NC | T - SUMMER CAMP
CA3301642 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301643 | LPA63 - RIVERSIDE COUNTY | SSWS | R - RESIDENTIAL AREA
CA3301644 | LPA63 - RIVERSIDE COUNTY | NC | T - RESTAURANT
CA3301676 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301682 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301683 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301687 | LPA63 - RIVERSIDE COUNTY | NC | R - MOBILE HOME PARK
CA3301690 | LPA63 - RIVERSIDE COUNTY | NC | NT - INSTITUTION
CA3301693 | LPA63 - RIVERSIDE COUNTY | NC | T - RECREATION AREA
CA3301699 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301701 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301704 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301706 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301709 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301717 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK
CA3301731 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301732 | LPA63 - RIVERSIDE COUNTY | LSS | T - RESTAURANT
CA3301750 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301756 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301775 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3301797 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301800 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301803 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK
CA3301850 | LPA63 - RIVERSIDE COUNTY | SSWS | R - RESIDENTIAL AREA
CA3301860 | LPA63 - RIVERSIDE COUNTY | NC | T - RECREATION AREA
CA3301863 | LPA63 - RIVERSIDE COUNTY | C | NT - INSTITUTION
CA3301877 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301879 | DISTRICT 20 - RIVERSIDE | C | R - MOBILE HOME PARK
CA3301902 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3301935 | LPA63 - RIVERSIDE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3301937 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301939 | LPA63 - RIVERSIDE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3301943 | DISTRICT 20 - RIVERSIDE | C | R - MOBILE HOME PARK
CA3301946 | LPA63 - RIVERSIDE COUNTY | NC | T - RESTAURANT
CA3301947 | LPA63 - RIVERSIDE COUNTY | NC | NT - SCHOOL
CA3301961 | LPA63 - RIVERSIDE COUNTY | NTNC | T - RECREATION AREA
CA3301979 | LPA63 - RIVERSIDE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3301981 | LPA63 - RIVERSIDE COUNTY | NC | R - MOBILE HOME PARK
CA3301989 | LPA63 - RIVERSIDE COUNTY | LSS | T - RESTAURANT
CA3301990 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3301991 | LPA63 - RIVERSIDE COUNTY | NC | T - RESTAURANT
CA3302009 | LPA63 - RIVERSIDE COUNTY | SSWS | R - MOBILE HOME PARK
CA3302018 | DISTRICT 20 - RIVERSIDE | NC | T - HIGHWAY REST AREA
CA3302020 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3302026 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3302049 | LPA63 - RIVERSIDE COUNTY | NC | T - RESTAURANT
CA3302051 | LPA63 - RIVERSIDE COUNTY | SSWS | NT - INDUSTRIAL/AGRICULTURAL
CA3302060 | LPA63 - RIVERSIDE COUNTY | NC | T - RESTAURANT
CA3302062 | LPA63 - RIVERSIDE COUNTY | NC | T - RESTAURANT
CA3302079 | LPA63 - RIVERSIDE COUNTY | SSWS | R - RESIDENTIAL AREA
CA3302081 | LPA63 - RIVERSIDE COUNTY | LSS | R - OTHER RESIDENTIAL AREA
CA3302091 | LPA63 - RIVERSIDE COUNTY | NC | T - SUMMER CAMP
CA3302094 | LPA63 - RIVERSIDE COUNTY | NC | T - SUMMER CAMP
CA3302099 | LPA63 - RIVERSIDE COUNTY | SSWS | R - MOBILE HOME PARK
CA3302102 | LPA63 - RIVERSIDE COUNTY | NC | T - SERVICE STATION
CA3303002 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3303003 | LPA63 - RIVERSIDE COUNTY | C | R - RESIDENTIAL AREA
CA3303007 | LPA63 - RIVERSIDE COUNTY | SSWS | T - SECONDARY RESIDENCES
CA3303010 | LPA63 - RIVERSIDE COUNTY | NC | T - RECREATION AREA
CA3303011 | LPA63 - RIVERSIDE COUNTY | NC | T - RECREATION AREA
CA3303014 | LPA63 - RIVERSIDE COUNTY | NC | T - RECREATION AREA
CA3303021 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3303026 | LPA63 - RIVERSIDE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3303028 | LPA63 - RIVERSIDE COUNTY | SSWS | R - MOBILE HOME PARK
CA3303035 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK
CA3303041 | LPA63 - RIVERSIDE COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA3303048 | LPA63 - RIVERSIDE COUNTY | SSWS | R - MOBILE HOME PARK
CA3303064 | LPA63 - RIVERSIDE COUNTY | NC | T - SERVICE STATION
CA3303071 | LPA63 - RIVERSIDE COUNTY | NTNC | T - RECREATION AREA
CA3303072 | LPA63 - RIVERSIDE COUNTY | NTNC | T - RECREATION AREA
CA3303077 | LPA63 - RIVERSIDE COUNTY | NC | T - RESTAURANT
CA3303084 | LPA63 - RIVERSIDE COUNTY | NC | T - OTHER TRANSIENT AREA
CA3303087 | LPA63 - RIVERSIDE COUNTY | C | R - MOBILE HOME PARK
CA3303090 | LPA63 - RIVERSIDE COUNTY | NC | T - RECREATION AREA
CA3303092 | LPA63 - RIVERSIDE COUNTY | NTNC | T - RESTAURANT
CA3303104 | LPA63 - RIVERSIDE COUNTY | NC | T - RESTAURANT
CA3303112 | LPA63 - RIVERSIDE COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3310001 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310002 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310003 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3310004 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310005 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310006 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310007 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3310008 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3310009 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310012 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3310016 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310017 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310018 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310019 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3310020 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310021 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310022 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310025 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310026 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310028 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310029 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3310030 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310031 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310032 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3310033 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310036 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310037 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310038 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3310040 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310044 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3310046 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310047 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310048 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3310049 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3310051 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310052 | DISTRICT 20 - RIVERSIDE | C | R - OTHER RESIDENTIAL AREA
CA3310074 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3310075 | DISTRICT 20 - RIVERSIDE | C | O - WHOLESALER (SELLS WATER)
CA3310076 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3310078 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3310080 | DISTRICT 20 - RIVERSIDE | C | R - MOBILE HOME PARK
CA3310081 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3310082 | DISTRICT 20 - RIVERSIDE | C | R - RESIDENTIAL AREA
CA3310083 | DISTRICT 20 - RIVERSIDE | C | O - WHOLESALER (SELLS WATER)
CA3310084 | DISTRICT 20 - RIVERSIDE | NTNC | NT - INSTITUTION
CA3310301 | DISTRICT 20 - RIVERSIDE | NC | T - RECREATION AREA
CA3310501 | DISTRICT 20 - RIVERSIDE | NC | T - RECREATION AREA
CA3310502 | DISTRICT 20 - RIVERSIDE | NC | T - RECREATION AREA
CA3310800 | DISTRICT 20 - RIVERSIDE | C | NT - INSTITUTION
CA3310801 | DISTRICT 20 - RIVERSIDE | C | NT - INSTITUTION
CA3310802 | DISTRICT 20 - RIVERSIDE | C | NT - INSTITUTION
CA3400100 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400101 | LPA64 - SACRAMENTO COUNTY | C | R - RESIDENTIAL AREA
CA3400103 | LPA64 - SACRAMENTO COUNTY | C | T - RECREATION AREA
CA3400106 | LPA64 - SACRAMENTO COUNTY | C | R - RESIDENTIAL AREA
CA3400107 | LPA64 - SACRAMENTO COUNTY | C | T - RECREATION AREA
CA3400113 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400117 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400119 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400121 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK
CA3400122 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK
CA3400123 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400125 | LPA64 - SACRAMENTO COUNTY | C | T - RECREATION AREA
CA3400128 | LPA64 - SACRAMENTO COUNTY | C | T - RECREATION AREA
CA3400130 | LPA64 - SACRAMENTO COUNTY | C | R - RESIDENTIAL AREA
CA3400131 | DISTRICT 09 - SACRAMENTO | NC | T - HIGHWAY REST AREA
CA3400133 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400135 | LPA64 - SACRAMENTO COUNTY | C | T - RECREATION AREA
CA3400137 | LPA64 - SACRAMENTO COUNTY | C | R - RESIDENTIAL AREA
CA3400138 | LPA64 - SACRAMENTO COUNTY | C | R - RESIDENTIAL AREA
CA3400139 | LPA64 - SACRAMENTO COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA3400141 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400144 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400147 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400149 | LPA64 - SACRAMENTO COUNTY | C | T - RECREATION AREA
CA3400150 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK
CA3400151 | LPA64 - SACRAMENTO COUNTY | NC | T - HOTEL/MOTEL
CA3400155 | LPA64 - SACRAMENTO COUNTY | C | R - RESIDENTIAL AREA
CA3400156 | LPA64 - SACRAMENTO COUNTY | C | R - RESIDENTIAL AREA
CA3400164 | LPA64 - SACRAMENTO COUNTY | C | T - RECREATION AREA
CA3400166 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400167 | LPA64 - SACRAMENTO COUNTY | NC | R - RESIDENTIAL AREA
CA3400168 | LPA64 - SACRAMENTO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3400169 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK
CA3400172 | LPA64 - SACRAMENTO COUNTY | C | R - RESIDENTIAL AREA
CA3400173 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3400175 | LPA64 - SACRAMENTO COUNTY | SSWS | T - HOTEL/MOTEL
CA3400179 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK
CA3400180 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - INSTITUTION
CA3400181 | LPA64 - SACRAMENTO COUNTY | C | T - RECREATION AREA
CA3400190 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK
CA3400191 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK
CA3400192 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK
CA3400201 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400202 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400204 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400206 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400208 | LPA64 - SACRAMENTO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3400213 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400216 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400217 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK
CA3400224 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400226 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400229 | LPA64 - SACRAMENTO COUNTY | C | NT - INSTITUTION
CA3400232 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3400240 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3400248 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL
CA3400250 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL
CA3400251 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL
CA3400253 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL
CA3400254 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL
CA3400267 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL
CA3400268 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL
CA3400271 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL
CA3400273 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL
CA3400278 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL
CA3400283 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400286 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400296 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK
CA3400297 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400302 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400303 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400331 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK
CA3400333 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400334 | LPA64 - SACRAMENTO COUNTY | NC | R - RESIDENTIAL AREA
CA3400335 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK
CA3400336 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400342 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3400346 | LPA64 - SACRAMENTO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3400356 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400358 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3400364 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - DAY CARE CENTER
CA3400374 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400375 | LPA64 - SACRAMENTO COUNTY | NC | NT - INSTITUTION
CA3400376 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400377 | LPA64 - SACRAMENTO COUNTY | NC | R - RESIDENTIAL AREA
CA3400379 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400380 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400382 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400383 | LPA64 - SACRAMENTO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3400387 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3400391 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL
CA3400393 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400394 | LPA64 - SACRAMENTO COUNTY | NTNC | T - RECREATION AREA
CA3400396 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400397 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK
CA3400399 | LPA64 - SACRAMENTO COUNTY | NP | T - RESTAURANT
CA3400401 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK
CA3400402 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - SCHOOL
CA3400406 | LPA64 - SACRAMENTO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3400408 | LPA64 - SACRAMENTO COUNTY | SSWS | R - MOBILE HOME PARK
CA3400410 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400416 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3400417 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400418 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400419 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400420 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400424 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400425 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3400426 | LPA64 - SACRAMENTO COUNTY | LSS | R - MOBILE HOME PARK
CA3400428 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400429 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3400432 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400433 | LPA64 - SACRAMENTO COUNTY | C | R - MOBILE HOME PARK
CA3400434 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3400435 | LPA64 - SACRAMENTO COUNTY | NC | T - SERVICE STATION
CA3400441 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400443 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400444 | LPA64 - SACRAMENTO COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA3400445 | LPA64 - SACRAMENTO COUNTY | SSWS | T - OTHER TRANSIENT AREA
CA3400446 | LPA64 - SACRAMENTO COUNTY | LSS | T - RESTAURANT
CA3400448 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400451 | LPA64 - SACRAMENTO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3400452 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3400453 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3400454 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3400455 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400456 | LPA64 - SACRAMENTO COUNTY | NTNC | O - WHOLESALER (SELLS WATER)
CA3400457 | LPA64 - SACRAMENTO COUNTY | NC | T - SERVICE STATION
CA3400458 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400459 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400460 | LPA64 - SACRAMENTO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3400461 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400462 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400463 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3400464 | LPA64 - SACRAMENTO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3400465 | LPA64 - SACRAMENTO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3400466 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400467 | LPA64 - SACRAMENTO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3400469 | LPA64 - SACRAMENTO COUNTY | NC | T - RESTAURANT
CA3400470 | LPA64 - SACRAMENTO COUNTY | NC | T - SERVICE STATION
CA3400471 | LPA64 - SACRAMENTO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3400473 | LPA64 - SACRAMENTO COUNTY | NTNC | T - RETAIL EMPLOYEES
CA3400475 | LPA64 - SACRAMENTO COUNTY | NTNC | NT - OTHER NON-TRANSIENT AREA
CA3410001 | DISTRICT 09 - SACRAMENTO | C | O - WHOLESALER (SELLS WATER)
CA3410002 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410003 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410004 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410005 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410006 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410007 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410008 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410009 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410010 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410011 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410012 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410013 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410014 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410015 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410016 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410017 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410018 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410020 | DISTRICT 09 - SACRAMENTO | C | O - WHOLESALER (SELLS WATER)
CA3410021 | DISTRICT 09 - SACRAMENTO | C | O - WHOLESALER (SELLS WATER)
CA3410022 | DISTRICT 09 - SACRAMENTO | C | R - MOBILE HOME PARK
CA3410023 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410026 | DISTRICT 09 - SACRAMENTO | C | O - OTHER AREA
CA3410027 | DISTRICT 09 - SACRAMENTO | NTNC | R - RESIDENTIAL AREA
CA3410029 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410030 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410031 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410032 | DISTRICT 09 - SACRAMENTO | C | NT - INSTITUTION
CA3410033 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410035 | LPA64 - SACRAMENTO COUNTY | NC | T - RECREATION AREA
CA3410045 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410047 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410301 | DISTRICT 09 - SACRAMENTO | NC | T - RECREATION AREA
CA3410302 | DISTRICT 09 - SACRAMENTO | NC | T - RECREATION AREA
CA3410303 | DISTRICT 09 - SACRAMENTO | NC | T - RECREATION AREA
CA3410704 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA3410802 | DISTRICT 09 - SACRAMENTO | NTNC | NT - SCHOOL
CA3500006 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500505 | DISTRICT 05 - MONTEREY | C | T - RECREATION AREA
CA3500507 | DISTRICT 05 - MONTEREY | NTNC | NT - SCHOOL
CA3500509 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500510 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500511 | DISTRICT 05 - MONTEREY | C | NT - INDUSTRIAL/AGRICULTURAL
CA3500521 | DISTRICT 05 - MONTEREY | NTNC | NT - SCHOOL
CA3500524 | DISTRICT 17 - SANTA CLARA | C | R - MOBILE HOME PARK
CA3500527 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500537 | DISTRICT 05 - MONTEREY | NC | R - RESIDENTIAL AREA
CA3500539 | DISTRICT 05 - MONTEREY | NC | O - OTHER AREA
CA3500549 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500550 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500552 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500556 | DISTRICT 05 - MONTEREY | C | R - MOBILE HOME PARK
CA3500557 | DISTRICT 05 - MONTEREY | NC | T - RECREATION AREA
CA3500559 | DISTRICT 05 - MONTEREY | NC | T - OTHER TRANSIENT AREA
CA3500562 | DISTRICT 05 - MONTEREY | NTNC | T - RECREATION AREA
CA3500563 | DISTRICT 05 - MONTEREY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3500570 | DISTRICT 05 - MONTEREY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3500571 | DISTRICT 05 - MONTEREY | NTNC | NT - SCHOOL
CA3500575 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500576 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500578 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500579 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500581 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500801 | DISTRICT 05 - MONTEREY | NTNC | NT - SCHOOL
CA3500804 | DISTRICT 05 - MONTEREY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3500805 | DISTRICT 05 - MONTEREY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3500810 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500823 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500825 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500830 | DISTRICT 05 - MONTEREY | C | NT - INDUSTRIAL/AGRICULTURAL
CA3500836 | DISTRICT 05 - MONTEREY | C | T - RECREATION AREA
CA3500900 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500904 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500905 | DISTRICT 05 - MONTEREY | NTNC | NT - SCHOOL
CA3500910 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500911 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500912 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500913 | DISTRICT 05 - MONTEREY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3500917 | DISTRICT 05 - MONTEREY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3500919 | DISTRICT 05 - MONTEREY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3500920 | DISTRICT 05 - MONTEREY | NC | T - OTHER TRANSIENT AREA
CA3500923 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3500925 | DISTRICT 05 - MONTEREY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3500927 | DISTRICT 05 - MONTEREY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3500928 | DISTRICT 05 - MONTEREY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3500929 | DISTRICT 05 - MONTEREY | NC | R - OTHER RESIDENTIAL AREA
CA3500930 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3510001 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3510002 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3510003 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3510004 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA3510006 | DISTRICT 05 - MONTEREY | C | R - MOBILE HOME PARK
CA3510007 | DISTRICT 05 - MONTEREY | C | O - WHOLESALER (SELLS WATER)
CA3510009 | DISTRICT 05 - MONTEREY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3510300 | DISTRICT 05 - MONTEREY | NC | T - RECREATION AREA
CA3510302 | DISTRICT 05 - MONTEREY | NC | T - RECREATION AREA
CA3510500 | DISTRICT 05 - MONTEREY | NC | T - RECREATION AREA
CA3510501 | DISTRICT 05 - MONTEREY | NC | T - RECREATION AREA
CA3510502 | DISTRICT 05 - MONTEREY | NC | T - RECREATION AREA
CA3600005 | LPA66 - SAN BERNARDINO COUNTY | SSWS | T - RECREATION AREA
CA3600008 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3600009 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3600010 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600011 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600012 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600022 | LPA66 - SAN BERNARDINO COUNTY | C | T - SECONDARY RESIDENCES
CA3600025 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600027 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600031 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600032 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SECONDARY RESIDENCES
CA3600036 | LPA66 - SAN BERNARDINO COUNTY | NTNC | T - RECREATION AREA
CA3600044 | DISTRICT 13 - SAN BERNARDINO | NC | T - OTHER TRANSIENT AREA
CA3600062 | LPA66 - SAN BERNARDINO COUNTY | NTNC | R - OTHER RESIDENTIAL AREA
CA3600063 | LPA66 - SAN BERNARDINO COUNTY | SSWS | T - RECREATION AREA
CA3600064 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600070 | LPA66 - SAN BERNARDINO COUNTY | C | T - SECONDARY RESIDENCES
CA3600071 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600086 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600087 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600088 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600089 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600094 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600105 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600106 | LPA66 - SAN BERNARDINO COUNTY | NTNC | R - RESIDENTIAL AREA
CA3600107 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600108 | LPA66 - SAN BERNARDINO COUNTY | C | T - RECREATION AREA
CA3600111 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3600114 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600123 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600124 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3600132 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3600133 | LPA66 - SAN BERNARDINO COUNTY | NC | R - RESIDENTIAL AREA
CA3600139 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3600140 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3600141 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3600149 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3600152 | LPA66 - SAN BERNARDINO COUNTY | C | NT - MEDICAL FACILITY
CA3600154 | LPA66 - SAN BERNARDINO COUNTY | NTNC | T - RESTAURANT
CA3600155 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK
CA3600156 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600157 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600158 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600166 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600172 | LPA66 - SAN BERNARDINO COUNTY | C | T - SECONDARY RESIDENCES
CA3600180 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600183 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SECONDARY RESIDENCES
CA3600184 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600185 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600187 | LPA66 - SAN BERNARDINO COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3600192 | LPA66 - SAN BERNARDINO COUNTY | NTNC | R - RESIDENTIAL AREA
CA3600193 | LPA66 - SAN BERNARDINO COUNTY | NTNC | R - RESIDENTIAL AREA
CA3600196 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600197 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA3600200 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600205 | LPA66 - SAN BERNARDINO COUNTY | NC | R - RESIDENTIAL AREA
CA3600209 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600215 | LPA66 - SAN BERNARDINO COUNTY | C | NT - MEDICAL FACILITY
CA3600220 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600222 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3600226 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600257 | LPA66 - SAN BERNARDINO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3600258 | LPA66 - SAN BERNARDINO COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3600260 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600262 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600270 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600279 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600283 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600297 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600298 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3600301 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600306 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3600307 | LPA66 - SAN BERNARDINO COUNTY | SSWS | T - RECREATION AREA
CA3600308 | LPA66 - SAN BERNARDINO COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3600314 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3600321 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA3600323 | DISTRICT 13 - SAN BERNARDINO | NC | T - OTHER TRANSIENT AREA
CA3600335 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3600345 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600356 | LPA66 - SAN BERNARDINO COUNTY | NC | R - MOBILE HOME PARK
CA3600360 | LPA66 - SAN BERNARDINO COUNTY | NC | R - MOBILE HOME PARK
CA3600365 | DISTRICT 13 - SAN BERNARDINO | NC | R - RESIDENTIAL AREA
CA3600367 | LPA66 - SAN BERNARDINO COUNTY | NC | R - RESIDENTIAL AREA
CA3600368 | LPA66 - SAN BERNARDINO COUNTY | NC | R - MOBILE HOME PARK
CA3600370 | DISTRICT 13 - SAN BERNARDINO | NC | R - RESIDENTIAL AREA
CA3600371 | LPA66 - SAN BERNARDINO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3600372 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK
CA3600375 | LPA66 - SAN BERNARDINO COUNTY | NC | R - RESIDENTIAL AREA
CA3600376 | DISTRICT 13 - SAN BERNARDINO | NC | T - HOTEL/MOTEL
CA3600377 | LPA66 - SAN BERNARDINO COUNTY | NC | T - HOTEL/MOTEL
CA3600378 | LPA66 - SAN BERNARDINO COUNTY | NC | R - RESIDENTIAL AREA
CA3600380 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SECONDARY RESIDENCES
CA3600381 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3600382 | DISTRICT 13 - SAN BERNARDINO | C | T - SECONDARY RESIDENCES
CA3600383 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3600384 | LPA66 - SAN BERNARDINO COUNTY | NC | R - MOBILE HOME PARK
CA3600385 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK
CA3600386 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK
CA3600388 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK
CA3600389 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - MOBILE HOME PARK
CA3600391 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK
CA3600393 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INSTITUTION
CA3600394 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - MOBILE HOME PARK
CA3600395 | LPA66 - SAN BERNARDINO COUNTY | NC | R - RESIDENTIAL AREA
CA3600397 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK
CA3600399 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK
CA3600400 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK
CA3600404 | LPA66 - SAN BERNARDINO COUNTY | NC | R - MOBILE HOME PARK
CA3600406 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RECREATION AREA
CA3600409 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RECREATION AREA
CA3600412 | LPA66 - SAN BERNARDINO COUNTY | NC | R - MOBILE HOME PARK
CA3600415 | LPA66 - SAN BERNARDINO COUNTY | NC | T - HOTEL/MOTEL
CA3600432 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - SCHOOL
CA3600437 | LPA66 - SAN BERNARDINO COUNTY | SSWS | T - RECREATION AREA
CA3600446 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600452 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RECREATION AREA
CA3600453 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RECREATION AREA
CA3600478 | LPA66 - SAN BERNARDINO COUNTY | NTNC | T - SUMMER CAMP
CA3600481 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600483 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600485 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600490 | LPA66 - SAN BERNARDINO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3600500 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SERVICE STATION
CA3600504 | LPA66 - SAN BERNARDINO COUNTY | C | T - OTHER TRANSIENT AREA
CA3600509 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3600510 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SECONDARY RESIDENCES
CA3600512 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3600513 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3600524 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3600530 | DISTRICT 13 - SAN BERNARDINO | NC | T - SUMMER CAMP
CA3600532 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600534 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600536 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600537 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600538 | DISTRICT 13 - SAN BERNARDINO | NC | T - RESTAURANT
CA3600540 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3600541 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3600554 | LPA66 - SAN BERNARDINO COUNTY | NC | T - HOTEL/MOTEL
CA3600568 | LPA66 - SAN BERNARDINO COUNTY | NC | T - HOTEL/MOTEL
CA3600585 | LPA66 - SAN BERNARDINO COUNTY | NTNC | T - SUMMER CAMP
CA3600586 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600587 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600588 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600589 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600591 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600593 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600595 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600596 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600597 | LPA66 - SAN BERNARDINO COUNTY | NTNC | T - SUMMER CAMP
CA3600600 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600601 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600602 | LPA66 - SAN BERNARDINO COUNTY | NC | NT - INSTITUTION
CA3600604 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600608 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3600613 | LPA66 - SAN BERNARDINO COUNTY | NC | T - HOTEL/MOTEL
CA3600620 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RECREATION AREA
CA3600704 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600707 | LPA66 - SAN BERNARDINO COUNTY | NTNC | T - RESTAURANT
CA3600740 | LPA66 - SAN BERNARDINO COUNTY | SSWS | T - RECREATION AREA
CA3600756 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SECONDARY RESIDENCES
CA3600760 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600765 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RECREATION AREA
CA3600767 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600768 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SECONDARY RESIDENCES
CA3600770 | DISTRICT 13 - SAN BERNARDINO | NC | T - SUMMER CAMP
CA3600771 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600772 | DISTRICT 13 - SAN BERNARDINO | NC | T - SUMMER CAMP
CA3600776 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3600777 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600783 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3600784 | LPA66 - SAN BERNARDINO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3600785 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3600790 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - SCHOOL
CA3600797 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INSTITUTION
CA3601004 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SECONDARY RESIDENCES
CA3601006 | LPA66 - SAN BERNARDINO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3601010 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3601012 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601013 | LPA66 - SAN BERNARDINO COUNTY | NTNC | R - RESIDENTIAL AREA
CA3601015 | LPA66 - SAN BERNARDINO COUNTY | C | T - SUMMER CAMP
CA3601016 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601019 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601020 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601024 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3601027 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SECONDARY RESIDENCES
CA3601029 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3601034 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3601036 | LPA66 - SAN BERNARDINO COUNTY | C | R - RESIDENTIAL AREA
CA3601037 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601040 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601045 | LPA66 - SAN BERNARDINO COUNTY | C | R - MOBILE HOME PARK
CA3601046 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3601047 | LPA66 - SAN BERNARDINO COUNTY | NC | NT - INSTITUTION
CA3601048 | DISTRICT 13 - SAN BERNARDINO | C | T - RECREATION AREA
CA3601051 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3601052 | LPA66 - SAN BERNARDINO COUNTY | NC | NT - INSTITUTION
CA3601057 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - SCHOOL
CA3601061 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3601062 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3601064 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3601070 | LPA66 - SAN BERNARDINO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3601077 | LPA66 - SAN BERNARDINO COUNTY | NC | T - HOTEL/MOTEL
CA3601079 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3601081 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3601082 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3601085 | LPA66 - SAN BERNARDINO COUNTY | C | NT - MEDICAL FACILITY
CA3601089 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3601095 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - SCHOOL
CA3601096 | DISTRICT 13 - SAN BERNARDINO | NC | T - OTHER TRANSIENT AREA
CA3601097 | DISTRICT 13 - SAN BERNARDINO | NC | T - OTHER TRANSIENT AREA
CA3601098 | DISTRICT 13 - SAN BERNARDINO | NC | T - OTHER TRANSIENT AREA
CA3601100 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SERVICE STATION
CA3601101 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SERVICE STATION
CA3601105 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SERVICE STATION
CA3601106 | LPA66 - SAN BERNARDINO COUNTY | NTNC | T - HIGHWAY REST AREA
CA3601107 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601108 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601109 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601110 | LPA66 - SAN BERNARDINO COUNTY | SSWS | T - RECREATION AREA
CA3601112 | LPA66 - SAN BERNARDINO COUNTY | NC | NT - MEDICAL FACILITY
CA3601113 | LPA66 - SAN BERNARDINO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3601115 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601117 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3601121 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SERVICE STATION
CA3601122 | LPA66 - SAN BERNARDINO COUNTY | NTNC | T - RECREATION AREA
CA3601128 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA3601130 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3601131 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601133 | LPA66 - SAN BERNARDINO COUNTY | NTNC | T - HIGHWAY REST AREA
CA3601134 | LPA66 - SAN BERNARDINO COUNTY | NC | T - HOTEL/MOTEL
CA3601135 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - MEDICAL FACILITY
CA3601137 | LPA66 - SAN BERNARDINO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3601139 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3601140 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3601141 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SUMMER CAMP
CA3601143 | LPA66 - SAN BERNARDINO COUNTY | NC | R - MOBILE HOME PARK
CA3601144 | LPA66 - SAN BERNARDINO COUNTY | NC | NT - INSTITUTION
CA3601145 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3601147 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601148 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601150 | LPA66 - SAN BERNARDINO COUNTY | NTNC | T - RECREATION AREA
CA3601151 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RECREATION AREA
CA3601152 | LPA66 - SAN BERNARDINO COUNTY | NC | R - RESIDENTIAL AREA
CA3601153 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3601155 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3601157 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RECREATION AREA
CA3601158 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RECREATION AREA
CA3601159 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3601161 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601162 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601163 | LPA66 - SAN BERNARDINO COUNTY | NC | O - OTHER AREA
CA3601165 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601166 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RECREATION AREA
CA3601167 | LPA66 - SAN BERNARDINO COUNTY | SSWS | T - RECREATION AREA
CA3601168 | LPA66 - SAN BERNARDINO COUNTY | NC | R - MOBILE HOME PARK
CA3601169 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SERVICE STATION
CA3601170 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601171 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601172 | LPA66 - SAN BERNARDINO COUNTY | NC | T - HOTEL/MOTEL
CA3601173 | LPA66 - SAN BERNARDINO COUNTY | NC | R - MOBILE HOME PARK
CA3601175 | LPA66 - SAN BERNARDINO COUNTY | NC | T - SERVICE STATION
CA3601176 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601179 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - SCHOOL
CA3601180 | LPA66 - SAN BERNARDINO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3601181 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3601182 | LPA66 - SAN BERNARDINO COUNTY | C | NT - INSTITUTION
CA3601183 | LPA66 - SAN BERNARDINO COUNTY | NC | T - RESTAURANT
CA3601184 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3601185 | LPA66 - SAN BERNARDINO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3601187 | LPA66 - SAN BERNARDINO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3610001 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610002 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610003 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610004 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610005 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610006 | DISTRICT 13 - SAN BERNARDINO | C | O - WHOLESALER (SELLS WATER)
CA3610008 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610009 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610011 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610012 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610013 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610014 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610015 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610016 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610017 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610018 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610019 | DISTRICT 13 - SAN BERNARDINO | C | O - WHOLESALER (SELLS WATER)
CA3610021 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610022 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610023 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610024 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610025 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610026 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610028 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610029 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610030 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610031 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610032 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610033 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610034 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610036 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610037 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610038 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610039 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610041 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610043 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610044 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610045 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610046 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610047 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610048 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610048 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610049 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610050 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610051 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610052 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610053 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610055 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610057 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610060 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610062 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610063 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610064 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610073 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610075 | DISTRICT 13 - SAN BERNARDINO | C | O - WHOLESALER (SELLS WATER)
CA3610082 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610085 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610086 | DISTRICT 13 - SAN BERNARDINO | C | O - WHOLESALER (SELLS WATER)
CA3610093 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610105 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610107 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610108 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610109 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610109 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610110 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610112 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610114 | DISTRICT 13 - SAN BERNARDINO | C | O - WHOLESALER (SELLS WATER)
CA3610117 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610118 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610120 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610121 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610125 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610125 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3610129 | DISTRICT 13 - SAN BERNARDINO | C | O - WHOLESALER (SELLS WATER)
CA3610130 | DISTRICT 13 - SAN BERNARDINO | NTNC | T - HIGHWAY REST AREA
CA3610131 | DISTRICT 13 - SAN BERNARDINO | NC | T - HIGHWAY REST AREA
CA3610300 | DISTRICT 13 - SAN BERNARDINO | NC | T - RECREATION AREA
CA3610301 | DISTRICT 13 - SAN BERNARDINO | NC | T - OTHER TRANSIENT AREA
CA3610701 | DISTRICT 13 - SAN BERNARDINO | C | R - OTHER RESIDENTIAL AREA
CA3610702 | DISTRICT 13 - SAN BERNARDINO | NTNC | R - OTHER RESIDENTIAL AREA
CA3610703 | DISTRICT 13 - SAN BERNARDINO | C | NT - INSTITUTION
CA3610705 | DISTRICT 13 - SAN BERNARDINO | C | R - OTHER RESIDENTIAL AREA
CA3610708 | DISTRICT 13 - SAN BERNARDINO | NTNC | NT - OTHER NON-TRANSIENT AREA
CA3610800 | DISTRICT 13 - SAN BERNARDINO | C | NT - INSTITUTION
CA3610801 | DISTRICT 13 - SAN BERNARDINO | C | NT - INSTITUTION
CA3610850 | DISTRICT 13 - SAN BERNARDINO | C | NT - INSTITUTION
CA3610851 | DISTRICT 13 - SAN BERNARDINO | C | NT - INSTITUTION
CA3610854 | DISTRICT 13 - SAN BERNARDINO | C | R - RESIDENTIAL AREA
CA3700001 | LPA67 - SAN DIEGO COUNTY | NC | R - MOBILE HOME PARK
CA3700003 | LPA67 - SAN DIEGO COUNTY | NC | NT - INSTITUTION
CA3700005 | LPA67 - SAN DIEGO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3700011 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700013 | LPA67 - SAN DIEGO COUNTY | NC | T - RESTAURANT
CA3700018 | LPA67 - SAN DIEGO COUNTY | NTNC | NT - SCHOOL
CA3700019 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700025 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700029 | LPA67 - SAN DIEGO COUNTY | NC | T - SECONDARY RESIDENCES
CA3700030 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700035 | LPA67 - SAN DIEGO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3700036 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700041 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK
CA3700044 | LPA67 - SAN DIEGO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3700047 | LPA67 - SAN DIEGO COUNTY | NC | T - SERVICE STATION
CA3700049 | LPA67 - SAN DIEGO COUNTY | NC | T - RESTAURANT
CA3700063 | LPA67 - SAN DIEGO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3700065 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700071 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK
CA3700072 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700073 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA
CA3700074 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA
CA3700117 | LPA67 - SAN DIEGO COUNTY | NTNC | NT - SCHOOL
CA3700118 | LPA67 - SAN DIEGO COUNTY | NTNC | NT - SCHOOL
CA3700149 | LPA67 - SAN DIEGO COUNTY | NC | NT - INSTITUTION
CA3700174 | LPA67 - SAN DIEGO COUNTY | NTNC | T - RECREATION AREA
CA3700195 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700235 | LPA67 - SAN DIEGO COUNTY | NC | NT - INSTITUTION
CA3700276 | LPA67 - SAN DIEGO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3700277 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA
CA3700291 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK
CA3700422 | LPA67 - SAN DIEGO COUNTY | C | T - SECONDARY RESIDENCES
CA3700782 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700846 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700847 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700855 | LPA67 - SAN DIEGO COUNTY | SSWS | R - MOBILE HOME PARK
CA3700857 | LPA67 - SAN DIEGO COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA3700858 | LPA67 - SAN DIEGO COUNTY | NC | R - MOBILE HOME PARK
CA3700859 | LPA67 - SAN DIEGO COUNTY | C | T - SECONDARY RESIDENCES
CA3700866 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA
CA3700873 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700875 | LPA67 - SAN DIEGO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3700880 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700895 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700897 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA
CA3700899 | LPA67 - SAN DIEGO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3700900 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA
CA3700903 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700905 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA
CA3700906 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700909 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA
CA3700911 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700912 | LPA67 - SAN DIEGO COUNTY | NTNC | T - RECREATION AREA
CA3700913 | LPA67 - SAN DIEGO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3700918 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA
CA3700919 | DISTRICT 14 - SAN DIEGO | C | R - MOBILE HOME PARK
CA3700922 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK
CA3700923 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA
CA3700924 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA
CA3700926 | LPA67 - SAN DIEGO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3700930 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700931 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3700933 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA
CA3700934 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA
CA3700936 | LPA67 - SAN DIEGO COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3700937 | LPA67 - SAN DIEGO COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3700938 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA
CA3700953 | LPA67 - SAN DIEGO COUNTY | NTNC | T - SECONDARY RESIDENCES
CA3700958 | LPA67 - SAN DIEGO COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3700959 | LPA67 - SAN DIEGO COUNTY | NTNC | T - HOTEL/MOTEL
CA3700962 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK
CA3700963 | LPA67 - SAN DIEGO COUNTY | NTNC | NT - SCHOOL
CA3700968 | LPA67 - SAN DIEGO COUNTY | C | T - SECONDARY RESIDENCES
CA3700970 | LPA67 - SAN DIEGO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3701005 | LPA67 - SAN DIEGO COUNTY | NTNC | NT - SCHOOL
CA3701010 | LPA67 - SAN DIEGO COUNTY | NTNC | NT - SCHOOL
CA3701021 | DISTRICT 14 - SAN DIEGO | NC | T - HIGHWAY REST AREA
CA3701070 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3701127 | LPA67 - SAN DIEGO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3701184 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK
CA3701217 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3701218 | LPA67 - SAN DIEGO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3701240 | LPA67 - SAN DIEGO COUNTY | NC | T - RESTAURANT
CA3701299 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3701341 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK
CA3701380 | LPA67 - SAN DIEGO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3701390 | LPA67 - SAN DIEGO COUNTY | NC | T - HOTEL/MOTEL
CA3701407 | LPA67 - SAN DIEGO COUNTY | NC | T - HOTEL/MOTEL
CA3701408 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3701476 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3701567 | LPA67 - SAN DIEGO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3701568 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3701588 | LPA67 - SAN DIEGO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3701594 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3701694 | LPA67 - SAN DIEGO COUNTY | NC | R - MOBILE HOME PARK
CA3701747 | LPA67 - SAN DIEGO COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3701780 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA
CA3701793 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK
CA3701826 | LPA67 - SAN DIEGO COUNTY | NC | T - RESTAURANT
CA3701837 | LPA67 - SAN DIEGO COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3701843 | LPA67 - SAN DIEGO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3701882 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3701884 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3701895 | LPA67 - SAN DIEGO COUNTY | SSWS | R - MOBILE HOME PARK
CA3701909 | LPA67 - SAN DIEGO COUNTY | NTNC | T - RECREATION AREA
CA3701934 | LPA67 - SAN DIEGO COUNTY | C | T - RECREATION AREA
CA3701961 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK
CA3701965 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3701982 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3701988 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK
CA3701995 | LPA67 - SAN DIEGO COUNTY | C | R - RESIDENTIAL AREA
CA3702059 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3702104 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3702111 | LPA67 - SAN DIEGO COUNTY | NC | T - HOTEL/MOTEL
CA3702135 | LPA67 - SAN DIEGO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3702181 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3702235 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3702236 | LPA67 - SAN DIEGO COUNTY | C | T - SECONDARY RESIDENCES
CA3702237 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3702283 | LPA67 - SAN DIEGO COUNTY | NTNC | R - RESIDENTIAL AREA
CA3702302 | LPA67 - SAN DIEGO COUNTY | NC | T - HOTEL/MOTEL
CA3702319 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3702338 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3702354 | DISTRICT 14 - SAN DIEGO | C | R - MOBILE HOME PARK
CA3702364 | LPA67 - SAN DIEGO COUNTY | NTNC | NT - SCHOOL
CA3702420 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3702459 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3702509 | LPA67 - SAN DIEGO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3702530 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3702686 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3702703 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3702706 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3702754 | LPA67 - SAN DIEGO COUNTY | C | R - MOBILE HOME PARK
CA3702757 | LPA67 - SAN DIEGO COUNTY | NC | T - RESTAURANT
CA3705046 | LPA67 - SAN DIEGO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3705050 | LPA67 - SAN DIEGO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3705051 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3705056 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3705057 | LPA67 - SAN DIEGO COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA3705058 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3705059 | LPA67 - SAN DIEGO COUNTY | NC | NT - INSTITUTION
CA3705060 | LPA67 - SAN DIEGO COUNTY | NC | T - SERVICE STATION
CA3705061 | LPA67 - SAN DIEGO COUNTY | NC | T - OTHER TRANSIENT AREA
CA3705063 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3705064 | LPA67 - SAN DIEGO COUNTY | SSWS | O - OTHER AREA
CA3705065 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3705066 | LPA67 - SAN DIEGO COUNTY | SSWS | R - RESIDENTIAL AREA
CA3705068 | LPA67 - SAN DIEGO COUNTY | NC | O - OTHER AREA
CA3705070 | LPA67 - SAN DIEGO COUNTY | NC | T - RESTAURANT
CA3705071 | LPA67 - SAN DIEGO COUNTY | NC | T - RESTAURANT
CA3705072 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3705073 | LPA67 - SAN DIEGO COUNTY | NTNC | NT - MEDICAL FACILITY
CA3705074 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3705075 | LPA67 - SAN DIEGO COUNTY | NC | T - RECREATION AREA
CA3705076 | LPA67 - SAN DIEGO COUNTY | NC | R - RESIDENTIAL AREA
CA3710001 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA
CA3710002 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710004 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710005 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710006 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710008 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710009 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710010 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710011 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710012 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710013 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710014 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3710015 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA
CA3710016 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710018 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710019 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710020 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA
CA3710021 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710023 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710025 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710026 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710027 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710029 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710034 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710036 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710037 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710039 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710041 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710042 | DISTRICT 14 - SAN DIEGO | C | O - WHOLESALER (SELLS WATER)
CA3710044 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710045 | DISTRICT 14 - SAN DIEGO | C | O - WHOLESALER (SELLS WATER)
CA3710047 | DISTRICT 14 - SAN DIEGO | C | R - RESIDENTIAL AREA
CA3710048 | DISTRICT 14 - SAN DIEGO | NTNC | T - OTHER TRANSIENT AREA
CA3710049 | DISTRICT 14 - SAN DIEGO | NTNC | T - SERVICE STATION
CA3710050 | DISTRICT 14 - SAN DIEGO | NC | T - OTHER TRANSIENT AREA
CA3710051 | DISTRICT 14 - SAN DIEGO | NTNC | NT - OTHER NON-TRANSIENT AREA
CA3710052 | DISTRICT 14 - SAN DIEGO | NTNC | NT - OTHER NON-TRANSIENT AREA
CA3710053 | DISTRICT 14 - SAN DIEGO | NTNC | NT - OTHER NON-TRANSIENT AREA
CA3710301 | DISTRICT 14 - SAN DIEGO | NC | T - RECREATION AREA
CA3710302 | DISTRICT 14 - SAN DIEGO | NC | T - RECREATION AREA
CA3710305 | DISTRICT 14 - SAN DIEGO | NC | T - RECREATION AREA
CA3710306 | DISTRICT 14 - SAN DIEGO | NC | T - RECREATION AREA
CA3710311 | DISTRICT 14 - SAN DIEGO | NC | T - RECREATION AREA
CA3710312 | DISTRICT 14 - SAN DIEGO | NC | T - RECREATION AREA
CA3710316 | DISTRICT 14 - SAN DIEGO | NC | NT - SCHOOL
CA3710317 | DISTRICT 14 - SAN DIEGO | NC | T - RECREATION AREA
CA3710318 | DISTRICT 14 - SAN DIEGO | NC | T - RECREATION AREA
CA3710319 | DISTRICT 14 - SAN DIEGO | NC | T - RECREATION AREA
CA3710320 | DISTRICT 14 - SAN DIEGO | NC | T - RECREATION AREA
CA3710700 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3710702 | DISTRICT 08 - SANTA ANA | C | R - RESIDENTIAL AREA
CA3710706 | DISTRICT 14 - SAN DIEGO | NC | O - OTHER AREA
CA3710707 | DISTRICT 14 - SAN DIEGO | C | R - OTHER RESIDENTIAL AREA
CA3710708 | DISTRICT 14 - SAN DIEGO | NC | T - OTHER TRANSIENT AREA
CA3710750 | DISTRICT 14 - SAN DIEGO | C | O - OTHER AREA
CA3710800 | DISTRICT 14 - SAN DIEGO | C | NT - INSTITUTION
CA3710802 | DISTRICT 14 - SAN DIEGO | C | NT - INSTITUTION
CA3810001 | DISTRICT 04 - SAN FRANCISCO | C | O - WHOLESALER (SELLS WATER)
CA3810003 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA3810005 | DISTRICT 04 - SAN FRANCISCO | NC | O - OTHER AREA
CA3810006 | DISTRICT 04 - SAN FRANCISCO | NC | O - OTHER AREA
CA3810008 | DISTRICT 04 - SAN FRANCISCO | C | O - WHOLESALER (SELLS WATER)
CA3810010 | DISTRICT 04 - SAN FRANCISCO | NTNC | O - OTHER AREA
CA3810011 | DISTRICT 04 - SAN FRANCISCO | C | R - MUNICIPALITY
CA3810700 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA3810702 | DISTRICT 04 - SAN FRANCISCO | C | NT - INSTITUTION
CA3900504 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900505 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900511 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3900512 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900517 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900523 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900543 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900558 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900559 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900561 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900563 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900568 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900569 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900578 | LPA69 - SAN JOAQUIN COUNTY | NC | T - HOTEL/MOTEL
CA3900579 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900581 | LPA69 - SAN JOAQUIN COUNTY | NTNC | R - RESIDENTIAL AREA
CA3900583 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RECREATION AREA
CA3900585 | LPA69 - SAN JOAQUIN COUNTY | NC | T - HOTEL/MOTEL
CA3900586 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900592 | LPA69 - SAN JOAQUIN COUNTY | NC | T - HOTEL/MOTEL
CA3900593 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3900596 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900598 | LPA69 - SAN JOAQUIN COUNTY | NC | T - HOTEL/MOTEL
CA3900602 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900606 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900607 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900616 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RECREATION AREA
CA3900624 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900637 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900648 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RECREATION AREA
CA3900649 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900653 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900661 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900664 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900666 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RECREATION AREA
CA3900682 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900701 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900702 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900705 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900709 | LPA69 - SAN JOAQUIN COUNTY | NC | T - HOTEL/MOTEL
CA3900714 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900719 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900720 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900721 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900722 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900724 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900732 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900733 | LPA69 - SAN JOAQUIN COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3900742 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3900748 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3900752 | LPA69 - SAN JOAQUIN COUNTY | NC | R - OTHER RESIDENTIAL AREA
CA3900755 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900756 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3900757 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3900759 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RECREATION AREA
CA3900762 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900768 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RECREATION AREA
CA3900779 | LPA69 - SAN JOAQUIN COUNTY | NC | NT - INSTITUTION
CA3900796 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3900797 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3900798 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3900799 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3900805 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900813 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900814 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RECREATION AREA
CA3900815 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3900825 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3900831 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900835 | LPA69 - SAN JOAQUIN COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3900837 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900840 | LPA69 - SAN JOAQUIN COUNTY | NC | T - SERVICE STATION
CA3900842 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900844 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900846 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3900848 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3900849 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3900850 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3900903 | LPA69 - SAN JOAQUIN COUNTY | NC | T - SERVICE STATION
CA3900907 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900921 | LPA69 - SAN JOAQUIN COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3900927 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3900962 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3900964 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900965 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3900974 | LPA69 - SAN JOAQUIN COUNTY | NC | T - HOTEL/MOTEL
CA3900978 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3900983 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3900991 | LPA69 - SAN JOAQUIN COUNTY | C | T - OTHER TRANSIENT AREA
CA3900993 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3900998 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901006 | LPA69 - SAN JOAQUIN COUNTY | NC | T - SERVICE STATION
CA3901010 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RECREATION AREA
CA3901011 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901014 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3901015 | LPA69 - SAN JOAQUIN COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3901031 | LPA69 - SAN JOAQUIN COUNTY | C | T - RESTAURANT
CA3901032 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3901041 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901046 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901074 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3901075 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3901080 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901081 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3901082 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - MEDICAL FACILITY
CA3901085 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3901086 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901090 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3901092 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3901106 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RECREATION AREA
CA3901107 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3901108 | LPA69 - SAN JOAQUIN COUNTY | NC | T - SERVICE STATION
CA3901113 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3901114 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3901116 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901120 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901123 | LPA69 - SAN JOAQUIN COUNTY | NC | T - SERVICE STATION
CA3901124 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901131 | LPA69 - SAN JOAQUIN COUNTY | NC | T - OTHER TRANSIENT AREA
CA3901159 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3901163 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3901164 | LPA69 - SAN JOAQUIN COUNTY | NC | T - SERVICE STATION
CA3901167 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3901169 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3901172 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3901176 | LPA69 - SAN JOAQUIN COUNTY | NTNC | T - RESTAURANT
CA3901179 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901181 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901182 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901194 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901197 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901205 | LPA69 - SAN JOAQUIN COUNTY | NC | T - OTHER TRANSIENT AREA
CA3901209 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3901213 | LPA69 - SAN JOAQUIN COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3901215 | LPA69 - SAN JOAQUIN COUNTY | C | R - MOBILE HOME PARK
CA3901216 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3901217 | LPA69 - SAN JOAQUIN COUNTY | C | NT - INSTITUTION
CA3901229 | LPA69 - SAN JOAQUIN COUNTY | NC | T - OTHER TRANSIENT AREA
CA3901231 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RECREATION AREA
CA3901238 | LPA69 - SAN JOAQUIN COUNTY | NC | T - OTHER TRANSIENT AREA
CA3901242 | LPA69 - SAN JOAQUIN COUNTY | NC | T - OTHER TRANSIENT AREA
CA3901245 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901248 | LPA69 - SAN JOAQUIN COUNTY | NTNC | T - SERVICE STATION
CA3901252 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901253 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901258 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901276 | LPA69 - SAN JOAQUIN COUNTY | C | R - OTHER RESIDENTIAL AREA
CA3901278 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901280 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RECREATION AREA
CA3901282 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901283 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901284 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RECREATION AREA
CA3901285 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901290 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901296 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901299 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901301 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901303 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3901304 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3901305 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901306 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901308 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901309 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901310 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901312 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901315 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901318 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901319 | LPA69 - SAN JOAQUIN COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA3901320 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901322 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901323 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901325 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3901328 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901329 | LPA69 - SAN JOAQUIN COUNTY | NC | T - OTHER TRANSIENT AREA
CA3901331 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3901336 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901337 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3901338 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901341 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901342 | LPA69 - SAN JOAQUIN COUNTY | NC | T - OTHER TRANSIENT AREA
CA3901343 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901344 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901345 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901348 | DISTRICT 10 - STOCKTON | C | O - WHOLESALER (SELLS WATER)
CA3901350 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901354 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901360 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901365 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901368 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901369 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901370 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901371 | LPA69 - SAN JOAQUIN COUNTY | NC | T - OTHER TRANSIENT AREA
CA3901373 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - DAY CARE CENTER
CA3901377 | LPA69 - SAN JOAQUIN COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA3901378 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901382 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901387 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901388 | LPA69 - SAN JOAQUIN COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3901390 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901391 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RECREATION AREA
CA3901392 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901393 | LPA69 - SAN JOAQUIN COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3901394 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901397 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901399 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901400 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901401 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901402 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901403 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901404 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901405 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901406 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901407 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901409 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901410 | LPA69 - SAN JOAQUIN COUNTY | NC | T - OTHER TRANSIENT AREA
CA3901411 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901412 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901414 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901416 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901417 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901418 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901421 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901422 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901423 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901424 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901425 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901426 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901428 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901429 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901430 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901432 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901433 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901435 | LPA69 - SAN JOAQUIN COUNTY | NC | T - SERVICE STATION
CA3901438 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901439 | LPA69 - SAN JOAQUIN COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3901441 | LPA69 - SAN JOAQUIN COUNTY | NC | T - OTHER TRANSIENT AREA
CA3901442 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901443 | LPA69 - SAN JOAQUIN COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3901445 | LPA69 - SAN JOAQUIN COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3901447 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901449 | LPA69 - SAN JOAQUIN COUNTY | NC | T - OTHER TRANSIENT AREA
CA3901450 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901452 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901456 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901457 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901459 | LPA69 - SAN JOAQUIN COUNTY | NC | T - OTHER TRANSIENT AREA
CA3901461 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901462 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901463 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901464 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901466 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901467 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3901469 | LPA69 - SAN JOAQUIN COUNTY | NC | NT - INSTITUTION
CA3901470 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901471 | LPA69 - SAN JOAQUIN COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3901472 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RECREATION AREA
CA3901473 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901474 | LPA69 - SAN JOAQUIN COUNTY | C | R - RESIDENTIAL AREA
CA3901477 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901478 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3901480 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - INTERSTATE CARRIER
CA3901481 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3901482 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RECREATION AREA
CA3901484 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3901485 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RECREATION AREA
CA3901486 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INSTITUTION
CA3901487 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3902109 | LPA69 - SAN JOAQUIN COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3902136 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - SCHOOL
CA3902172 | LPA69 - SAN JOAQUIN COUNTY | NTNC | O - OTHER AREA
CA3902180 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3902181 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3902182 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3902183 | LPA69 - SAN JOAQUIN COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3902184 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3902187 | LPA69 - SAN JOAQUIN COUNTY | NC | O - OTHER AREA
CA3902189 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3902190 | LPA69 - SAN JOAQUIN COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA3902191 | LPA69 - SAN JOAQUIN COUNTY | NC | NT - INSTITUTION
CA3902193 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3902194 | LPA69 - SAN JOAQUIN COUNTY | NC | T - OTHER TRANSIENT AREA
CA3902206 | LPA69 - SAN JOAQUIN COUNTY | NC | T - OTHER TRANSIENT AREA
CA3902207 | LPA69 - SAN JOAQUIN COUNTY | NC | T - OTHER TRANSIENT AREA
CA3902210 | LPA69 - SAN JOAQUIN COUNTY | NC | T - RESTAURANT
CA3902212 | LPA69 - SAN JOAQUIN COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA3910001 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910002 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910003 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910004 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910005 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910006 | DISTRICT 10 - STOCKTON | C | O - WHOLESALER (SELLS WATER)
CA3910007 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910008 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910009 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910010 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910011 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910012 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910014 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910015 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910017 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910018 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910019 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910020 | DISTRICT 10 - STOCKTON | C | R - MOBILE HOME PARK
CA3910022 | DISTRICT 10 - STOCKTON | C | O - WHOLESALER (SELLS WATER)
CA3910022 | DISTRICT 10 - STOCKTON | C | O - WHOLESALER (SELLS WATER)
CA3910023 | DISTRICT 10 - STOCKTON | C | O - WHOLESALER (SELLS WATER)
CA3910024 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910025 | DISTRICT 10 - STOCKTON | NTNC | O - OTHER AREA
CA3910027 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA3910300 | DISTRICT 10 - STOCKTON | NC | T - RECREATION AREA
CA3910301 | DISTRICT 10 - STOCKTON | NC | T - RECREATION AREA
CA3910302 | DISTRICT 10 - STOCKTON | NC | T - RECREATION AREA
CA3910701 | DISTRICT 10 - STOCKTON | C | R - OTHER RESIDENTIAL AREA
CA3910702 | DISTRICT 10 - STOCKTON | NTNC | T - OTHER TRANSIENT AREA
CA3910800 | DISTRICT 10 - STOCKTON | C | NT - INSTITUTION
CA3910803 | DISTRICT 10 - STOCKTON | C | NT - INSTITUTION
CA4000200 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000202 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000203 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000205 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - SCHOOL
CA4000206 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - SCHOOL
CA4000208 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000209 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000210 | LPA70 - SAN LUIS OBISPO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4000211 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000213 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000214 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000216 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000219 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RECREATION AREA
CA4000221 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000222 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4000223 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000224 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000225 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000226 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | R - MOBILE HOME PARK
CA4000230 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000501 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000502 | LPA70 - SAN LUIS OBISPO COUNTY | SSWS | R - RESIDENTIAL AREA
CA4000503 | LPA70 - SAN LUIS OBISPO COUNTY | SSWS | R - RESIDENTIAL AREA
CA4000504 | LPA70 - SAN LUIS OBISPO COUNTY | SSWS | R - RESIDENTIAL AREA
CA4000505 | LPA70 - SAN LUIS OBISPO COUNTY | SSWS | R - RESIDENTIAL AREA
CA4000506 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000507 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000523 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000554 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000555 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000563 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000568 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4000587 | LPA70 - SAN LUIS OBISPO COUNTY | SSWS | R - RESIDENTIAL AREA
CA4000589 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000590 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | T - RECREATION AREA
CA4000598 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000604 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000620 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000623 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000629 | LPA70 - SAN LUIS OBISPO COUNTY | SSWS | R - RESIDENTIAL AREA
CA4000631 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000632 | LPA70 - SAN LUIS OBISPO COUNTY | SSWS | R - MOBILE HOME PARK
CA4000635 | LPA70 - SAN LUIS OBISPO COUNTY | SSWS | R - RESIDENTIAL AREA
CA4000637 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000639 | LPA70 - SAN LUIS OBISPO COUNTY | SSWS | R - RESIDENTIAL AREA
CA4000640 | LPA70 - SAN LUIS OBISPO COUNTY | NC | R - RESIDENTIAL AREA
CA4000642 | LPA70 - SAN LUIS OBISPO COUNTY | NC | R - RESIDENTIAL AREA
CA4000644 | LPA70 - SAN LUIS OBISPO COUNTY | NC | R - MOBILE HOME PARK
CA4000648 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - MOBILE HOME PARK
CA4000649 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - MOBILE HOME PARK
CA4000650 | DISTRICT 06 - SANTA BARBARA | C | R - OTHER RESIDENTIAL AREA
CA4000652 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RECREATION AREA
CA4000653 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - MOBILE HOME PARK
CA4000654 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - MOBILE HOME PARK
CA4000655 | LPA70 - SAN LUIS OBISPO COUNTY | NC | R - MOBILE HOME PARK
CA4000656 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RECREATION AREA
CA4000658 | LPA70 - SAN LUIS OBISPO COUNTY | SSWS | R - RESIDENTIAL AREA
CA4000659 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RECREATION AREA
CA4000660 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000664 | LPA70 - SAN LUIS OBISPO COUNTY | NC | R - RESIDENTIAL AREA
CA4000670 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000671 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | T - RECREATION AREA
CA4000673 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RESTAURANT
CA4000675 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - SCHOOL
CA4000678 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000684 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | T - HOTEL/MOTEL
CA4000689 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | T - HOTEL/MOTEL
CA4000692 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000693 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - SCHOOL
CA4000698 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RESTAURANT
CA4000699 | LPA70 - SAN LUIS OBISPO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4000700 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - SUMMER CAMP
CA4000701 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RECREATION AREA
CA4000702 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RECREATION AREA
CA4000705 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000707 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RESTAURANT
CA4000708 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RESTAURANT
CA4000714 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RECREATION AREA
CA4000716 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000722 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000725 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000730 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000732 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - SCHOOL
CA4000733 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RECREATION AREA
CA4000734 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000741 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000744 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000747 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RESTAURANT
CA4000749 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000750 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000752 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000753 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000757 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RECREATION AREA
CA4000765 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000766 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000767 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - SCHOOL
CA4000768 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000770 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000771 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000772 | LPA70 - SAN LUIS OBISPO COUNTY | SSWS | R - RESIDENTIAL AREA
CA4000774 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - SCHOOL
CA4000775 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000777 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000778 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000780 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | T - HOTEL/MOTEL
CA4000781 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000784 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000788 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RECREATION AREA
CA4000789 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000790 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RECREATION AREA
CA4000800 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | T - RESTAURANT
CA4000802 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000803 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000805 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000806 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000808 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000809 | LPA70 - SAN LUIS OBISPO COUNTY | NC | O - OTHER AREA
CA4000815 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000816 | LPA70 - SAN LUIS OBISPO COUNTY | SSWS | R - RESIDENTIAL AREA
CA4000817 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000818 | LPA70 - SAN LUIS OBISPO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4000819 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4000822 | LPA70 - SAN LUIS OBISPO COUNTY | SSWS | R - RESIDENTIAL AREA
CA4000823 | LPA70 - SAN LUIS OBISPO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4000824 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - OTHER TRANSIENT AREA
CA4000825 | LPA70 - SAN LUIS OBISPO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4000829 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RECREATION AREA
CA4000830 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - RECREATION AREA
CA4000831 | LPA70 - SAN LUIS OBISPO COUNTY | NC | O - OTHER AREA
CA4000832 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - OTHER TRANSIENT AREA
CA4000834 | LPA70 - SAN LUIS OBISPO COUNTY | C | R - RESIDENTIAL AREA
CA4000837 | LPA70 - SAN LUIS OBISPO COUNTY | NTNC | NT - DAY CARE CENTER
CA4000838 | LPA70 - SAN LUIS OBISPO COUNTY | NC | T - OTHER TRANSIENT AREA
CA4000841 | LPA70 - SAN LUIS OBISPO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4010001 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010002 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010003 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010004 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010005 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010006 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010007 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010008 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010009 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010010 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010011 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010012 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010014 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010014 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010015 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010016 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010017 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010018 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010019 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010022 | DISTRICT 06 - SANTA BARBARA | C | O - WHOLESALER (SELLS WATER)
CA4010023 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010024 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010025 | DISTRICT 06 - SANTA BARBARA | C | O - WHOLESALER (SELLS WATER)
CA4010026 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010027 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010028 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010040 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010080 | DISTRICT 06 - SANTA BARBARA | C | O - WHOLESALER (SELLS WATER)
CA4010081 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4010300 | DISTRICT 06 - SANTA BARBARA | NTNC | T - OTHER TRANSIENT AREA
CA4010301 | DISTRICT 06 - SANTA BARBARA | NC | T - OTHER TRANSIENT AREA
CA4010305 | DISTRICT 06 - SANTA BARBARA | NC | T - OTHER TRANSIENT AREA
CA4010830 | DISTRICT 06 - SANTA BARBARA | C | NT - INSTITUTION
CA4010832 | DISTRICT 06 - SANTA BARBARA | C | NT - INSTITUTION
CA4010900 | DISTRICT 06 - SANTA BARBARA | NC | T - HIGHWAY REST AREA
CA4010901 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4100502 | DISTRICT 17 - SANTA CLARA | NC | T - SUMMER CAMP
CA4100503 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4100509 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4100510 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4100512 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4100513 | DISTRICT 17 - SANTA CLARA | NTNC | NT - SCHOOL
CA4100515 | DISTRICT 17 - SANTA CLARA | NC | R - OTHER RESIDENTIAL AREA
CA4100522 | DISTRICT 17 - SANTA CLARA | C | T - SUMMER CAMP
CA4100523 | DISTRICT 17 - SANTA CLARA | NC | T - SUMMER CAMP
CA4100527 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4100529 | DISTRICT 17 - SANTA CLARA | C | T - SUMMER CAMP
CA4100533 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4100536 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4100538 | DISTRICT 17 - SANTA CLARA | C | T - RECREATION AREA
CA4100539 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4100540 | DISTRICT 17 - SANTA CLARA | C | NT - INDUSTRIAL/AGRICULTURAL
CA4100551 | DISTRICT 17 - SANTA CLARA | C | NT - INDUSTRIAL/AGRICULTURAL
CA4100552 | DISTRICT 17 - SANTA CLARA | NC | T - SUMMER CAMP
CA4100553 | DISTRICT 17 - SANTA CLARA | NC | T - HOTEL/MOTEL
CA4100555 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4100559 | DISTRICT 17 - SANTA CLARA | NC | T - OTHER TRANSIENT AREA
CA4100560 | DISTRICT 17 - SANTA CLARA | NC | T - RESTAURANT
CA4100566 | DISTRICT 17 - SANTA CLARA | NC | T - RESTAURANT
CA4100575 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4100582 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4100583 | DISTRICT 17 - SANTA CLARA | C | NT - INDUSTRIAL/AGRICULTURAL
CA4100603 | DISTRICT 17 - SANTA CLARA | NTNC | T - RECREATION AREA
CA4100605 | DISTRICT 17 - SANTA CLARA | NTNC | NT - INSTITUTION
CA4100607 | DISTRICT 17 - SANTA CLARA | NC | T - OTHER TRANSIENT AREA
CA4110001 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110002 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110003 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110005 | DISTRICT 17 - SANTA CLARA | C | NT - INDUSTRIAL/AGRICULTURAL
CA4110006 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110007 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110008 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110009 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110010 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110011 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110012 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110013 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110016 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110017 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110018 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110019 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110020 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110021 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110022 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110023 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110024 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110025 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110027 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4110029 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4200505 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200511 | LPA72 - SANTA BARBARA COUNTY | SSWS | R - RESIDENTIAL AREA
CA4200514 | LPA72 - SANTA BARBARA COUNTY | NC | R - RESIDENTIAL AREA
CA4200531 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200539 | LPA72 - SANTA BARBARA COUNTY | NC | T - RECREATION AREA
CA4200543 | LPA72 - SANTA BARBARA COUNTY | NC | R - RESIDENTIAL AREA
CA4200556 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200560 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200562 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200572 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200577 | LPA72 - SANTA BARBARA COUNTY | NC | T - RESTAURANT
CA4200578 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200579 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200580 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200612 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200616 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200618 | LPA72 - SANTA BARBARA COUNTY | C | NT - SCHOOL
CA4200619 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200626 | LPA72 - SANTA BARBARA COUNTY | NC | R - RESIDENTIAL AREA
CA4200630 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INSTITUTION
CA4200631 | LPA72 - SANTA BARBARA COUNTY | NC | R - RESIDENTIAL AREA
CA4200633 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200634 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200639 | LPA72 - SANTA BARBARA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA4200644 | LPA72 - SANTA BARBARA COUNTY | NC | T - SUMMER CAMP
CA4200666 | LPA72 - SANTA BARBARA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA4200678 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200684 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200691 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200693 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200702 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200703 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200714 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200717 | LPA72 - SANTA BARBARA COUNTY | NC | T - HOTEL/MOTEL
CA4200718 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200721 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200725 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200731 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200733 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200741 | LPA72 - SANTA BARBARA COUNTY | NC | T - HOTEL/MOTEL
CA4200743 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200747 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - SCHOOL
CA4200800 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200802 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200804 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200807 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200814 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200818 | LPA72 - SANTA BARBARA COUNTY | NC | T - SUMMER CAMP
CA4200822 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200824 | LPA72 - SANTA BARBARA COUNTY | NC | T - RECREATION AREA
CA4200826 | LPA72 - SANTA BARBARA COUNTY | NC | T - SUMMER CAMP
CA4200827 | LPA72 - SANTA BARBARA COUNTY | C | R - MOBILE HOME PARK
CA4200830 | LPA72 - SANTA BARBARA COUNTY | NC | T - RECREATION AREA
CA4200832 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200833 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - SCHOOL
CA4200837 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200842 | LPA72 - SANTA BARBARA COUNTY | C | R - MOBILE HOME PARK
CA4200846 | LPA72 - SANTA BARBARA COUNTY | NC | T - RECREATION AREA
CA4200848 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200851 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200854 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200856 | LPA72 - SANTA BARBARA COUNTY | NC | T - RESTAURANT
CA4200862 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200865 | LPA72 - SANTA BARBARA COUNTY | NC | T - RECREATION AREA
CA4200866 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200867 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200870 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200872 | LPA72 - SANTA BARBARA COUNTY | NC | T - RESTAURANT
CA4200876 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200877 | LPA72 - SANTA BARBARA COUNTY | NC | T - SERVICE STATION
CA4200879 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - SCHOOL
CA4200881 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200882 | LPA72 - SANTA BARBARA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4200885 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200886 | LPA72 - SANTA BARBARA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4200891 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200894 | LPA72 - SANTA BARBARA COUNTY | SSWS | NT - INDUSTRIAL/AGRICULTURAL
CA4200895 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200897 | LPA72 - SANTA BARBARA COUNTY | SSWS | NT - INDUSTRIAL/AGRICULTURAL
CA4200902 | LPA72 - SANTA BARBARA COUNTY | NC | T - RECREATION AREA
CA4200904 | LPA72 - SANTA BARBARA COUNTY | SSWS | NT - INDUSTRIAL/AGRICULTURAL
CA4200905 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200907 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200911 | LPA72 - SANTA BARBARA COUNTY | NC | T - RECREATION AREA
CA4200915 | LPA72 - SANTA BARBARA COUNTY | NC | NT - INSTITUTION
CA4200918 | LPA72 - SANTA BARBARA COUNTY | C | R - RESIDENTIAL AREA
CA4200919 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200924 | LPA72 - SANTA BARBARA COUNTY | C | NT - INDUSTRIAL/AGRICULTURAL
CA4200925 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200927 | LPA72 - SANTA BARBARA COUNTY | SSWS | R - RESIDENTIAL AREA
CA4200928 | LPA72 - SANTA BARBARA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4200929 | LPA72 - SANTA BARBARA COUNTY | SSWS | R - RESIDENTIAL AREA
CA4200930 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200931 | LPA72 - SANTA BARBARA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4200933 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200934 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200936 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200938 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200939 | LPA72 - SANTA BARBARA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4200941 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200942 | LPA72 - SANTA BARBARA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4200943 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200944 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200946 | LPA72 - SANTA BARBARA COUNTY | SSWS | R - RESIDENTIAL AREA
CA4200947 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200948 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200949 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200950 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200951 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200952 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200957 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200960 | LPA72 - SANTA BARBARA COUNTY | NC | T - RECREATION AREA
CA4200961 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200962 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200963 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200964 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200965 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200967 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200968 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200969 | LPA72 - SANTA BARBARA COUNTY | C | NT - OTHER NON-TRANSIENT AREA
CA4200970 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200971 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200972 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200973 | LPA72 - SANTA BARBARA COUNTY | NC | O - OTHER AREA
CA4200974 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200976 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200977 | LPA72 - SANTA BARBARA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4200978 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4200979 | LPA72 - SANTA BARBARA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4210001 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210002 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210003 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210004 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210005 | DISTRICT 06 - SANTA BARBARA | C | R - MOBILE HOME PARK
CA4210006 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210007 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210009 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210010 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210011 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210013 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210016 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210017 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210018 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210019 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210020 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210021 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210022 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210024 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA4210028 | DISTRICT 06 - SANTA BARBARA | C | O - WHOLESALER (SELLS WATER)
CA4210030 | DISTRICT 06 - SANTA BARBARA | C | O - WHOLESALER (SELLS WATER)
CA4210303 | DISTRICT 06 - SANTA BARBARA | NC | T - RECREATION AREA
CA4210304 | DISTRICT 06 - SANTA BARBARA | NC | T - RECREATION AREA
CA4210305 | DISTRICT 06 - SANTA BARBARA | NC | T - SECONDARY RESIDENCES
CA4210700 | DISTRICT 06 - SANTA BARBARA | C | NT - INSTITUTION
CA4210900 | DISTRICT 06 - SANTA BARBARA | NC | T - HIGHWAY REST AREA
CA4300516 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300517 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300520 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300521 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300522 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300525 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300526 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300542 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300543 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300545 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300546 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300550 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300551 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300560 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300562 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300563 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300567 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300571 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300573 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300575 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300577 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300578 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300581 | DISTRICT 17 - SANTA CLARA | C | R - MOBILE HOME PARK
CA4300593 | DISTRICT 17 - SANTA CLARA | NTNC | NT - SCHOOL
CA4300596 | DISTRICT 17 - SANTA CLARA | NTNC | T - RECREATION AREA
CA4300602 | DISTRICT 17 - SANTA CLARA | NC | T - HOTEL/MOTEL
CA4300603 | DISTRICT 17 - SANTA CLARA | C | R - MOBILE HOME PARK
CA4300605 | DISTRICT 17 - SANTA CLARA | NTNC | NT - SCHOOL
CA4300608 | DISTRICT 17 - SANTA CLARA | NTNC | NT - SCHOOL
CA4300610 | DISTRICT 17 - SANTA CLARA | NTNC | NT - SCHOOL
CA4300611 | DISTRICT 17 - SANTA CLARA | C | R - MOBILE HOME PARK
CA4300612 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4300614 | DISTRICT 17 - SANTA CLARA | NC | T - SUMMER CAMP
CA4300615 | DISTRICT 17 - SANTA CLARA | C | T - RECREATION AREA
CA4300616 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4300630 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300637 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300638 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300716 | DISTRICT 17 - SANTA CLARA | C | T - RECREATION AREA
CA4300721 | DISTRICT 17 - SANTA CLARA | NTNC | NT - SCHOOL
CA4300737 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4300740 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300741 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300748 | DISTRICT 17 - SANTA CLARA | NC | T - RESTAURANT
CA4300760 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300763 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4300764 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4300766 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4300770 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300771 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300779 | DISTRICT 17 - SANTA CLARA | NTNC | NT - SCHOOL
CA4300783 | DISTRICT 17 - SANTA CLARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4300791 | DISTRICT 17 - SANTA CLARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4300792 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300808 | DISTRICT 17 - SANTA CLARA | NTNC | NT - MEDICAL FACILITY
CA4300814 | DISTRICT 17 - SANTA CLARA | NC | T - OTHER TRANSIENT AREA
CA4300815 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4300816 | DISTRICT 17 - SANTA CLARA | NTNC | NT - MEDICAL FACILITY
CA4300831 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300832 | DISTRICT 17 - SANTA CLARA | C | NT - INSTITUTION
CA4300833 | DISTRICT 17 - SANTA CLARA | NTNC | NT - MEDICAL FACILITY
CA4300839 | DISTRICT 17 - SANTA CLARA | NC | T - OTHER TRANSIENT AREA
CA4300851 | DISTRICT 17 - SANTA CLARA | NC | T - OTHER TRANSIENT AREA
CA4300856 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300859 | DISTRICT 17 - SANTA CLARA | NTNC | NT - MEDICAL FACILITY
CA4300909 | DISTRICT 17 - SANTA CLARA | C | NT - INSTITUTION
CA4300912 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300924 | DISTRICT 17 - SANTA CLARA | C | R - MOBILE HOME PARK
CA4300929 | DISTRICT 17 - SANTA CLARA | NTNC | NT - INSTITUTION
CA4300937 | DISTRICT 17 - SANTA CLARA | NC | T - SECONDARY RESIDENCES
CA4300939 | DISTRICT 17 - SANTA CLARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4300941 | DISTRICT 17 - SANTA CLARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4300948 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4300949 | DISTRICT 17 - SANTA CLARA | NC | T - RESTAURANT
CA4300951 | DISTRICT 17 - SANTA CLARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4300957 | DISTRICT 17 - SANTA CLARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4300964 | DISTRICT 17 - SANTA CLARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4300967 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4300971 | DISTRICT 17 - SANTA CLARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4300976 | DISTRICT 17 - SANTA CLARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4300978 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300979 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300983 | DISTRICT 17 - SANTA CLARA | NC | T - HOTEL/MOTEL
CA4300986 | DISTRICT 17 - SANTA CLARA | NTNC | T - RECREATION AREA
CA4300987 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4300988 | DISTRICT 17 - SANTA CLARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4300989 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4300991 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4300992 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300993 | DISTRICT 17 - SANTA CLARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4300994 | DISTRICT 17 - SANTA CLARA | C | R - MOBILE HOME PARK
CA4300996 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4300997 | DISTRICT 17 - SANTA CLARA | C | NT - INSTITUTION
CA4300998 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4300999 | DISTRICT 17 - SANTA CLARA | C | R - MOBILE HOME PARK
CA4301003 | DISTRICT 17 - SANTA CLARA | NC | T - OTHER TRANSIENT AREA
CA4301004 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4301006 | DISTRICT 17 - SANTA CLARA | NC | T - OTHER TRANSIENT AREA
CA4301011 | DISTRICT 17 - SANTA CLARA | NC | T - OTHER TRANSIENT AREA
CA4301013 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4301014 | DISTRICT 17 - SANTA CLARA | NC | T - OTHER TRANSIENT AREA
CA4310001 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4310004 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4310005 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4310006 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4310007 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4310009 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4310011 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4310012 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4310013 | DISTRICT 17 - SANTA CLARA | C | NT - SCHOOL
CA4310014 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4310018 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4310019 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4310020 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4310021 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4310022 | DISTRICT 17 - SANTA CLARA | C | R - RESIDENTIAL AREA
CA4310027 | DISTRICT 17 - SANTA CLARA | C | O - WHOLESALER (SELLS WATER)
CA4310028 | DISTRICT 17 - SANTA CLARA | C | NT - SCHOOL
CA4310300 | DISTRICT 17 - SANTA CLARA | NC | T - RECREATION AREA
CA4400502 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400505 | LPA74 - SANTA CRUZ COUNTY | NC | T - OTHER TRANSIENT AREA
CA4400517 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400526 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400528 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4400530 | LPA74 - SANTA CRUZ COUNTY | NTNC | T - SUMMER CAMP
CA4400543 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4400557 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400558 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400559 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4400560 | LPA74 - SANTA CRUZ COUNTY | NC | T - SUMMER CAMP
CA4400570 | LPA74 - SANTA CRUZ COUNTY | NC | T - RESTAURANT
CA4400571 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4400572 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400582 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400585 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400595 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4400597 | LPA74 - SANTA CRUZ COUNTY | NC | T - OTHER TRANSIENT AREA
CA4400598 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400599 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400604 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4400605 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400608 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4400611 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400613 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400617 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400618 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400619 | LPA74 - SANTA CRUZ COUNTY | NC | T - SECONDARY RESIDENCES
CA4400621 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4400624 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400625 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400631 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4400642 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4400645 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400652 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400660 | LPA74 - SANTA CRUZ COUNTY | C | NT - INDUSTRIAL/AGRICULTURAL
CA4400662 | LPA74 - SANTA CRUZ COUNTY | NC | T - RESTAURANT
CA4400664 | LPA74 - SANTA CRUZ COUNTY | C | NT - INDUSTRIAL/AGRICULTURAL
CA4400665 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400668 | LPA74 - SANTA CRUZ COUNTY | NC | R - RESIDENTIAL AREA
CA4400684 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400692 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400701 | DISTRICT 05 - MONTEREY | NC | T - SUMMER CAMP
CA4400704 | LPA74 - SANTA CRUZ COUNTY | NC | T - SUMMER CAMP
CA4400705 | LPA74 - SANTA CRUZ COUNTY | NC | T - SUMMER CAMP
CA4400709 | LPA74 - SANTA CRUZ COUNTY | NC | T - SUMMER CAMP
CA4400710 | LPA74 - SANTA CRUZ COUNTY | NC | T - SUMMER CAMP
CA4400711 | LPA74 - SANTA CRUZ COUNTY | NC | T - SUMMER CAMP
CA4400715 | DISTRICT 05 - MONTEREY | NC | T - SUMMER CAMP
CA4400717 | LPA74 - SANTA CRUZ COUNTY | NC | T - SUMMER CAMP
CA4400723 | LPA74 - SANTA CRUZ COUNTY | C | R - RESIDENTIAL AREA
CA4400725 | DISTRICT 05 - MONTEREY | NTNC | T - OTHER TRANSIENT AREA
CA4400726 | LPA74 - SANTA CRUZ COUNTY | NC | T - SUMMER CAMP
CA4400750 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - SCHOOL
CA4400751 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - SCHOOL
CA4400753 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - SCHOOL
CA4400754 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - SCHOOL
CA4400755 | LPA74 - SANTA CRUZ COUNTY | C | NT - SCHOOL
CA4400756 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - SCHOOL
CA4400757 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - SCHOOL
CA4400758 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - SCHOOL
CA4400762 | LPA74 - SANTA CRUZ COUNTY | C | NT - INSTITUTION
CA4400763 | LPA74 - SANTA CRUZ COUNTY | C | NT - INDUSTRIAL/AGRICULTURAL
CA4400764 | LPA74 - SANTA CRUZ COUNTY | C | T - SUMMER CAMP
CA4400774 | LPA74 - SANTA CRUZ COUNTY | NC | T - RECREATION AREA
CA4400800 | LPA74 - SANTA CRUZ COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA4400801 | DISTRICT 05 - MONTEREY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4400803 | LPA74 - SANTA CRUZ COUNTY | NC | T - SUMMER CAMP
CA4400823 | LPA74 - SANTA CRUZ COUNTY | NC | T - OTHER TRANSIENT AREA
CA4400825 | LPA74 - SANTA CRUZ COUNTY | NC | T - RECREATION AREA
CA4400850 | LPA74 - SANTA CRUZ COUNTY | C | R - MOBILE HOME PARK
CA4400851 | LPA74 - SANTA CRUZ COUNTY | NC | T - SUMMER CAMP
CA4400875 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - SCHOOL
CA4400902 | LPA74 - SANTA CRUZ COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4400903 | LPA74 - SANTA CRUZ COUNTY | NC | T - SUMMER CAMP
CA4400904 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4400905 | LPA74 - SANTA CRUZ COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4400906 | LPA74 - SANTA CRUZ COUNTY | NC | T - OTHER TRANSIENT AREA
CA4400907 | LPA74 - SANTA CRUZ COUNTY | NC | T - OTHER TRANSIENT AREA
CA4400908 | LPA74 - SANTA CRUZ COUNTY | NC | T - RECREATION AREA
CA4400912 | DISTRICT 05 - MONTEREY | NC | T - RECREATION AREA
CA4400913 | LPA74 - SANTA CRUZ COUNTY | NC | T - OTHER TRANSIENT AREA
CA4410001 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4410002 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4410008 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4410010 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4410011 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4410013 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4410014 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4410016 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4410017 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4410018 | DISTRICT 05 - MONTEREY | C | R - RESIDENTIAL AREA
CA4410304 | DISTRICT 05 - MONTEREY | NC | T - RECREATION AREA
CA4410306 | DISTRICT 05 - MONTEREY | NC | T - RECREATION AREA
CA4410307 | DISTRICT 05 - MONTEREY | NC | T - OTHER TRANSIENT AREA
CA4410308 | DISTRICT 05 - MONTEREY | NC | T - RECREATION AREA
CA4410800 | DISTRICT 05 - MONTEREY | NTNC | NT - INSTITUTION
CA4500003 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500006 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4500007 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500008 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500009 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500011 | LPA75 - SHASTA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA4500012 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500013 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500014 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4500014 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4500015 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4500016 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500017 | LPA75 - SHASTA COUNTY | NC | R - RESIDENTIAL AREA
CA4500018 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500020 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500022 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4500023 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4500024 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500027 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500028 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4500030 | LPA75 - SHASTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4500035 | LPA75 - SHASTA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA4500036 | DISTRICT 02 - LASSEN | NTNC | R - OTHER RESIDENTIAL AREA
CA4500037 | LPA75 - SHASTA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA4500038 | DISTRICT 02 - LASSEN | SSWS | R - OTHER RESIDENTIAL AREA
CA4500039 | DISTRICT 02 - LASSEN | SSWS | R - OTHER RESIDENTIAL AREA
CA4500041 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL
CA4500053 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500054 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500058 | LPA75 - SHASTA COUNTY | NC | R - MOBILE HOME PARK
CA4500061 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500062 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500063 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500066 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500069 | LPA75 - SHASTA COUNTY | SSWS | T - RECREATION AREA
CA4500071 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500072 | DISTRICT 02 - LASSEN | NC | T - OTHER TRANSIENT AREA
CA4500074 | LPA75 - SHASTA COUNTY | SSWS | R - MOBILE HOME PARK
CA4500078 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500080 | LPA75 - SHASTA COUNTY | NC | R - MOBILE HOME PARK
CA4500081 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500082 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500083 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500085 | LPA75 - SHASTA COUNTY | NC | R - MOBILE HOME PARK
CA4500086 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500089 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500090 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500091 | LPA75 - SHASTA COUNTY | SSWS | R - MOBILE HOME PARK
CA4500092 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500093 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500094 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500097 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500098 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500099 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500101 | LPA75 - SHASTA COUNTY | C | T - RECREATION AREA
CA4500102 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500104 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500105 | LPA75 - SHASTA COUNTY | SSWS | O - OTHER AREA
CA4500106 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500107 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500110 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500113 | LPA75 - SHASTA COUNTY | NTNC | T - RECREATION AREA
CA4500120 | LPA75 - SHASTA COUNTY | NC | T - RESTAURANT
CA4500140 | LPA75 - SHASTA COUNTY | NC | T - RESTAURANT
CA4500142 | LPA75 - SHASTA COUNTY | SSWS | T - HOTEL/MOTEL
CA4500143 | LPA75 - SHASTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4500149 | LPA75 - SHASTA COUNTY | NTNC | T - RESTAURANT
CA4500153 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA4500160 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL
CA4500161 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL
CA4500162 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL
CA4500163 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL
CA4500167 | LPA75 - SHASTA COUNTY | NC | T - RESTAURANT
CA4500169 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL
CA4500170 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL
CA4500173 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500178 | LPA75 - SHASTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4500180 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL
CA4500181 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL
CA4500183 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL
CA4500184 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500185 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500186 | LPA75 - SHASTA COUNTY | NC | NT - OTHER NON-TRANSIENT AREA
CA4500190 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL
CA4500191 | LPA75 - SHASTA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4500192 | LPA75 - SHASTA COUNTY | NC | T - HOTEL/MOTEL
CA4500193 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL
CA4500194 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500195 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500200 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500203 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500204 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500208 | LPA75 - SHASTA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA4500210 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4500213 | LPA75 - SHASTA COUNTY | NTNC | T - RESTAURANT
CA4500214 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL
CA4500215 | LPA75 - SHASTA COUNTY | NC | T - SERVICE STATION
CA4500216 | LPA75 - SHASTA COUNTY | NTNC | T - RECREATION AREA
CA4500217 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500219 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500220 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500221 | LPA75 - SHASTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4500224 | LPA75 - SHASTA COUNTY | NC | T - RESTAURANT
CA4500226 | LPA75 - SHASTA COUNTY | SSWS | R - RESIDENTIAL AREA
CA4500230 | LPA75 - SHASTA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA4500231 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500235 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500237 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA4500241 | LPA75 - SHASTA COUNTY | NC | T - RESTAURANT
CA4500242 | LPA75 - SHASTA COUNTY | SSWS | R - RESIDENTIAL AREA
CA4500243 | LPA75 - SHASTA COUNTY | NC | T - SUMMER CAMP
CA4500244 | LPA75 - SHASTA COUNTY | NC | T - SUMMER CAMP
CA4500245 | LPA75 - SHASTA COUNTY | NC | T - SUMMER CAMP
CA4500246 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500247 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500248 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500254 | LPA75 - SHASTA COUNTY | C | R - OTHER RESIDENTIAL AREA
CA4500255 | LPA75 - SHASTA COUNTY | C | T - OTHER TRANSIENT AREA
CA4500256 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500258 | LPA75 - SHASTA COUNTY | SSWS | O - WHOLESALER (SELLS WATER)
CA4500259 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500260 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500261 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500262 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500265 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500271 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500274 | LPA75 - SHASTA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA4500277 | LPA75 - SHASTA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA4500283 | DISTRICT 02 - LASSEN | NC | T - HIGHWAY REST AREA
CA4500284 | DISTRICT 02 - LASSEN | NC | T - HIGHWAY REST AREA
CA4500285 | DISTRICT 02 - LASSEN | NC | T - HIGHWAY REST AREA
CA4500289 | DISTRICT 02 - LASSEN | NC | T - HIGHWAY REST AREA
CA4500290 | LPA75 - SHASTA COUNTY | C | R - MOBILE HOME PARK
CA4500293 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500294 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500302 | LPA75 - SHASTA COUNTY | NC | T - RESTAURANT
CA4500303 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500306 | LPA75 - SHASTA COUNTY | NC | T - RESTAURANT
CA4500309 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500310 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500313 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500314 | LPA75 - SHASTA COUNTY | C | R - RESIDENTIAL AREA
CA4500315 | LPA75 - SHASTA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA4500316 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500317 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4500320 | LPA75 - SHASTA COUNTY | NC | T - HOTEL/MOTEL
CA4500322 | LPA75 - SHASTA COUNTY | NTNC | NT - SCHOOL
CA4500324 | LPA75 - SHASTA COUNTY | NC | T - SUMMER CAMP
CA4500325 | LPA75 - SHASTA COUNTY | NC | T - SUMMER CAMP
CA4500327 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500328 | LPA75 - SHASTA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA4500329 | LPA75 - SHASTA COUNTY | NC | T - RESTAURANT
CA4500331 | LPA75 - SHASTA COUNTY | NC | T - RESTAURANT
CA4500333 | LPA75 - SHASTA COUNTY | NTNC | T - RESTAURANT
CA4500334 | LPA75 - SHASTA COUNTY | NC | R - MOBILE HOME PARK
CA4500336 | LPA75 - SHASTA COUNTY | NC | T - RECREATION AREA
CA4500337 | LPA75 - SHASTA COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA4500339 | LPA75 - SHASTA COUNTY | NC | T - RESTAURANT
CA4500341 | LPA75 - SHASTA COUNTY | NTNC | NT - MEDICAL FACILITY
CA4500343 | LPA75 - SHASTA COUNTY | NC | T - RETAIL EMPLOYEES
CA4500344 | LPA75 - SHASTA COUNTY | NTNC | NT - OTHER NON-TRANSIENT AREA
CA4500345 | LPA75 - SHASTA COUNTY | NC | T - HOTEL/MOTEL
CA4500346 | LPA75 - SHASTA COUNTY | NC | T - SUMMER CAMP
CA4500347 | LPA75 - SHASTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4500348 | LPA75 - SHASTA COUNTY | NC | T - RESTAURANT
CA4500349 | LPA75 - SHASTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4500350 | LPA75 - SHASTA COUNTY | NC | T - OTHER TRANSIENT AREA
CA4500351 | LPA75 - SHASTA COUNTY | NC | T - SERVICE STATION
CA4510001 | DISTRICT 02 - LASSEN | C | O - OTHER AREA
CA4510002 | DISTRICT 02 - LASSEN | C | O - OTHER AREA
CA4510003 | DISTRICT 02 - LASSEN | C | O - OTHER AREA
CA4510004 | DISTRICT 02 - LASSEN | C | O - OTHER AREA
CA4510005 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4510006 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4510007 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4510008 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4510009 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4510011 | DISTRICT 02 - LASSEN | C | T - RECREATION AREA
CA4510013 | DISTRICT 02 - LASSEN | C | T - RECREATION AREA
CA4510014 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4510015 | DISTRICT 02 - LASSEN | C | T - RECREATION AREA
CA4510016 | DISTRICT 02 - LASSEN | C | O - WHOLESALER (SELLS WATER)
CA4510302 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA4510303 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA4510503 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA4510504 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA4510505 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA4510506 | DISTRICT 02 - LASSEN | NTNC | T - RECREATION AREA
CA4510507 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA4510508 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA4510800 | DISTRICT 02 - LASSEN | NTNC | NT - INSTITUTION
CA4600003 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600005 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600006 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600009 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4600012 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4600017 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4600017 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4600018 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4600019 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4600037 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA4600051 | DISTRICT 02 - LASSEN | NC | R - RESIDENTIAL AREA
CA4600056 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4600061 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600062 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600064 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA4600066 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600068 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600069 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600071 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600072 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600075 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600078 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600079 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600080 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600081 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600082 | DISTRICT 02 - LASSEN | NC | T - OTHER TRANSIENT AREA
CA4600084 | DISTRICT 02 - LASSEN | NC | T - HOTEL/MOTEL
CA4600086 | DISTRICT 02 - LASSEN | NC | T - RECREATION AREA
CA4600094 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600096 | DISTRICT 02 - LASSEN | NC | NT - SCHOOL
CA4600098 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4600103 | DISTRICT 02 - LASSEN | NC | T - SUMMER CAMP
CA4610001 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4610002 | DISTRICT 02 - LASSEN | C | R - RESIDENTIAL AREA
CA4700501 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA4700503 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4700503 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4700513 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4700521 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4700523 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4700528 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4700531 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4700541 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK
CA4700542 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK
CA4700545 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA4700546 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK
CA4700549 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4700551 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4700554 | DISTRICT 01 - KLAMATH | NC | T - HIGHWAY REST AREA
CA4700557 | DISTRICT 01 - KLAMATH | NC | T - HIGHWAY REST AREA
CA4700558 | DISTRICT 01 - KLAMATH | NC | T - HIGHWAY REST AREA
CA4700559 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA4700562 | DISTRICT 01 - KLAMATH | NC | T - HOTEL/MOTEL
CA4700563 | DISTRICT 01 - KLAMATH | NC | T - HOTEL/MOTEL
CA4700565 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA4700569 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA4700571 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA4700573 | DISTRICT 01 - KLAMATH | NTNC | T - OTHER TRANSIENT AREA
CA4700577 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA4700582 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA4700585 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA4700591 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA4700593 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA4700594 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA4700597 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA4700601 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA4700603 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA4700612 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA4700626 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK
CA4700627 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK
CA4700630 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4700638 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4700663 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA4700666 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA4700669 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA4700686 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4700702 | DISTRICT 01 - KLAMATH | NC | O - OTHER AREA
CA4700705 | DISTRICT 01 - KLAMATH | NC | O - OTHER AREA
CA4700722 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA4700803 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK
CA4700807 | DISTRICT 01 - KLAMATH | NC | T - SUMMER CAMP
CA4700814 | DISTRICT 01 - KLAMATH | NC | T - SUMMER CAMP
CA4700825 | DISTRICT 01 - KLAMATH | NC | T - SECONDARY RESIDENCES
CA4700828 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA4700839 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA4700851 | DISTRICT 01 - KLAMATH | NC | O - OTHER AREA
CA4700863 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA4700870 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA4700872 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4700875 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA4700880 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4700881 | DISTRICT 01 - KLAMATH | NTNC | NT - MEDICAL FACILITY
CA4700884 | DISTRICT 01 - KLAMATH | C | T - OTHER TRANSIENT AREA
CA4700891 | DISTRICT 01 - KLAMATH | NC | R - OTHER RESIDENTIAL AREA
CA4700894 | DISTRICT 01 - KLAMATH | NC | T - RETAIL EMPLOYEES
CA4710001 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4710002 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4710003 | DISTRICT 01 - KLAMATH | C | T - RECREATION AREA
CA4710004 | DISTRICT 01 - KLAMATH | C | T - RECREATION AREA
CA4710006 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4710007 | DISTRICT 01 - KLAMATH | C | T - RECREATION AREA
CA4710008 | DISTRICT 01 - KLAMATH | C | T - RECREATION AREA
CA4710009 | DISTRICT 01 - KLAMATH | C | T - RECREATION AREA
CA4710010 | DISTRICT 01 - KLAMATH | C | T - RECREATION AREA
CA4710011 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA4710012 | DISTRICT 01 - KLAMATH | C | T - RECREATION AREA
CA4710013 | DISTRICT 01 - KLAMATH | C | T - RECREATION AREA
CA4710500 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA4710800 | DISTRICT 01 - KLAMATH | NTNC | NT - INSTITUTION
CA4800527 | DISTRICT 04 - SAN FRANCISCO | NC | T - HOTEL/MOTEL
CA4800531 | DISTRICT 04 - SAN FRANCISCO | C | R - OTHER RESIDENTIAL AREA
CA4800558 | DISTRICT 04 - SAN FRANCISCO | NC | T - RESTAURANT
CA4800561 | DISTRICT 04 - SAN FRANCISCO | C | T - RECREATION AREA
CA4800564 | DISTRICT 04 - SAN FRANCISCO | C | R - MOBILE HOME PARK
CA4800574 | DISTRICT 04 - SAN FRANCISCO | C | R - OTHER RESIDENTIAL AREA
CA4800589 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA4800595 | DISTRICT 04 - SAN FRANCISCO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4800596 | DISTRICT 04 - SAN FRANCISCO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4800612 | DISTRICT 04 - SAN FRANCISCO | NC | T - RESTAURANT
CA4800615 | DISTRICT 04 - SAN FRANCISCO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4800651 | DISTRICT 04 - SAN FRANCISCO | NC | T - RECREATION AREA
CA4800695 | DISTRICT 04 - SAN FRANCISCO | NC | T - RESTAURANT
CA4800709 | DISTRICT 04 - SAN FRANCISCO | NC | T - RECREATION AREA
CA4800727 | DISTRICT 04 - SAN FRANCISCO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4800732 | DISTRICT 04 - SAN FRANCISCO | NC | T - SERVICE STATION
CA4800753 | DISTRICT 04 - SAN FRANCISCO | C | R - MOBILE HOME PARK
CA4800755 | DISTRICT 04 - SAN FRANCISCO | NC | T - OTHER TRANSIENT AREA
CA4800767 | DISTRICT 04 - SAN FRANCISCO | NTNC | R - RESIDENTIAL AREA
CA4800773 | DISTRICT 04 - SAN FRANCISCO | NC | T - RESTAURANT
CA4800781 | DISTRICT 04 - SAN FRANCISCO | NC | T - HIGHWAY REST AREA
CA4800784 | DISTRICT 04 - SAN FRANCISCO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4800786 | DISTRICT 04 - SAN FRANCISCO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4800797 | DISTRICT 04 - SAN FRANCISCO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4800801 | DISTRICT 04 - SAN FRANCISCO | NTNC | T - SERVICE STATION
CA4800804 | DISTRICT 04 - SAN FRANCISCO | NTNC | T - SECONDARY RESIDENCES
CA4800807 | DISTRICT 04 - SAN FRANCISCO | NC | T - SERVICE STATION
CA4800809 | DISTRICT 04 - SAN FRANCISCO | NC | NT - INSTITUTION
CA4800812 | DISTRICT 04 - SAN FRANCISCO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4800818 | DISTRICT 04 - SAN FRANCISCO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4800820 | DISTRICT 04 - SAN FRANCISCO | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4800826 | DISTRICT 04 - SAN FRANCISCO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4810001 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA4810002 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA4810003 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA4810004 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA4810005 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA4810007 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA4810008 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA4810009 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA4810010 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA4810011 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA4810012 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA4810013 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA4810015 | DISTRICT 04 - SAN FRANCISCO | C | O - WHOLESALER (SELLS WATER)
CA4810017 | DISTRICT 04 - SAN FRANCISCO | NC | T - RECREATION AREA
CA4810019 | DISTRICT 04 - SAN FRANCISCO | NTNC | O - OTHER AREA
CA4810020 | DISTRICT 04 - SAN FRANCISCO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4810021 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA4810023 | DISTRICT 04 - SAN FRANCISCO | NC | T - RESTAURANT
CA4810024 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA4810025 | DISTRICT 04 - SAN FRANCISCO | C | R - RESIDENTIAL AREA
CA4810026 | DISTRICT 04 - SAN FRANCISCO | C | T - SECONDARY RESIDENCES
CA4810030 | DISTRICT 04 - SAN FRANCISCO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4810033 | DISTRICT 04 - SAN FRANCISCO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4810034 | DISTRICT 04 - SAN FRANCISCO | NC | T - SERVICE STATION
CA4810035 | DISTRICT 04 - SAN FRANCISCO | NC | T - RECREATION AREA
CA4810036 | DISTRICT 04 - SAN FRANCISCO | NC | NT - OTHER NON-TRANSIENT AREA
CA4810038 | DISTRICT 04 - SAN FRANCISCO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4810040 | DISTRICT 04 - SAN FRANCISCO | NTNC | NT - OTHER NON-TRANSIENT AREA
CA4810043 | DISTRICT 04 - SAN FRANCISCO | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4810701 | DISTRICT 04 - SAN FRANCISCO | C | NT - INSTITUTION
CA4810800 | DISTRICT 04 - SAN FRANCISCO | C | NT - MEDICAL FACILITY
CA4810801 | DISTRICT 04 - SAN FRANCISCO | C | NT - INSTITUTION
CA4900033 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900107 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900508 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900510 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900510 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900512 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900513 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900514 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900521 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900532 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900533 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900536 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900536 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900543 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900545 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900546 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900547 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900548 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900549 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900549 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900551 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900552 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900553 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900558 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900559 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900560 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900561 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900562 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900563 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900568 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900570 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900570 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900573 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900575 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900577 | DISTRICT 18 - SONOMA | C | NT - SCHOOL
CA4900578 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900580 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900584 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900585 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900587 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900588 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900599 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900600 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900603 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900604 | DISTRICT 25 - MARIN | NC | NT - SCHOOL
CA4900605 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900608 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900611 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900611 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900612 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900620 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900629 | DISTRICT 25 - MARIN | NC | R - RESIDENTIAL AREA
CA4900630 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900634 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900637 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900639 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900640 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900641 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900644 | DISTRICT 18 - SONOMA | C | T - OTHER TRANSIENT AREA
CA4900646 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900647 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900647 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900653 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900660 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900665 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900667 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900669 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900673 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900674 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900675 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900679 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900680 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900684 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900686 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4900687 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900693 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900694 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900695 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900699 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900703 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900704 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900705 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900707 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900708 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900710 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900711 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900714 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900716 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900719 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900720 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900721 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900722 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4900723 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900728 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900736 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900737 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4900739 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900743 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4900745 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4900748 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4900774 | DISTRICT 25 - MARIN | NC | T - SUMMER CAMP
CA4900785 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900787 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900788 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900789 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900791 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900792 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900793 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900794 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900795 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900796 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900797 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900798 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900799 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900812 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4900813 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900817 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4900832 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900841 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900843 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900844 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4900846 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900847 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4900850 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900850 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900853 | DISTRICT 25 - MARIN | NC | R - RESIDENTIAL AREA
CA4900859 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4900871 | DISTRICT 18 - SONOMA | C | R - MOBILE HOME PARK
CA4900873 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900875 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4900878 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4900892 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900893 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900897 | DISTRICT 18 - SONOMA | NTNC | T - OTHER TRANSIENT AREA
CA4900898 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4900901 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900904 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4900905 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900907 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900909 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4900911 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900912 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900913 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900916 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900924 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900925 | DISTRICT 18 - SONOMA | NTNC | T - OTHER TRANSIENT AREA
CA4900934 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900935 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4900936 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900943 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900945 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4900946 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900949 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4900957 | DISTRICT 18 - SONOMA | NTNC | T - OTHER TRANSIENT AREA
CA4900968 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900973 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4900974 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900975 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900981 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900982 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900986 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900994 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900998 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4900999 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4901004 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901008 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901016 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901017 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4901018 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4901024 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901025 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4901027 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901028 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4901030 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901038 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901042 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901044 | DISTRICT 25 - MARIN | NC | T - SUMMER CAMP
CA4901046 | DISTRICT 18 - SONOMA | NTNC | T - HOTEL/MOTEL
CA4901060 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4901061 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901062 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4901063 | DISTRICT 25 - MARIN | NC | NT - INSTITUTION
CA4901066 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901068 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4901069 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901071 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4901073 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901074 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901077 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4901079 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901080 | DISTRICT 18 - SONOMA | NTNC | T - OTHER TRANSIENT AREA
CA4901082 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901083 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901084 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4901086 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901090 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901093 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901094 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901095 | DISTRICT 18 - SONOMA | NTNC | T - SUMMER CAMP
CA4901096 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4901101 | DISTRICT 25 - MARIN | NC | T - SUMMER CAMP
CA4901105 | DISTRICT 25 - MARIN | NC | T - SUMMER CAMP
CA4901106 | DISTRICT 25 - MARIN | NC | T - SUMMER CAMP
CA4901107 | DISTRICT 25 - MARIN | NC | T - SUMMER CAMP
CA4901109 | DISTRICT 25 - MARIN | NC | T - SUMMER CAMP
CA4901112 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4901113 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901115 | DISTRICT 25 - MARIN | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4901118 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4901119 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4901120 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901122 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901129 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4901130 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901133 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901135 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901139 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901141 | DISTRICT 18 - SONOMA | NTNC | T - SUMMER CAMP
CA4901143 | DISTRICT 18 - SONOMA | NTNC | T - SUMMER CAMP
CA4901144 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4901147 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901151 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901152 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4901156 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4901161 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4901162 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4901164 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901165 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901168 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4901170 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901175 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4901176 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901179 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901181 | DISTRICT 25 - MARIN | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4901189 | DISTRICT 25 - MARIN | NC | R - OTHER RESIDENTIAL AREA
CA4901190 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4901191 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901193 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901196 | DISTRICT 25 - MARIN | NC | T - HOTEL/MOTEL
CA4901201 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901202 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901203 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901204 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901205 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4901206 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901207 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901208 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901212 | DISTRICT 18 - SONOMA | NTNC | T - OTHER TRANSIENT AREA
CA4901213 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901214 | DISTRICT 18 - SONOMA | NTNC | NT - DAY CARE CENTER
CA4901215 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4901216 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901218 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901220 | DISTRICT 25 - MARIN | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4901221 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4901222 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4901223 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4901225 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901227 | DISTRICT 18 - SONOMA | NTNC | T - OTHER TRANSIENT AREA
CA4901231 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901232 | DISTRICT 18 - SONOMA | NTNC | T - OTHER TRANSIENT AREA
CA4901233 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901234 | DISTRICT 25 - MARIN | NC | NT - INSTITUTION
CA4901236 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4901244 | DISTRICT 18 - SONOMA | NTNC | T - OTHER TRANSIENT AREA
CA4901245 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901246 | DISTRICT 18 - SONOMA | C | T - OTHER TRANSIENT AREA
CA4901247 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901248 | DISTRICT 18 - SONOMA | NTNC | T - OTHER TRANSIENT AREA
CA4901250 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901251 | DISTRICT 18 - SONOMA | NTNC | T - RECREATION AREA
CA4901252 | DISTRICT 18 - SONOMA | NTNC | T - OTHER TRANSIENT AREA
CA4901253 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901254 | DISTRICT 18 - SONOMA | NTNC | T - RESTAURANT
CA4901255 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901257 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901258 | DISTRICT 18 - SONOMA | NTNC | T - RECREATION AREA
CA4901259 | DISTRICT 18 - SONOMA | NTNC | T - OTHER TRANSIENT AREA
CA4901261 | DISTRICT 25 - MARIN | NC | T - HIGHWAY REST AREA
CA4901262 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901263 | DISTRICT 25 - MARIN | NC | R - OTHER RESIDENTIAL AREA
CA4901264 | DISTRICT 18 - SONOMA | NTNC | O - OTHER AREA
CA4901265 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901266 | DISTRICT 18 - SONOMA | NTNC | O - OTHER AREA
CA4901267 | DISTRICT 18 - SONOMA | NTNC | NT - INSTITUTION
CA4901269 | DISTRICT 25 - MARIN | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4901272 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901273 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901274 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901275 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901277 | DISTRICT 18 - SONOMA | NTNC | O - OTHER AREA
CA4901278 | DISTRICT 18 - SONOMA | NTNC | O - OTHER AREA
CA4901282 | DISTRICT 18 - SONOMA | NTNC | O - OTHER AREA
CA4901283 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901284 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901286 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901287 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901290 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901291 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901293 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901294 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901295 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901297 | DISTRICT 18 - SONOMA | NTNC | NT - OTHER NON-TRANSIENT AREA
CA4901298 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901299 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901300 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901301 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901305 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901308 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901309 | DISTRICT 18 - SONOMA | C | O - OTHER AREA
CA4901310 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901312 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901313 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901314 | DISTRICT 18 - SONOMA | NTNC | O - OTHER AREA
CA4901316 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901317 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901321 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901324 | DISTRICT 18 - SONOMA | NTNC | O - OTHER AREA
CA4901327 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901328 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901329 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901330 | DISTRICT 18 - SONOMA | NTNC | O - OTHER AREA
CA4901331 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901332 | DISTRICT 18 - SONOMA | NTNC | O - OTHER AREA
CA4901333 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901334 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901336 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901338 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901340 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901341 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901342 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901343 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901345 | DISTRICT 18 - SONOMA | NTNC | O - OTHER AREA
CA4901346 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4901347 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4901348 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901353 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901355 | DISTRICT 18 - SONOMA | C | O - OTHER AREA
CA4901356 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901357 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901360 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901361 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901362 | DISTRICT 18 - SONOMA | NTNC | O - OTHER AREA
CA4901363 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901364 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901365 | DISTRICT 18 - SONOMA | NTNC | O - OTHER AREA
CA4901366 | DISTRICT 18 - SONOMA | NTNC | O - OTHER AREA
CA4901368 | DISTRICT 18 - SONOMA | NTNC | NT - OTHER NON-TRANSIENT AREA
CA4901370 | DISTRICT 18 - SONOMA | NTNC | NT - MEDICAL FACILITY
CA4901373 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901374 | DISTRICT 18 - SONOMA | NTNC | T - OTHER TRANSIENT AREA
CA4901375 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901377 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901381 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4901382 | DISTRICT 18 - SONOMA | NTNC | NT - DAY CARE CENTER
CA4901383 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901384 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901388 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901390 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901392 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901393 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901394 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901395 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901398 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901399 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4901400 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901401 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901403 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901404 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901405 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901406 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901407 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901408 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901409 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901411 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901412 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901413 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901414 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901419 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901420 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901423 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901425 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901426 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901431 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901432 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901433 | DISTRICT 25 - MARIN | NC | T - RETAIL EMPLOYEES
CA4901436 | DISTRICT 18 - SONOMA | NTNC | NT - SCHOOL
CA4901437 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901440 | DISTRICT 25 - MARIN | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4901442 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901444 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901445 | DISTRICT 18 - SONOMA | C | R - SUBDIVISION
CA4901446 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901447 | DISTRICT 25 - MARIN | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4901448 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901449 | DISTRICT 25 - MARIN | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4901451 | DISTRICT 25 - MARIN | NC | O - OTHER AREA
CA4901452 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901453 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901454 | DISTRICT 18 - SONOMA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA4901455 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901459 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901460 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901464 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901465 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901466 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901468 | DISTRICT 25 - MARIN | NC | T - RESTAURANT
CA4901473 | DISTRICT 25 - MARIN | NC | T - OTHER TRANSIENT AREA
CA4901474 | DISTRICT 25 - MARIN | NC | NT - INDUSTRIAL/AGRICULTURAL
CA4910002 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910003 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910004 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910005 | DISTRICT 18 - SONOMA | C | O - WHOLESALER (SELLS WATER)
CA4910006 | DISTRICT 18 - SONOMA | C | O - WHOLESALER (SELLS WATER)
CA4910007 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910008 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910009 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910010 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910011 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910012 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910013 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910014 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910016 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910017 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910018 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910019 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910020 | DISTRICT 18 - SONOMA | C | O - WHOLESALER (SELLS WATER)
CA4910021 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910022 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910022 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910023 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910024 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910025 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910026 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910027 | DISTRICT 18 - SONOMA | C | NT - SCHOOL
CA4910028 | DISTRICT 18 - SONOMA | C | R - RESIDENTIAL AREA
CA4910029 | DISTRICT 18 - SONOMA | C | O - WHOLESALER (SELLS WATER)
CA4910302 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4910304 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4910305 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4910306 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4910308 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4910309 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4910310 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4910311 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4910313 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA4910701 | DISTRICT 18 - SONOMA | C | NT - INSTITUTION
CA4910702 | DISTRICT 25 - MARIN | NC | T - RECREATION AREA
CA5000003 | LPA80 - STANISLAUS COUNTY | SSWS | R - RESIDENTIAL AREA
CA5000005 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000008 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000010 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000013 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000014 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000015 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000016 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000017 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000019 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000020 | LPA80 - STANISLAUS COUNTY | SSWS | R - RESIDENTIAL AREA
CA5000033 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK
CA5000041 | LPA80 - STANISLAUS COUNTY | NC | R - MOBILE HOME PARK
CA5000048 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK
CA5000049 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK
CA5000054 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK
CA5000055 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK
CA5000058 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK
CA5000060 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK
CA5000061 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK
CA5000062 | LPA80 - STANISLAUS COUNTY | SSWS | R - MOBILE HOME PARK
CA5000066 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK
CA5000067 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK
CA5000071 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK
CA5000072 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK
CA5000076 | LPA80 - STANISLAUS COUNTY | NC | T - RECREATION AREA
CA5000080 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK
CA5000082 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK
CA5000090 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK
CA5000091 | LPA80 - STANISLAUS COUNTY | NC | T - RESTAURANT
CA5000095 | LPA80 - STANISLAUS COUNTY | C | R - MOBILE HOME PARK
CA5000099 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000101 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL
CA5000109 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL
CA5000110 | LPA80 - STANISLAUS COUNTY | NC | T - RESTAURANT
CA5000117 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000132 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL
CA5000133 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL
CA5000134 | DISTRICT 10 - STOCKTON | NC | T - HIGHWAY REST AREA
CA5000136 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000141 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000154 | LPA80 - STANISLAUS COUNTY | NTNC | T - RESTAURANT
CA5000155 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL
CA5000158 | LPA80 - STANISLAUS COUNTY | NC | T - SERVICE STATION
CA5000164 | LPA80 - STANISLAUS COUNTY | NC | T - RECREATION AREA
CA5000165 | LPA80 - STANISLAUS COUNTY | NC | T - RECREATION AREA
CA5000166 | LPA80 - STANISLAUS COUNTY | NC | T - RECREATION AREA
CA5000175 | LPA80 - STANISLAUS COUNTY | NC | T - RESTAURANT
CA5000177 | LPA80 - STANISLAUS COUNTY | NC | T - SUMMER CAMP
CA5000179 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000189 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000202 | LPA80 - STANISLAUS COUNTY | NTNC | T - RESTAURANT
CA5000211 | DISTRICT 10 - STOCKTON | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000213 | LPA80 - STANISLAUS COUNTY | NC | T - HOTEL/MOTEL
CA5000218 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000219 | LPA80 - STANISLAUS COUNTY | SSWS | R - RESIDENTIAL AREA
CA5000224 | LPA80 - STANISLAUS COUNTY | SSWS | R - RESIDENTIAL AREA
CA5000225 | LPA80 - STANISLAUS COUNTY | SSWS | T - HOTEL/MOTEL
CA5000237 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000238 | LPA80 - STANISLAUS COUNTY | SSWS | NT - INDUSTRIAL/AGRICULTURAL
CA5000239 | LPA80 - STANISLAUS COUNTY | NC | T - RECREATION AREA
CA5000243 | LPA80 - STANISLAUS COUNTY | NC | T - RECREATION AREA
CA5000249 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL
CA5000255 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL
CA5000261 | LPA80 - STANISLAUS COUNTY | NC | T - RESTAURANT
CA5000263 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000268 | LPA80 - STANISLAUS COUNTY | SSWS | R - RESIDENTIAL AREA
CA5000272 | LPA80 - STANISLAUS COUNTY | NC | T - RECREATION AREA
CA5000273 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL
CA5000274 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL
CA5000277 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL
CA5000284 | LPA80 - STANISLAUS COUNTY | NC | T - RECREATION AREA
CA5000286 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000290 | LPA80 - STANISLAUS COUNTY | NC | T - RESTAURANT
CA5000295 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL
CA5000297 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000298 | LPA80 - STANISLAUS COUNTY | NC | T - RECREATION AREA
CA5000301 | LPA80 - STANISLAUS COUNTY | SSWS | R - RESIDENTIAL AREA
CA5000306 | LPA80 - STANISLAUS COUNTY | SSWS | R - RESIDENTIAL AREA
CA5000307 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000313 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000316 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000317 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000319 | LPA80 - STANISLAUS COUNTY | SSWS | R - RESIDENTIAL AREA
CA5000332 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000335 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL
CA5000336 | LPA80 - STANISLAUS COUNTY | SSWS | NT - INDUSTRIAL/AGRICULTURAL
CA5000337 | LPA80 - STANISLAUS COUNTY | SSWS | R - RESIDENTIAL AREA
CA5000346 | LPA80 - STANISLAUS COUNTY | NC | T - RESTAURANT
CA5000347 | LPA80 - STANISLAUS COUNTY | NC | T - RESTAURANT
CA5000368 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000371 | LPA80 - STANISLAUS COUNTY | SSWS | R - RESIDENTIAL AREA
CA5000372 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000382 | LPA80 - STANISLAUS COUNTY | NC | T - RESTAURANT
CA5000383 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000384 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000388 | LPA80 - STANISLAUS COUNTY | SSWS | T - OTHER TRANSIENT AREA
CA5000389 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000395 | LPA80 - STANISLAUS COUNTY | NC | T - RECREATION AREA
CA5000400 | LPA80 - STANISLAUS COUNTY | NC | T - RESTAURANT
CA5000401 | LPA80 - STANISLAUS COUNTY | NC | T - RECREATION AREA
CA5000402 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000404 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL
CA5000408 | LPA80 - STANISLAUS COUNTY | C | R - RESIDENTIAL AREA
CA5000409 | LPA80 - STANISLAUS COUNTY | NC | T - RESTAURANT
CA5000411 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000413 | LPA80 - STANISLAUS COUNTY | SSWS | R - RESIDENTIAL AREA
CA5000414 | LPA80 - STANISLAUS COUNTY | NC | NT - OTHER NON-TRANSIENT AREA
CA5000426 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000427 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000433 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5000435 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000439 | LPA80 - STANISLAUS COUNTY | NC | T - SERVICE STATION
CA5000440 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000443 | LPA80 - STANISLAUS COUNTY | NC | T - SERVICE STATION
CA5000446 | LPA80 - STANISLAUS COUNTY | NC | T - RESTAURANT
CA5000447 | LPA80 - STANISLAUS COUNTY | NTNC | T - SERVICE STATION
CA5000454 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000457 | LPA80 - STANISLAUS COUNTY | NC | T - SERVICE STATION
CA5000462 | LPA80 - STANISLAUS COUNTY | NC | T - HOTEL/MOTEL
CA5000465 | LPA80 - STANISLAUS COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA5000467 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000470 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000473 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INSTITUTION
CA5000474 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000478 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000480 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000481 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000482 | LPA80 - STANISLAUS COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA5000483 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000486 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000487 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000490 | LPA80 - STANISLAUS COUNTY | NC | T - RECREATION AREA
CA5000493 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000494 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000498 | LPA80 - STANISLAUS COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA5000499 | LPA80 - STANISLAUS COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA5000500 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000501 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000502 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000503 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000505 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000507 | LPA80 - STANISLAUS COUNTY | NC | T - SECONDARY RESIDENCES
CA5000509 | LPA80 - STANISLAUS COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5000512 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000516 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000517 | LPA80 - STANISLAUS COUNTY | NTNC | O - OTHER AREA
CA5000525 | LPA80 - STANISLAUS COUNTY | NC | T - SERVICE STATION
CA5000527 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000529 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000530 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000532 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000535 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000536 | LPA80 - STANISLAUS COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5000538 | LPA80 - STANISLAUS COUNTY | NC | O - OTHER AREA
CA5000547 | LPA80 - STANISLAUS COUNTY | NC | T - SERVICE STATION
CA5000548 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000551 | LPA80 - STANISLAUS COUNTY | NC | T - RECREATION AREA
CA5000552 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000554 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000555 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000557 | LPA80 - STANISLAUS COUNTY | NC | O - OTHER AREA
CA5000561 | LPA80 - STANISLAUS COUNTY | NC | O - OTHER AREA
CA5000562 | LPA80 - STANISLAUS COUNTY | NC | T - SECONDARY RESIDENCES
CA5000563 | LPA80 - STANISLAUS COUNTY | NTNC | O - OTHER AREA
CA5000565 | LPA80 - STANISLAUS COUNTY | NTNC | O - OTHER AREA
CA5000568 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL
CA5000571 | LPA80 - STANISLAUS COUNTY | NC | T - OTHER TRANSIENT AREA
CA5000573 | LPA80 - STANISLAUS COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA5000574 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000577 | LPA80 - STANISLAUS COUNTY | NC | T - RESTAURANT
CA5000578 | LPA80 - STANISLAUS COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5000579 | LPA80 - STANISLAUS COUNTY | C | NT - INDUSTRIAL/AGRICULTURAL
CA5000580 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000581 | LPA80 - STANISLAUS COUNTY | NTNC | O - OTHER AREA
CA5000582 | LPA80 - STANISLAUS COUNTY | NC | T - SERVICE STATION
CA5000583 | LPA80 - STANISLAUS COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5000584 | LPA80 - STANISLAUS COUNTY | NTNC | NT - SCHOOL
CA5000585 | LPA80 - STANISLAUS COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5000586 | LPA80 - STANISLAUS COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5000588 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000590 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000592 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000593 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000595 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000596 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000599 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000600 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000601 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000603 | LPA80 - STANISLAUS COUNTY | NTNC | T - RESTAURANT
CA5000604 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5000605 | LPA80 - STANISLAUS COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5010005 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010006 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010007 | DISTRICT 10 - STOCKTON | C | R - OTHER RESIDENTIAL AREA
CA5010008 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010009 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010010 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010013 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010014 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010017 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010018 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010019 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010021 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010023 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010026 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010028 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010029 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010031 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010033 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010034 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010035 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010038 | DISTRICT 10 - STOCKTON | C | O - WHOLESALER (SELLS WATER)
CA5010039 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010040 | DISTRICT 10 - STOCKTON | C | O - WHOLESALER (SELLS WATER)
CA5010042 | DISTRICT 10 - STOCKTON | C | R - RESIDENTIAL AREA
CA5010044 | DISTRICT 10 - STOCKTON | NTNC | NT - OTHER NON-TRANSIENT AREA
CA5010300 | DISTRICT 10 - STOCKTON | NC | T - RECREATION AREA
CA5100107 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5100112 | DISTRICT 21 - VALLEY | C | R - MOBILE HOME PARK
CA5100117 | DISTRICT 21 - VALLEY | NC | T - OTHER TRANSIENT AREA
CA5100118 | DISTRICT 21 - VALLEY | NC | T - RESTAURANT
CA5100125 | DISTRICT 21 - VALLEY | C | T - HOTEL/MOTEL
CA5100135 | DISTRICT 21 - VALLEY | NC | R - RESIDENTIAL AREA
CA5100136 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL
CA5100138 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL
CA5100140 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL
CA5100141 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL
CA5100142 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL
CA5100143 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL
CA5100145 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL
CA5100149 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL
CA5100153 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5100159 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA5100160 | DISTRICT 21 - VALLEY | NC | T - RESTAURANT
CA5100172 | DISTRICT 21 - VALLEY | NTNC | NT - SCHOOL
CA5100180 | DISTRICT 21 - VALLEY | NC | NT - SCHOOL
CA5101009 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5101013 | DISTRICT 21 - VALLEY | NC | T - RESTAURANT
CA5102009 | DISTRICT 21 - VALLEY | NTNC | T - OTHER TRANSIENT AREA
CA5102016 | DISTRICT 21 - VALLEY | NC | T - RESTAURANT
CA5102025 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5102032 | DISTRICT 21 - VALLEY | NTNC | T - OTHER TRANSIENT AREA
CA5103005 | DISTRICT 21 - VALLEY | NC | T - RESTAURANT
CA5103014 | DISTRICT 21 - VALLEY | NC | R - RESIDENTIAL AREA
CA5103015 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5103327 | DISTRICT 21 - VALLEY | NC | T - OTHER TRANSIENT AREA
CA5103335 | DISTRICT 21 - VALLEY | NTNC | NT - DAY CARE CENTER
CA5105002 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA5105004 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5105011 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5105013 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5105014 | DISTRICT 21 - VALLEY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5110001 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5110002 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5110007 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5200006 | LPA82 - TEHAMA COUNTY | NTNC | NT - INSTITUTION
CA5200007 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200008 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200010 | LPA82 - TEHAMA COUNTY | C | T - OTHER TRANSIENT AREA
CA5200012 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200013 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200014 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200015 | LPA82 - TEHAMA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5200255 | LPA82 - TEHAMA COUNTY | C | T - OTHER TRANSIENT AREA
CA5200338 | LPA82 - TEHAMA COUNTY | NC | NT - INSTITUTION
CA5200500 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200502 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200503 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5200504 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5200506 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL
CA5200507 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL
CA5200508 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK
CA5200510 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK
CA5200511 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL
CA5200512 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK
CA5200513 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL
CA5200514 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK
CA5200518 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL
CA5200519 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL
CA5200520 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL
CA5200521 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK
CA5200524 | LPA82 - TEHAMA COUNTY | NTNC | NT - INSTITUTION
CA5200525 | LPA82 - TEHAMA COUNTY | NTNC | NT - DAY CARE CENTER
CA5200526 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK
CA5200527 | LPA82 - TEHAMA COUNTY | C | T - RECREATION AREA
CA5200529 | LPA82 - TEHAMA COUNTY | NTNC | NT - INSTITUTION
CA5200531 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK
CA5200532 | LPA82 - TEHAMA COUNTY | NC | NT - SCHOOL
CA5200534 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5200534 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5200535 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200538 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL
CA5200539 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK
CA5200540 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL
CA5200541 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL
CA5200544 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL
CA5200545 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200546 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK
CA5200547 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK
CA5200548 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200549 | LPA82 - TEHAMA COUNTY | SSWS | R - MOBILE HOME PARK
CA5200551 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200555 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200556 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK
CA5200558 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK
CA5200559 | LPA82 - TEHAMA COUNTY | C | NT - INSTITUTION
CA5200560 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200562 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200565 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL
CA5200569 | LPA82 - TEHAMA COUNTY | SSWS | R - MOBILE HOME PARK
CA5200570 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200571 | LPA82 - TEHAMA COUNTY | C | T - OTHER TRANSIENT AREA
CA5200574 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5200575 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200579 | LPA82 - TEHAMA COUNTY | NC | T - OTHER TRANSIENT AREA
CA5200582 | LPA82 - TEHAMA COUNTY | NC | O - OTHER AREA
CA5200584 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200585 | LPA82 - TEHAMA COUNTY | NC | R - RESIDENTIAL AREA
CA5200586 | LPA82 - TEHAMA COUNTY | NC | T - OTHER TRANSIENT AREA
CA5200588 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200598 | LPA82 - TEHAMA COUNTY | NC | NT - SCHOOL
CA5200600 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200602 | DISTRICT 21 - VALLEY | NC | T - HIGHWAY REST AREA
CA5200603 | DISTRICT 21 - VALLEY | NC | T - HIGHWAY REST AREA
CA5200606 | LPA82 - TEHAMA COUNTY | NC | T - RECREATION AREA
CA5200608 | LPA82 - TEHAMA COUNTY | NC | T - RECREATION AREA
CA5200611 | LPA82 - TEHAMA COUNTY | NC | T - OTHER TRANSIENT AREA
CA5200613 | LPA82 - TEHAMA COUNTY | SSWS | T - RECREATION AREA
CA5200616 | LPA82 - TEHAMA COUNTY | NC | T - OTHER TRANSIENT AREA
CA5200618 | LPA82 - TEHAMA COUNTY | NC | R - RESIDENTIAL AREA
CA5200626 | LPA82 - TEHAMA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5200642 | LPA82 - TEHAMA COUNTY | NC | T - RECREATION AREA
CA5200645 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5200653 | LPA82 - TEHAMA COUNTY | NC | T - RECREATION AREA
CA5200655 | LPA82 - TEHAMA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5200657 | LPA82 - TEHAMA COUNTY | C | R - MOBILE HOME PARK
CA5200670 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA5200672 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA5200688 | LPA82 - TEHAMA COUNTY | NC | T - HOTEL/MOTEL
CA5200710 | LPA82 - TEHAMA COUNTY | NC | T - RETAIL EMPLOYEES
CA5200714 | LPA82 - TEHAMA COUNTY | NC | O - OTHER AREA
CA5200716 | LPA82 - TEHAMA COUNTY | NC | T - RECREATION AREA
CA5200864 | LPA82 - TEHAMA COUNTY | C | R - OTHER RESIDENTIAL AREA
CA5200865 | LPA82 - TEHAMA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5201055 | LPA82 - TEHAMA COUNTY | NTNC | NT - INSTITUTION
CA5201057 | LPA82 - TEHAMA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5201083 | LPA82 - TEHAMA COUNTY | NC | T - RESTAURANT
CA5201127 | LPA82 - TEHAMA COUNTY | NC | T - OTHER TRANSIENT AREA
CA5201140 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5201142 | DISTRICT 21 - VALLEY | NC | T - SECONDARY RESIDENCES
CA5201143 | LPA82 - TEHAMA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5201147 | LPA82 - TEHAMA COUNTY | C | R - RESIDENTIAL AREA
CA5205006 | DISTRICT 21 - VALLEY | NTNC | T - OTHER TRANSIENT AREA
CA5205007 | LPA82 - TEHAMA COUNTY | NTNC | NT - SCHOOL
CA5205009 | DISTRICT 21 - VALLEY | NTNC | NT - INSTITUTION
CA5210001 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5210002 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5210003 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5210004 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5210005 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5210301 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA5210302 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA5210500 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA5210501 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA5210502 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA5210503 | DISTRICT 21 - VALLEY | NTNC | T - RECREATION AREA
CA5210504 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA5210505 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA5210506 | DISTRICT 21 - VALLEY | NC | T - RECREATION AREA
CA5210800 | DISTRICT 21 - VALLEY | NTNC | NT - INSTITUTION
CA5210801 | DISTRICT 21 - VALLEY | NTNC | NT - INSTITUTION
CA5301001 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA5301002 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA5301004 | DISTRICT 01 - KLAMATH | NC | R - RESIDENTIAL AREA
CA5301006 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA5301008 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK
CA5301009 | DISTRICT 01 - KLAMATH | NC | T - HOTEL/MOTEL
CA5301010 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA5301012 | DISTRICT 01 - KLAMATH | NC | R - MOBILE HOME PARK
CA5301013 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA5301014 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA5301017 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA5301101 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA5301102 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA5301103 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA5301104 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA5301105 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA5301106 | DISTRICT 01 - KLAMATH | NC | T - HOTEL/MOTEL
CA5301108 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA5301109 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA5301110 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA5301112 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA5301113 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA5301114 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA5301201 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA5303002 | DISTRICT 01 - KLAMATH | C | R - MOBILE HOME PARK
CA5304102 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA5304105 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA5304109 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA5304113 | DISTRICT 01 - KLAMATH | NC | R - MOBILE HOME PARK
CA5304209 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA5304501 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA5304502 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA5304507 | DISTRICT 01 - KLAMATH | NC | T - HIGHWAY REST AREA
CA5305003 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA5305004 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA5305006 | DISTRICT 01 - KLAMATH | NC | T - HOTEL/MOTEL
CA5305007 | DISTRICT 01 - KLAMATH | C | T - OTHER TRANSIENT AREA
CA5305103 | DISTRICT 01 - KLAMATH | NTNC | R - RESIDENTIAL AREA
CA5305107 | DISTRICT 01 - KLAMATH | NTNC | NT - SCHOOL
CA5305402 | DISTRICT 01 - KLAMATH | NC | T - RECREATION AREA
CA5305504 | DISTRICT 01 - KLAMATH | NC | T - OTHER TRANSIENT AREA
CA5310001 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA5310002 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA5310003 | DISTRICT 01 - KLAMATH | C | R - RESIDENTIAL AREA
CA5310800 | DISTRICT 01 - KLAMATH | NTNC | NT - INSTITUTION
CA5400504 | DISTRICT 24 - TULARE | C | R - MOBILE HOME PARK
CA5400505 | DISTRICT 24 - TULARE | C | T - RECREATION AREA
CA5400506 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400509 | DISTRICT 24 - TULARE | NC | T - OTHER TRANSIENT AREA
CA5400511 | DISTRICT 24 - TULARE | NC | R - MOBILE HOME PARK
CA5400513 | DISTRICT 24 - TULARE | NC | R - RESIDENTIAL AREA
CA5400519 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400523 | DISTRICT 24 - TULARE | C | R - MOBILE HOME PARK
CA5400526 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5400529 | DISTRICT 24 - TULARE | C | R - MOBILE HOME PARK
CA5400536 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400537 | DISTRICT 24 - TULARE | C | T - RECREATION AREA
CA5400538 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400541 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5400542 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400543 | DISTRICT 24 - TULARE | NC | R - RESIDENTIAL AREA
CA5400544 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400548 | DISTRICT 24 - TULARE | NC | T - HOTEL/MOTEL
CA5400549 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400550 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400552 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400553 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5400556 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400558 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400567 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400581 | DISTRICT 24 - TULARE | NC | R - RESIDENTIAL AREA
CA5400583 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400598 | DISTRICT 24 - TULARE | NC | R - RESIDENTIAL AREA
CA5400602 | DISTRICT 24 - TULARE | C | T - RECREATION AREA
CA5400604 | DISTRICT 24 - TULARE | C | R - OTHER RESIDENTIAL AREA
CA5400616 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400620 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400623 | DISTRICT 24 - TULARE | NC | T - HOTEL/MOTEL
CA5400624 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400629 | DISTRICT 24 - TULARE | NC | R - MOBILE HOME PARK
CA5400631 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400636 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400637 | DISTRICT 24 - TULARE | NC | T - HOTEL/MOTEL
CA5400641 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400644 | DISTRICT 24 - TULARE | NC | T - HOTEL/MOTEL
CA5400647 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400655 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400660 | DISTRICT 24 - TULARE | C | R - MOBILE HOME PARK
CA5400665 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5400666 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5400670 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400679 | DISTRICT 24 - TULARE | NC | T - HOTEL/MOTEL
CA5400682 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5400696 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400701 | DISTRICT 24 - TULARE | NC | R - RESIDENTIAL AREA
CA5400703 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400704 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400708 | DISTRICT 24 - TULARE | NC | R - RESIDENTIAL AREA
CA5400709 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400710 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400711 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400713 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400714 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400718 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400722 | DISTRICT 24 - TULARE | NC | T - SECONDARY RESIDENCES
CA5400724 | DISTRICT 24 - TULARE | NC | T - OTHER TRANSIENT AREA
CA5400728 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400732 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400735 | DISTRICT 24 - TULARE | C | R - OTHER RESIDENTIAL AREA
CA5400736 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400737 | DISTRICT 24 - TULARE | NC | NT - INSTITUTION
CA5400738 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400743 | DISTRICT 24 - TULARE | NC | R - MOBILE HOME PARK
CA5400744 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400747 | DISTRICT 24 - TULARE | NC | T - HOTEL/MOTEL
CA5400749 | DISTRICT 24 - TULARE | NC | T - HOTEL/MOTEL
CA5400750 | DISTRICT 24 - TULARE | NC | T - SECONDARY RESIDENCES
CA5400751 | DISTRICT 24 - TULARE | NC | R - MOBILE HOME PARK
CA5400754 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400755 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400756 | DISTRICT 24 - TULARE | NC | T - HOTEL/MOTEL
CA5400757 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400760 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400765 | DISTRICT 24 - TULARE | NC | T - OTHER TRANSIENT AREA
CA5400766 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400767 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5400769 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400774 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400778 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400783 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400792 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400795 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400797 | DISTRICT 24 - TULARE | NTNC | NT - INSTITUTION
CA5400805 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400810 | DISTRICT 24 - TULARE | NC | T - RESTAURANT
CA5400811 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400816 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400819 | DISTRICT 24 - TULARE | C | R - MOBILE HOME PARK
CA5400823 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400824 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400826 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400838 | DISTRICT 24 - TULARE | NTNC | O - OTHER AREA
CA5400844 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400846 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400848 | DISTRICT 24 - TULARE | NC | NT - INSTITUTION
CA5400850 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400863 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400868 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400873 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400875 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400880 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400881 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400882 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400884 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400886 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400887 | DISTRICT 24 - TULARE | NTNC | T - OTHER TRANSIENT AREA
CA5400889 | DISTRICT 24 - TULARE | NC | T - SUMMER CAMP
CA5400890 | DISTRICT 24 - TULARE | NC | T - SUMMER CAMP
CA5400896 | DISTRICT 24 - TULARE | NC | T - SUMMER CAMP
CA5400898 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400903 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400907 | DISTRICT 24 - TULARE | NC | T - RESTAURANT
CA5400916 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400917 | DISTRICT 24 - TULARE | NC | T - SERVICE STATION
CA5400919 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400921 | DISTRICT 24 - TULARE | NC | R - RESIDENTIAL AREA
CA5400922 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400924 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400928 | DISTRICT 24 - TULARE | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5400929 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400934 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400935 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5400940 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400942 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400945 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400951 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5400959 | DISTRICT 24 - TULARE | NC | T - SUMMER CAMP
CA5400961 | DISTRICT 24 - TULARE | NC | T - SUMMER CAMP
CA5400964 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400968 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5400969 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5400972 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5400984 | DISTRICT 24 - TULARE | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5400985 | DISTRICT 24 - TULARE | NC | T - SERVICE STATION
CA5400987 | DISTRICT 24 - TULARE | NC | T - RESTAURANT
CA5400994 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5401001 | DISTRICT 24 - TULARE | NC | T - RESTAURANT
CA5401003 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5401006 | DISTRICT 24 - TULARE | NTNC | NT - INSTITUTION
CA5401010 | DISTRICT 24 - TULARE | NC | T - SUMMER CAMP
CA5401024 | DISTRICT 24 - TULARE | NC | T - HIGHWAY REST AREA
CA5401025 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5401026 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5401033 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5401038 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5401039 | DISTRICT 24 - TULARE | NTNC | NT - INSTITUTION
CA5401044 | DISTRICT 24 - TULARE | NTNC | T - SERVICE STATION
CA5401045 | DISTRICT 24 - TULARE | NC | T - HIGHWAY REST AREA
CA5401047 | DISTRICT 24 - TULARE | NC | T - HIGHWAY REST AREA
CA5401048 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5401049 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5401063 | DISTRICT 24 - TULARE | NC | T - RESTAURANT
CA5401071 | DISTRICT 12 - VISALIA | NC | T - RECREATION AREA
CA5401074 | DISTRICT 24 - TULARE | NTNC | NT - INSTITUTION
CA5401076 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5401082 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5401084 | DISTRICT 24 - TULARE | NC | T - RESTAURANT
CA5401089 | DISTRICT 24 - TULARE | NC | T - SUMMER CAMP
CA5401093 | DISTRICT 24 - TULARE | NC | R - RESIDENTIAL AREA
CA5401094 | DISTRICT 24 - TULARE | NC | T - SERVICE STATION
CA5401099 | DISTRICT 24 - TULARE | NC | T - SUMMER CAMP
CA5402008 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5402013 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5402016 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5402017 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5402019 | DISTRICT 24 - TULARE | NC | T - OTHER TRANSIENT AREA
CA5402022 | DISTRICT 24 - TULARE | NC | T - RESTAURANT
CA5402024 | DISTRICT 24 - TULARE | NC | T - OTHER TRANSIENT AREA
CA5402026 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5402027 | DISTRICT 24 - TULARE | NTNC | T - OTHER TRANSIENT AREA
CA5402030 | DISTRICT 24 - TULARE | NC | T - OTHER TRANSIENT AREA
CA5402031 | DISTRICT 24 - TULARE | NC | T - SERVICE STATION
CA5402036 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5402037 | DISTRICT 24 - TULARE | NC | NT - INSTITUTION
CA5402038 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5402041 | DISTRICT 24 - TULARE | NC | T - HOTEL/MOTEL
CA5402046 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5402047 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5402048 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5402050 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5402056 | DISTRICT 24 - TULARE | NC | T - OTHER TRANSIENT AREA
CA5402057 | DISTRICT 24 - TULARE | NC | R - MOBILE HOME PARK
CA5403001 | DISTRICT 24 - TULARE | NC | T - RESTAURANT
CA5403007 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403011 | DISTRICT 24 - TULARE | NC | T - RESTAURANT
CA5403020 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5403022 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403023 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5403025 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5403026 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5403027 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5403031 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403032 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403039 | DISTRICT 24 - TULARE | NC | R - RESIDENTIAL AREA
CA5403041 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403042 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403043 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5403046 | DISTRICT 24 - TULARE | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5403047 | DISTRICT 24 - TULARE | NC | R - RESIDENTIAL AREA
CA5403048 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403049 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5403050 | DISTRICT 24 - TULARE | NTNC | T - OTHER TRANSIENT AREA
CA5403051 | DISTRICT 24 - TULARE | NC | R - MOBILE HOME PARK
CA5403053 | DISTRICT 24 - TULARE | NC | T - SERVICE STATION
CA5403054 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403055 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403061 | DISTRICT 24 - TULARE | NC | T - RESTAURANT
CA5403062 | DISTRICT 24 - TULARE | NC | T - HOTEL/MOTEL
CA5403072 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5403073 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5403074 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403080 | DISTRICT 24 - TULARE | NTNC | T - OTHER TRANSIENT AREA
CA5403081 | DISTRICT 24 - TULARE | NTNC | T - OTHER TRANSIENT AREA
CA5403082 | DISTRICT 24 - TULARE | NC | T - OTHER TRANSIENT AREA
CA5403083 | DISTRICT 24 - TULARE | NTNC | T - OTHER TRANSIENT AREA
CA5403084 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5403088 | DISTRICT 24 - TULARE | NC | T - OTHER TRANSIENT AREA
CA5403089 | DISTRICT 24 - TULARE | NC | T - RESTAURANT
CA5403090 | DISTRICT 24 - TULARE | NC | T - RESTAURANT
CA5403102 | DISTRICT 24 - TULARE | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5403105 | DISTRICT 24 - TULARE | NC | T - RESTAURANT
CA5403106 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403109 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5403110 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5403113 | DISTRICT 24 - TULARE | C | R - OTHER RESIDENTIAL AREA
CA5403114 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403116 | DISTRICT 24 - TULARE | NC | T - HOTEL/MOTEL
CA5403118 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403119 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403120 | DISTRICT 24 - TULARE | NC | T - RESTAURANT
CA5403121 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403122 | DISTRICT 24 - TULARE | NC | T - SERVICE STATION
CA5403126 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5403127 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403130 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5403131 | DISTRICT 24 - TULARE | NTNC | NT - DAY CARE CENTER
CA5403132 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403135 | DISTRICT 24 - TULARE | NC | R - RESIDENTIAL AREA
CA5403137 | DISTRICT 24 - TULARE | NC | T - RECREATION AREA
CA5403138 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403139 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403140 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403141 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403144 | DISTRICT 24 - TULARE | C | T - SERVICE STATION
CA5403145 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403146 | DISTRICT 24 - TULARE | NTNC | NT - SCHOOL
CA5403147 | DISTRICT 24 - TULARE | NC | T - OTHER TRANSIENT AREA
CA5403148 | DISTRICT 24 - TULARE | NTNC | NT - INSTITUTION
CA5403150 | DISTRICT 24 - TULARE | NC | T - OTHER TRANSIENT AREA
CA5403151 | DISTRICT 24 - TULARE | NC | T - SERVICE STATION
CA5403152 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403153 | DISTRICT 24 - TULARE | NC | T - OTHER TRANSIENT AREA
CA5403154 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403156 | DISTRICT 24 - TULARE | NC | T - OTHER TRANSIENT AREA
CA5403159 | DISTRICT 24 - TULARE | NC | T - OTHER TRANSIENT AREA
CA5403200 | DISTRICT 24 - TULARE | NC | T - RESTAURANT
CA5403201 | DISTRICT 24 - TULARE | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5403204 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403205 | DISTRICT 24 - TULARE | NTNC | O - OTHER AREA
CA5403206 | DISTRICT 24 - TULARE | NTNC | NT - OTHER NON-TRANSIENT AREA
CA5403207 | DISTRICT 24 - TULARE | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5403208 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403211 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403212 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5403213 | DISTRICT 24 - TULARE | C | NT - INSTITUTION
CA5403214 | DISTRICT 24 - TULARE | NC | T - OTHER TRANSIENT AREA
CA5403215 | DISTRICT 24 - TULARE | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5403217 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5403218 | DISTRICT 24 - TULARE | NC | T - OTHER TRANSIENT AREA
CA5403219 | DISTRICT 24 - TULARE | NC | T - SERVICE STATION
CA5410001 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5410002 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5410003 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5410004 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5410006 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5410007 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5410008 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5410009 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5410010 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5410011 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5410012 | DISTRICT 12 - VISALIA | C | O - WHOLESALER (SELLS WATER)
CA5410014 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5410015 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5410016 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5410017 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5410019 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5410020 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5410021 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5410022 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5410024 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5410025 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5410026 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5410034 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5410036 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5410038 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5410039 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5410041 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5410048 | DISTRICT 24 - TULARE | C | R - RESIDENTIAL AREA
CA5410050 | DISTRICT 12 - VISALIA | C | R - RESIDENTIAL AREA
CA5410503 | DISTRICT 12 - VISALIA | C | T - RECREATION AREA
CA5410510 | DISTRICT 12 - VISALIA | NC | T - RECREATION AREA
CA5410511 | DISTRICT 12 - VISALIA | NC | T - RECREATION AREA
CA5410512 | DISTRICT 12 - VISALIA | NC | T - RECREATION AREA
CA5410513 | DISTRICT 12 - VISALIA | C | T - RECREATION AREA
CA5410515 | DISTRICT 12 - VISALIA | NC | T - RECREATION AREA
CA5410517 | DISTRICT 12 - VISALIA | NC | T - RECREATION AREA
CA5410519 | DISTRICT 12 - VISALIA | NC | T - RECREATION AREA
CA5410520 | DISTRICT 12 - VISALIA | NC | T - RECREATION AREA
CA5410800 | DISTRICT 24 - TULARE | C | NT - INSTITUTION
CA5410801 | DISTRICT 24 - TULARE | C | NT - INSTITUTION
CA5500001 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500003 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500005 | DISTRICT 11 - MERCED | NC | T - RESTAURANT
CA5500010 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500013 | DISTRICT 11 - MERCED | NC | T - SECONDARY RESIDENCES
CA5500016 | DISTRICT 11 - MERCED | NTNC | O - OTHER AREA
CA5500019 | DISTRICT 11 - MERCED | C | T - OTHER TRANSIENT AREA
CA5500020 | DISTRICT 11 - MERCED | NC | T - SUMMER CAMP
CA5500026 | DISTRICT 11 - MERCED | NC | T - SUMMER CAMP
CA5500027 | DISTRICT 11 - MERCED | NC | T - SECONDARY RESIDENCES
CA5500030 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500031 | DISTRICT 11 - MERCED | NC | T - SUMMER CAMP
CA5500040 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5500041 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5500042 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5500048 | DISTRICT 11 - MERCED | C | T - RECREATION AREA
CA5500049 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA5500053 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5500054 | DISTRICT 11 - MERCED | NC | R - OTHER RESIDENTIAL AREA
CA5500057 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5500060 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5500064 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5500071 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5500074 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5500077 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5500080 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5500086 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA5500089 | DISTRICT 11 - MERCED | NTNC | T - HOTEL/MOTEL
CA5500090 | DISTRICT 11 - MERCED | NC | T - RESTAURANT
CA5500092 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA5500096 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA5500102 | DISTRICT 11 - MERCED | NC | T - SERVICE STATION
CA5500104 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA5500109 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA5500112 | DISTRICT 11 - MERCED | NC | T - SUMMER CAMP
CA5500113 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA5500115 | DISTRICT 11 - MERCED | C | T - OTHER TRANSIENT AREA
CA5500116 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA5500119 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5500120 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA5500124 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA5500125 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA5500128 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA5500132 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA5500138 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500141 | DISTRICT 11 - MERCED | NC | T - SUMMER CAMP
CA5500145 | DISTRICT 11 - MERCED | NC | T - SUMMER CAMP
CA5500148 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA5500149 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA5500151 | DISTRICT 11 - MERCED | NC | T - SUMMER CAMP
CA5500152 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA5500160 | DISTRICT 11 - MERCED | NC | T - HOTEL/MOTEL
CA5500168 | DISTRICT 11 - MERCED | NTNC | T - RECREATION AREA
CA5500171 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA5500173 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500175 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500176 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500178 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500179 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500181 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA5500182 | DISTRICT 11 - MERCED | NC | R - RESIDENTIAL AREA
CA5500186 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500191 | DISTRICT 11 - MERCED | NC | R - OTHER RESIDENTIAL AREA
CA5500193 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA5500194 | DISTRICT 11 - MERCED | NC | T - RESTAURANT
CA5500201 | DISTRICT 11 - MERCED | NC | T - RESTAURANT
CA5500208 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500210 | DISTRICT 11 - MERCED | NC | T - RESTAURANT
CA5500213 | DISTRICT 11 - MERCED | NC | T - RESTAURANT
CA5500221 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA5500233 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA5500237 | DISTRICT 11 - MERCED | NC | T - HOTEL/MOTEL
CA5500242 | DISTRICT 11 - MERCED | NTNC | NT - SCHOOL
CA5500243 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA5500245 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500248 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500250 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500253 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500258 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA5500259 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5500263 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500265 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500266 | DISTRICT 11 - MERCED | NC | T - RESTAURANT
CA5500268 | DISTRICT 11 - MERCED | NC | O - OTHER AREA
CA5500269 | DISTRICT 11 - MERCED | NC | T - RESTAURANT
CA5500272 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500274 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500353 | DISTRICT 11 - MERCED | C | R - MOBILE HOME PARK
CA5500358 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5500359 | DISTRICT 11 - MERCED | NC | T - SUMMER CAMP
CA5500360 | DISTRICT 11 - MERCED | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5500363 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5500364 | DISTRICT 11 - MERCED | NC | T - OTHER TRANSIENT AREA
CA5500368 | DISTRICT 11 - MERCED | NC | T - SUMMER CAMP
CA5500369 | DISTRICT 11 - MERCED | NTNC | T - HOTEL/MOTEL
CA5510001 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510002 | DISTRICT 11 - MERCED | C | O - WHOLESALER (SELLS WATER)
CA5510003 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510004 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510005 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510006 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510007 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510008 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510009 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510011 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510012 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510013 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510015 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510016 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510021 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510023 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510024 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510025 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510026 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510028 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510033 | DISTRICT 11 - MERCED | C | R - RESIDENTIAL AREA
CA5510500 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5510503 | DISTRICT 11 - MERCED | C | T - RECREATION AREA
CA5510504 | DISTRICT 11 - MERCED | NC | T - RECREATION AREA
CA5510851 | DISTRICT 11 - MERCED | C | NT - INSTITUTION
CA5510852 | DISTRICT 11 - MERCED | C | NT - INSTITUTION
CA5601104 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5601105 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5601106 | DISTRICT 06 - SANTA BARBARA | C | R - MOBILE HOME PARK
CA5601110 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5601116 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5601117 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5601119 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5601120 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5601122 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5601125 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5601134 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5601135 | DISTRICT 06 - SANTA BARBARA | NTNC | R - RESIDENTIAL AREA
CA5601137 | DISTRICT 06 - SANTA BARBARA | C | NT - INDUSTRIAL/AGRICULTURAL
CA5601139 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - SCHOOL
CA5601141 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5601144 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5601201 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5601301 | DISTRICT 06 - SANTA BARBARA | NC | T - SUMMER CAMP
CA5601306 | DISTRICT 06 - SANTA BARBARA | NC | T - OTHER TRANSIENT AREA
CA5601401 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5601405 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - SCHOOL
CA5601605 | DISTRICT 06 - SANTA BARBARA | NC | T - RESTAURANT
CA5601701 | DISTRICT 06 - SANTA BARBARA | NC | T - OTHER TRANSIENT AREA
CA5601706 | DISTRICT 06 - SANTA BARBARA | NC | T - RECREATION AREA
CA5601716 | DISTRICT 06 - SANTA BARBARA | NC | T - OTHER TRANSIENT AREA
CA5601721 | DISTRICT 06 - SANTA BARBARA | NTNC | T - OTHER TRANSIENT AREA
CA5601725 | DISTRICT 06 - SANTA BARBARA | NC | T - RECREATION AREA
CA5602101 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5602103 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5602104 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5602108 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5602109 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5602110 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5602111 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5602115 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5602117 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5602120 | DISTRICT 06 - SANTA BARBARA | NTNC | R - RESIDENTIAL AREA
CA5602130 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5602132 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5602133 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5602140 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5602301 | DISTRICT 15 - METROPOLITAN | NC | T - OTHER TRANSIENT AREA
CA5602302 | DISTRICT 06 - SANTA BARBARA | NTNC | T - SUMMER CAMP
CA5602403 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - SCHOOL
CA5602406 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - SCHOOL
CA5602407 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - SCHOOL
CA5602408 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - SCHOOL
CA5602512 | DISTRICT 06 - SANTA BARBARA | NC | O - OTHER AREA
CA5602513 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5602514 | DISTRICT 06 - SANTA BARBARA | NTNC | O - OTHER AREA
CA5602516 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5602656 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5603116 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5603117 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5603118 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5603122 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5603123 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5603124 | DISTRICT 06 - SANTA BARBARA | NC | T - SUMMER CAMP
CA5603125 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5603301 | DISTRICT 06 - SANTA BARBARA | NTNC | NT - INSTITUTION
CA5610001 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610002 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610003 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610005 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610006 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610007 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610008 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610009 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610010 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610011 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610014 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610015 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610016 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610017 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610018 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610019 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610020 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610021 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610022 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610023 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610024 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610029 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610035 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610039 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610040 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610043 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610046 | DISTRICT 06 - SANTA BARBARA | C | O - WHOLESALER (SELLS WATER)
CA5610050 | DISTRICT 06 - SANTA BARBARA | C | O - WHOLESALER (SELLS WATER)
CA5610056 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610058 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610059 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610063 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610068 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610069 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610080 | DISTRICT 06 - SANTA BARBARA | C | O - WHOLESALER (SELLS WATER)
CA5610081 | DISTRICT 06 - SANTA BARBARA | C | R - RESIDENTIAL AREA
CA5610500 | DISTRICT 06 - SANTA BARBARA | NC | T - RECREATION AREA
CA5610700 | DISTRICT 06 - SANTA BARBARA | C | R - OTHER RESIDENTIAL AREA
CA5610701 | DISTRICT 06 - SANTA BARBARA | C | R - OTHER RESIDENTIAL AREA
CA5610702 | DISTRICT 06 - SANTA BARBARA | C | R - OTHER RESIDENTIAL AREA
CA5700504 | LPA87 - YOLO COUNTY | NC | T - HOTEL/MOTEL
CA5700506 | LPA87 - YOLO COUNTY | NC | T - RESTAURANT
CA5700508 | LPA87 - YOLO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5700509 | LPA87 - YOLO COUNTY | NTNC | NT - SCHOOL
CA5700510 | LPA87 - YOLO COUNTY | NTNC | NT - SCHOOL
CA5700514 | LPA87 - YOLO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5700516 | LPA87 - YOLO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5700518 | LPA87 - YOLO COUNTY | NC | T - OTHER TRANSIENT AREA
CA5700521 | LPA87 - YOLO COUNTY | NC | T - RESTAURANT
CA5700522 | LPA87 - YOLO COUNTY | NC | T - OTHER TRANSIENT AREA
CA5700523 | LPA87 - YOLO COUNTY | NC | T - RESTAURANT
CA5700528 | LPA87 - YOLO COUNTY | NC | T - OTHER TRANSIENT AREA
CA5700532 | LPA87 - YOLO COUNTY | NC | O - OTHER AREA
CA5700537 | LPA87 - YOLO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5700539 | LPA87 - YOLO COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA5700542 | LPA87 - YOLO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5700543 | LPA87 - YOLO COUNTY | NC | T - RESTAURANT
CA5700552 | LPA87 - YOLO COUNTY | NTNC | T - RESTAURANT
CA5700553 | LPA87 - YOLO COUNTY | NC | T - OTHER TRANSIENT AREA
CA5700554 | LPA87 - YOLO COUNTY | C | R - MOBILE HOME PARK
CA5700555 | LPA87 - YOLO COUNTY | C | T - HOTEL/MOTEL
CA5700556 | DISTRICT 09 - SACRAMENTO | NC | T - HIGHWAY REST AREA
CA5700562 | LPA87 - YOLO COUNTY | NC | T - RESTAURANT
CA5700568 | LPA87 - YOLO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5700571 | LPA87 - YOLO COUNTY | C | R - RESIDENTIAL AREA
CA5700575 | LPA87 - YOLO COUNTY | NC | T - RESTAURANT
CA5700584 | LPA87 - YOLO COUNTY | NC | R - MOBILE HOME PARK
CA5700588 | LPA87 - YOLO COUNTY | NC | T - RECREATION AREA
CA5700597 | LPA87 - YOLO COUNTY | NC | T - RESTAURANT
CA5700608 | DISTRICT 09 - SACRAMENTO | NC | T - RECREATION AREA
CA5700615 | LPA87 - YOLO COUNTY | C | R - RESIDENTIAL AREA
CA5700616 | LPA87 - YOLO COUNTY | NC | T - HOTEL/MOTEL
CA5700617 | LPA87 - YOLO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5700618 | LPA87 - YOLO COUNTY | NC | T - RESTAURANT
CA5700623 | LPA87 - YOLO COUNTY | NTNC | NT - SCHOOL
CA5700636 | LPA87 - YOLO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5700642 | LPA87 - YOLO COUNTY | NC | T - RESTAURANT
CA5700643 | LPA87 - YOLO COUNTY | NTNC | NT - SCHOOL
CA5700652 | LPA87 - YOLO COUNTY | NTNC | T - RESTAURANT
CA5700653 | LPA87 - YOLO COUNTY | NC | T - RECREATION AREA
CA5700673 | LPA87 - YOLO COUNTY | NC | T - RESTAURANT
CA5700700 | LPA87 - YOLO COUNTY | C | R - RESIDENTIAL AREA
CA5700701 | LPA87 - YOLO COUNTY | NC | T - OTHER TRANSIENT AREA
CA5700702 | LPA87 - YOLO COUNTY | NTNC | NT - SCHOOL
CA5700707 | LPA87 - YOLO COUNTY | C | R - RESIDENTIAL AREA
CA5700712 | LPA87 - YOLO COUNTY | C | R - MOBILE HOME PARK
CA5700713 | LPA87 - YOLO COUNTY | NC | T - RECREATION AREA
CA5700714 | LPA87 - YOLO COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA5700720 | LPA87 - YOLO COUNTY | SSWS | R - MOBILE HOME PARK
CA5700722 | LPA87 - YOLO COUNTY | SSWS | R - RESIDENTIAL AREA
CA5700723 | LPA87 - YOLO COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA5700728 | LPA87 - YOLO COUNTY | NC | T - RESTAURANT
CA5700729 | LPA87 - YOLO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5700730 | LPA87 - YOLO COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA5700734 | LPA87 - YOLO COUNTY | NC | O - OTHER AREA
CA5700737 | LPA87 - YOLO COUNTY | NC | R - RESIDENTIAL AREA
CA5700748 | LPA87 - YOLO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5700751 | LPA87 - YOLO COUNTY | NC | T - SERVICE STATION
CA5700754 | LPA87 - YOLO COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA5700756 | LPA87 - YOLO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5700757 | LPA87 - YOLO COUNTY | NC | T - RECREATION AREA
CA5700761 | LPA87 - YOLO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5700763 | LPA87 - YOLO COUNTY | NC | T - RECREATION AREA
CA5700764 | LPA87 - YOLO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5700769 | LPA87 - YOLO COUNTY | LSS | T - RESTAURANT
CA5700773 | LPA87 - YOLO COUNTY | NTNC | NT - INSTITUTION
CA5700774 | LPA87 - YOLO COUNTY | NC | T - RECREATION AREA
CA5700778 | LPA87 - YOLO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5700784 | LPA87 - YOLO COUNTY | NTNC | T - OTHER TRANSIENT AREA
CA5700785 | LPA87 - YOLO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5700788 | LPA87 - YOLO COUNTY | C | R - RESIDENTIAL AREA
CA5700791 | LPA87 - YOLO COUNTY | NC | T - OTHER TRANSIENT AREA
CA5700795 | LPA87 - YOLO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5700797 | LPA87 - YOLO COUNTY | C | NT - INSTITUTION
CA5700798 | LPA87 - YOLO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5700802 | LPA87 - YOLO COUNTY | NC | T - RECREATION AREA
CA5700804 | LPA87 - YOLO COUNTY | NC | T - OTHER TRANSIENT AREA
CA5700815 | LPA87 - YOLO COUNTY | NC | T - RESTAURANT
CA5700816 | LPA87 - YOLO COUNTY | NC | T - OTHER TRANSIENT AREA
CA5700817 | LPA87 - YOLO COUNTY | NC | T - OTHER TRANSIENT AREA
CA5700820 | LPA87 - YOLO COUNTY | NC | T - OTHER TRANSIENT AREA
CA5700821 | LPA87 - YOLO COUNTY | NC | T - OTHER TRANSIENT AREA
CA5700827 | LPA87 - YOLO COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5700828 | LPA87 - YOLO COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5700829 | LPA87 - YOLO COUNTY | SSWS | R - RESIDENTIAL AREA
CA5710001 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA5710003 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA5710004 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA5710005 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA5710006 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA5710007 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA5710009 | DISTRICT 09 - SACRAMENTO | C | NT - SCHOOL
CA5710011 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA5710012 | DISTRICT 09 - SACRAMENTO | C | O - WHOLESALER (SELLS WATER)
CA5710013 | DISTRICT 09 - SACRAMENTO | NTNC | NT - MEDICAL FACILITY
CA5800001 | LPA88 - YUBA COUNTY | NC | T - SERVICE STATION
CA5800002 | LPA88 - YUBA COUNTY | NC | T - OTHER TRANSIENT AREA
CA5800003 | LPA88 - YUBA COUNTY | NC | T - RECREATION AREA
CA5800004 | LPA88 - YUBA COUNTY | NC | NT - INDUSTRIAL/AGRICULTURAL
CA5800006 | LPA88 - YUBA COUNTY | NTNC | NT - SCHOOL
CA5800009 | LPA88 - YUBA COUNTY | NC | T - OTHER TRANSIENT AREA
CA5800010 | LPA88 - YUBA COUNTY | NC | T - OTHER TRANSIENT AREA
CA5800014 | LPA88 - YUBA COUNTY | NC | T - OTHER TRANSIENT AREA
CA5800202 | LPA88 - YUBA COUNTY | NC | T - RESTAURANT
CA5800205 | LPA88 - YUBA COUNTY | NC | T - RESTAURANT
CA5800572 | LPA88 - YUBA COUNTY | C | R - RESIDENTIAL AREA
CA5800576 | LPA88 - YUBA COUNTY | NC | T - SERVICE STATION
CA5800800 | LPA88 - YUBA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5800801 | LPA88 - YUBA COUNTY | NC | T - RECREATION AREA
CA5800803 | LPA88 - YUBA COUNTY | C | R - RESIDENTIAL AREA
CA5800805 | LPA88 - YUBA COUNTY | C | R - RESIDENTIAL AREA
CA5800809 | LPA88 - YUBA COUNTY | NTNC | T - RECREATION AREA
CA5800812 | LPA88 - YUBA COUNTY | SSWS | R - OTHER RESIDENTIAL AREA
CA5800814 | LPA88 - YUBA COUNTY | NC | T - RECREATION AREA
CA5800820 | LPA88 - YUBA COUNTY | C | R - RESIDENTIAL AREA
CA5800821 | LPA88 - YUBA COUNTY | C | R - MOBILE HOME PARK
CA5800823 | LPA88 - YUBA COUNTY | C | R - MOBILE HOME PARK
CA5800824 | LPA88 - YUBA COUNTY | C | R - MOBILE HOME PARK
CA5800826 | LPA88 - YUBA COUNTY | NC | R - MOBILE HOME PARK
CA5800827 | LPA88 - YUBA COUNTY | C | R - MOBILE HOME PARK
CA5800828 | LPA88 - YUBA COUNTY | C | R - MOBILE HOME PARK
CA5800829 | LPA88 - YUBA COUNTY | NC | T - RECREATION AREA
CA5800831 | LPA88 - YUBA COUNTY | NC | T - SUMMER CAMP
CA5800832 | LPA88 - YUBA COUNTY | C | R - MOBILE HOME PARK
CA5800838 | LPA88 - YUBA COUNTY | NC | T - SUMMER CAMP
CA5800840 | LPA88 - YUBA COUNTY | NTNC | NT - SCHOOL
CA5800843 | LPA88 - YUBA COUNTY | NTNC | NT - SCHOOL
CA5800844 | LPA88 - YUBA COUNTY | NTNC | NT - SCHOOL
CA5800845 | LPA88 - YUBA COUNTY | NTNC | NT - SCHOOL
CA5800847 | LPA88 - YUBA COUNTY | NTNC | NT - SCHOOL
CA5800849 | LPA88 - YUBA COUNTY | NC | T - OTHER TRANSIENT AREA
CA5800850 | LPA88 - YUBA COUNTY | C | R - MOBILE HOME PARK
CA5800851 | LPA88 - YUBA COUNTY | C | NT - INSTITUTION
CA5800853 | LPA88 - YUBA COUNTY | NC | T - RECREATION AREA
CA5800858 | LPA88 - YUBA COUNTY | NC | T - RESTAURANT
CA5800863 | LPA88 - YUBA COUNTY | C | T - SECONDARY RESIDENCES
CA5800866 | LPA88 - YUBA COUNTY | NC | T - RECREATION AREA
CA5800868 | LPA88 - YUBA COUNTY | NC | T - SERVICE STATION
CA5800874 | LPA88 - YUBA COUNTY | NC | T - OTHER TRANSIENT AREA
CA5800875 | LPA88 - YUBA COUNTY | NC | T - RESTAURANT
CA5800876 | LPA88 - YUBA COUNTY | NC | T - OTHER TRANSIENT AREA
CA5800883 | LPA88 - YUBA COUNTY | SSWS | R - MOBILE HOME PARK
CA5800884 | LPA88 - YUBA COUNTY | NC | T - SUMMER CAMP
CA5800886 | LPA88 - YUBA COUNTY | SSWS | R - MOBILE HOME PARK
CA5800887 | LPA88 - YUBA COUNTY | NC | T - RESTAURANT
CA5800888 | LPA88 - YUBA COUNTY | NC | T - RESTAURANT
CA5800892 | LPA88 - YUBA COUNTY | SSWS | R - RESIDENTIAL AREA
CA5800893 | LPA88 - YUBA COUNTY | NC | T - SUMMER CAMP
CA5800897 | LPA88 - YUBA COUNTY | NC | T - OTHER TRANSIENT AREA
CA5800899 | LPA88 - YUBA COUNTY | NTNC | T - SECONDARY RESIDENCES
CA5800901 | LPA88 - YUBA COUNTY | NC | T - RESTAURANT
CA5800909 | LPA88 - YUBA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5800913 | LPA88 - YUBA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5800914 | LPA88 - YUBA COUNTY | NC | T - OTHER TRANSIENT AREA
CA5800919 | LPA88 - YUBA COUNTY | NTNC | NT - INDUSTRIAL/AGRICULTURAL
CA5800920 | LPA88 - YUBA COUNTY | NC | T - RECREATION AREA
CA5800923 | LPA88 - YUBA COUNTY | NC | T - OTHER TRANSIENT AREA
CA5800924 | LPA88 - YUBA COUNTY | C | R - RESIDENTIAL AREA
CA5805001 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5810001 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5810002 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5810003 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5810004 | DISTRICT 21 - VALLEY | C | O - OTHER AREA
CA5810005 | DISTRICT 09 - SACRAMENTO | C | R - RESIDENTIAL AREA
CA5810006 | DISTRICT 21 - VALLEY | C | R - RESIDENTIAL AREA
CA5810700 | DISTRICT 21 - VALLEY | C | NT - INSTITUTION