Public water system:							ID No.:

Name of source:						ID No.:

Assessment date:		Assessment conducted by

Water System Contact Name:						Phone #:

Water System Contact Address:

The following information should be contained in the drinking water source assessment submittal.

Delineation of groundwater protection zones

Well Data Sheet

Possible Contaminating Activities (PCA) inventory form

Assessment map with source location and protection zone

Additional maps (optional) (e.g. local maps of zones and PCAs, recharge area maps, or maps indicating direction of ground water flow)

Means of Public Availability of Report (indicate those that will be used)

Notice in the Consumer Confidence Report* (minimum)

Copy in regulatory agency (CDPH or LPA) office (minimum)

Copy in public water system office (recommended)

Copy in public library/libraries

Internet (indicate Internet address:  __________________________)

Other (describe)

*The CCR should indicate where customers can review the assessments.

Delineation of Ground Water Protection Zones

# Procedures

Three zones are delineated around a well (see specific guidance for springs and horizontal wells), using the Calculated Fixed Radius method.  The default shape of these zones is circular and the radius of the zones is based on the Time of Travel (TOT) of water from a point in the aquifer to the well.  The three zones are defined as:

Zone A 	(2 year TOT)

Zone B5 	(5 year TOT)

Zone B10 	(10 year TOT)

For porous media aquifers (consisting primarily of rocks, sands, gravels and clays), the radius also considers the pumping rate of the well (Q in gallons per minute), the screened interval of the well (H in feet), and the effective porosity of the aquifer ( - assumed to be 0.2).  For fractured rock aquifers, the procedures are the same, but the radius of the zones is increased by 50%.

There are more complicated methods for determining the size, shape and location of zones.  Water systems interested in these methods should consult with a hydrogeologist or other knowledgeable professional.

The following table has been developed to assist water systems and regulators in determining the procedures to use in delineating protection zones.

## TABLE 1

| Aquifer Media | Type of System | Pumping Rate (Q gpm) | Radius Zone A (R2 feet) | Radius Zone B5 (R5 feet) | Radius Zone B10 (R10 feet) |
| --- | --- | --- | --- | --- | --- |
| Porous Media |  |  | 600’min. | 1,000’min. | 1,500’min. |
|  | Transient Noncommunity | Any | 600’ | ----- | ----- |
|  | Non-Transient Noncommunity | 0 to 100 gpm | Calculate or Refer to Table 2 |  |  |
|  | Non-Transient Noncommunity | > 100 gpm | Calculate |  |  |
|  | Community | 0 to 100 gpm | Calculate or Refer to Table 2 |  |  |
|  | Community | > 100 gpm | Calculate |  |  |
| Fractured Rock |  |  | 900’min. | 1,500’min. | 2,250 min. |
|  | Transient Noncommunity | Any | 900’ | ----- | ----- |
|  | Non-Transient Noncommunity | 0 to 100 gpm | Calculate or Refer to Table 3 |  |  |
|  | Non-Transient Noncommunity | > 100 gpm | Calculate |  |  |
|  | Community | 0 to 100 gpm | Calculate or Refer to Table 3 |  |  |
|  | Community | > 100 gpm | Contact CDPH* |  |  |

Delineation of Ground Water Protection Zones

Public water system:						ID No.:

Name of source:						ID No.:

Delineation date:______________Delineation conducted by _____________________________

### Equation

Porous Media Aquifers

RT=QTπηH

Fractured Rock Aquifers

RT=1.5×QTπηH

RT = Radius (in feet) of zone for Time of Travel T

T  = Time of Travel (years) (2, 5, or 10 years)

Q = Pumping capacity of well (in ft3/year) 
       (ft3/year = gpm x 70,267)

 = 3.1416

 = Aquifer effective porosity (default = 0.2)

H = Well screened interval (in feet) (10’ min.)

### Calculations

Aquifer Material (select one) 		Porous Media		Fractured Rock

Pumping Rate		Q = 		gpm  (if unknown use Table 2 or Table 3)

Screened Interval	H =		feet  (if unknown assume 10%Q or use Table 2 or Table 3)

### Porous Media Aquifer

| Zone | TOT (years) | Equation | Use one or the other |  | Minimum | Value (use larger) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Calculated Radius | Table 2 Radius |  |  |
| A | 2 | 473Qgpm/Hft |  |  | 600 |  |
| B5 | 5 | 748Qgpm/Hft |  |  | 1,000 |  |
| B10 | 10 | 1058Qgpm/Hft |  |  | 1,500 |  |

Fractured Rock Aquifer  (Increase size of zones by 50%)

| Zone | TOT (years) | Equation | Use one or the other |  | Minimum | Value |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Calculated Radius | Table 3 Radius |  |  |
| A | 2 | 709Qgpm/Hft |  |  | 900 |  |
| B5 | 5 | 1122Qgpm/Hft |  |  | 1,500 |  |
| B10 | 10 | 1586Qgpm/Hft |  |  | 2,250 |  |

##### DEFAULT PROTECTION ZONES

##### POROUS MEDIA AQUIFERS

##### TABLE 2

| Q | H (feet) (default minimum) | Radius Zone A (feet) | Radius Zone B5 (feet) | Radius Zone B10 (feet) |
| --- | --- | --- | --- | --- |
| < 10 gpm | 10 | 600 | 1,000 | 1,500 |
| 10 to 20 gpm | 10 | 669 | 1,056 | 1,500 |
| 21 to 30 gpm | 10 | 819 | 1,295 | 1,832 |
| 31 to 40 gpm | 10 | 946 | 1,496 | 2,115 |
| 41 to 50 gpm | 10 | 1,058 | 1,672 | 2,365 |
| 51 to 60 gpm | 10 | 1,158 | 1,832 | 2,590 |
| 61 to 70 gpm | 10 | 1,251 | 1,978 | 2,798 |
| 71 to 80 gpm | 10 | 1,338 | 2,115 | 2,991 |
| 81 to 90 gpm | 10 | 1,419 | 2,243 | 3,173 |
| 91 to 100 gpm | 10 | 1,496 | 2,365 | 3,344 |

FRACTURED ROCK AQUIFERS

TABLE 3

| Q | H (feet) (default minimum) | Radius Zone A (feet) | Radius Zone B5 (feet) | Radius Zone B10 (feet) |
| --- | --- | --- | --- | --- |
| < 10 gpm | 10 | 900 | 1,500 | 2,250 |
| 10 to 20 gpm | 10 | 1,003 | 1,587 | 2,250 |
| 21 to 30 gpm | 10 | 1,228 | 1,943 | 2,747 |
| 31 to 40 gpm | 10 | 1,418 | 2,244 | 3,172 |
| 41 to 50 gpm | 10 | 1,585 | 2,509 | 3,546 |
| 51 to 60 gpm | 10 | 1,737 | 2,748 | 3,885 |
| 61 to 70 gpm | 10 | 1,876 | 2,968 | 4,196 |
| 71 to 80 gpm | 10 | 2,005 | 3,173 | 4,486 |
| 81 to 90 gpm | 10 | 2,127 | 3,366 | 4,758 |
| 91 to 100 gpm | 10 | 2,242 | 3,548 | 5,015 |

| WELL DATA SHEET Sheet 1 of 3 |  |  |
| --- | --- | --- |
| Complete as much information as possible. Leave blank if information is not available, use N.A. if not applicable. |  |  |
| * Indicates items required for Source Water Assessment |  |  |
| ** Indicates additional items required for assessments and Ground Water Rule |  |  |
|  | (separate multiple entries in field with semi-colon) | Actual, Estimated or Default? |
| DATA SHEET GENERAL INFORMATION |  |  |
| System Name |  |  |
| System Number |  |  |
| Source of Information (well log, CDPH/County files, system, etc) |  |  |
| Organization Collecting Information (CDPH, County, System, other) |  |  |
| Date Information Collected/Updated |  |  |
| WELL IDENTIFICATION |  |  |
| * Well Number or Name |  |  |
| * CDPH Source Identification Number (FRDS ID No.) |  |  |
| DWR Well Log on File? ("YES" or "NO") |  |  |
| State Well Number (from DWR) |  |  |
| Well Status (Active, Standby, Inactive) |  |  |
| WELL LOCATION |  |  |
| Latitude |  |  |
| Longitude |  |  |
| Ground Surface Elevation (ft above Mean Sea Level) |  |  |
| Street Address |  |  |
| Nearest Cross Street |  |  |
| City |  |  |
| County |  |  |
| * Neighborhood/Surrounding Area (see Note 1) |  |  |
| Site plan on file? ("YES" or "NO") |  |  |
| DWR Ground Water Basin |  |  |
| DWR Ground Water Sub-basin |  |  |
| SANITARY CONDITIONS |  |  |
| ** Distance to closest Sewer Line, Sewage Disposal, Septic Tank (ft) |  |  |
| Distance to Active Wells (ft) |  |  |
| Distance to Abandoned Wells (ft) |  |  |
| Distance to Surface Water (ft) |  |  |
| ** Size of controlled area around well (square feet) |  |  |
| * Type of access control to well site (fencing, building, etc) |  |  |
| * Surface Seal? (Concrete slab)("YES", "NO" or "UNKNOWN") |  |  |
| * Dimensions of concrete slab: Length(ft)/ Width(ft)/ Thick(in) |  |  |
| * Within 100 year flood plain? ("YES", "NO" or "UNKNOWN") |  |  |
| * Drainage away from well? ("YES" or "NO") |  |  |
| ENCLOSURE/HOUSING |  |  |
| Enclosure Type (building, vault, none, etc.) |  |  |
| Floor material |  |  |
| Located in Pit? ("YES" or "NO") |  |  |
| Pit depth (feet) (if applicable) |  |  |

| WELL DATA SHEET Sheet 2 of 3 |  |  |
| --- | --- | --- |
| WELL CONSTRUCTION | (separate multiple entries in field with semi-colon) | Actual, Estimated or Default? |
| Date drilled |  |  |
| Drilling Method |  |  |
| Depth of Bore Hole (feet below ground surface) |  |  |
| Casing Beginning Depth/Ending Depth(ft below surface); 2nd Casing Beginning Depth/Ending Depth; 3rd Casing, etc. |  |  |
| Casing Diameter (inches); 2nd Casing Diameter; 3rd Casing, etc. |  |  |
| Casing Material; 2nd Casing Material; 3rd Casing, etc. |  |  |
| Conductor casing used? ("YES", "NO" or "UNKNOWN") (See Note 2) |  |  |
| Conductor casing removed? ("YES", "NO" or "UNKNOWN") |  |  |
| * Depth to highest perforations/screens (ft below surface) (or "UNKNOWN") |  |  |
| Screened Interval Beginning Depth/Ending Depth (ft below surface); 2nd Screened Interval Beg. Depth/Ending Depth; 3rd Screened Interval, etc. |  |  |
| * Total length of screened interval (ft) (default = 10% pump capacity in gpm) (or "UNKNOWN") |  |  |
| * Annular Seal?("YES", "NO" or "UNKNOWN") (See Note 3) |  |  |
| * Depth of Annular Seal (ft) |  |  |
| Material of Annular Seal (cement grout, bentonite, etc.) |  |  |
| Gravel pack, Depth to top (ft below ground surface) |  |  |
| Total length of gravel pack (ft) |  |  |
| AQUIFER |  |  |
| * Aquifer Materials (list all that apply: sand, silt, clay, gravel, rock, fractured rock) |  |  |
| * Effective porosity (decimal percent) (default = 0.2) (or "UNKNOWN") |  |  |
| * Confining layer (Impervious Strata) above aquifer? ("YES", "NO" or "UNKNOWN") |  |  |
| Thickness of confining layer, if known (ft) |  |  |
| Depth to confining layer, if known (ft below ground) |  |  |
| * Static water level (ft below ground surface) |  |  |
| Static water level measurement: Date/Method |  |  |
| Pumping water level (ft below ground surface) |  |  |
| Pumping water level measurement: Date/Method |  |  |
| WELL PRODUCTION |  |  |
| Well Yield (gpm) |  |  |
| Well Yield Based On (i.e., pump test, etc.) |  |  |
| Date measured |  |  |
| Is the well metered? ("YES" or "NO") |  |  |
| Production (gallons per year) |  |  |
| Frequency of Use (hours/year) |  |  |
| Typical pumping duration (hours/day) |  |  |
| PUMP |  |  |
| Make |  |  |
| Type |  |  |
| Size (hp) |  |  |

| WELL DATA SHEET Sheet 3 of 3 |  |  |
| --- | --- | --- |
| PUMP (continued) |  |  |
| * Capacity (gpm) |  |  |
| Depth to suction intake (ft below ground surface) |  |  |
| Lubrication Type |  |  |
| Type of Power: (i.e., electric, diesel, etc.) |  |  |
| Auxiliary power available? ("YES" or "NO") |  |  |
| Operation controlled by: (i.e., level in tank, pressure, etc.) |  |  |
| Pump to Waste capability? ("YES" or "NO") |  |  |
| Discharges to: (i.e., distribution system, storage, etc.) |  |  |
| REMARKS AND DEFECTS (use additional sheets as necessary) |  |  |
| NOTES |  |  |
| 1. Neighborhood/Surrounding Area (list all that apply): A= Agricultural, Ru = Rural, Re = Residential, Co = Commercial, I = Industrial, Mu = Municipal, P = Pristine, O = Other |  |  |
| 2. Conductor Casing - Oversized casing used to stabilize bore hole during well construction. Should be removed during installation of annular seal. |  |  |
| 3. Annular Seal - Seal of grout in the space between the well casing and the wall of the drilled hole. Sometimes called "sanitary seal". |  |  |
| Please Note: |  |  |
| The information on this Well Data Sheet is considered confidential. To allow the information to be included |  |  |
| in the permit report, or made available subject to a public information act request, the waiver clause below has |  |  |
| to be signed and dated by the owner (public water system). In lieu of this signature, the WDS has to be |  |  |
| retained in a confidential file, or the information shown in the shaded rows has to be "blacked out." |  |  |
| I/We,(Name)_______________________________________, certify that I/We am/are the present owners of the well described on this well data sheet. I/We have reviewed the information presented on this well data sheet and I/We take no exception to having the information included in the Department of Public Health' Engineering Report. I/We understand that by including the well data sheet in the Engineering Report, it will be part of a public document that can be reviewed and copied subject to the public information act request. |  |  |
|  | , |  |
| ________________________ ________________ |  |  |
| (Signature) (Date) |  |  |

Possible Contaminating Activities (PCA) Inventory Form

Ground Water Source

Public water system name:	_____________			ID No.	____________

Name of drinking water source:	_______			ID No.	_______

Inventory date: 			         Inventory conducted by:

Indicate PCAs pertinent to the drinking water source protection zones, from the following tables, as applicable:

Commercial/Industrial

Residential/Municipal

Agricultural/Rural		______

Other (required for all)	______

Proceed to appropriate checklist or checklists.  Indicate whether the PCA is located in the zone by placing a Y (yes), N (no), or U (unknown) in the appropriate boxes.

Example:

| Zone A | Zone B5 | Zone B10 |
| --- | --- | --- |
| ## Y | N | N |
| N | ## Y | ## U |
| ## U | N | N |

Risk Ranking of PCAs, where  VH = Very High Risk, H = High Risk, M = Moderate Risk, L = Low Risk

| PCA Checklist COMMERCIAL/INDUSTRIAL |  |  |  |  |
| --- | --- | --- | --- | --- |
| PCA (Risk Ranking) | PCA in Zone A? | PCA in Zone B5? | PCA in Zone B10? | Comments |
| Automobile- Body shops (H) |  |  |  |  |
| Automobile- Car washes (M) |  |  |  |  |
| Automobile- Gas stations (VH) |  |  |  |  |
| Automobile- Repair shops (H) |  |  |  |  |
| Boat services/repair/ refinishing (H) |  |  |  |  |
| Chemical/petroleum pipelines (H) |  |  |  |  |
| Chemical/petroleum processing/storage (VH) |  |  |  |  |
| Dry cleaners (VH) |  |  |  |  |
| Electrical/electronic manufacturing (H) |  |  |  |  |
| Fleet/truck/bus terminals (H) |  |  |  |  |
| Furniture repair/ manufacturing (H) |  |  |  |  |
| Home manufacturing (H) |  |  |  |  |
| Junk/scrap/salvage yards (H) |  |  |  |  |
| Machine shops (H) |  |  |  |  |
| Metal plating/ finishing/fabricating (VH) |  |  |  |  |
| Photo processing/printing (H) |  |  |  |  |
| Plastics/synthetics producers (VH) |  |  |  |  |
| Research laboratories (H) |  |  |  |  |
| Wood preserving/treating (H) |  |  |  |  |
| Wood/pulp/paper processing and mills (H) |  |  |  |  |
| Lumber processing and manufacturing (H) |  |  |  |  |
| Sewer collection systems (H, if in Zone A, otherwise L) |  |  |  |  |
| Parking lots/malls (>50 spaces) (M) |  |  |  |  |
| Cement/concrete plants (M) |  |  |  |  |
| Food processing (M) |  |  |  |  |
| Funeral services/graveyards (M) |  |  |  |  |
| Hardware/lumber/parts stores (M) |  |  |  |  |
| Appliance/Electronic Repair (L) |  |  |  |  |
| Office buildings/complexes (L) |  |  |  |  |
| Rental Yards (L) |  |  |  |  |
| RV/mini storage (L) |  |  |  |  |

| PCA Checklist RESIDENTIAL/MUNICIPAL |  |  |  |  |
| --- | --- | --- | --- | --- |
| PCA (Risk Ranking) | PCA in Zone A? | PCA in Zone B5? | PCA in Zone B10? | Comments |
| Airports - Maintenance/ fueling areas (VH) |  |  |  |  |
| Landfills/dumps (VH) |  |  |  |  |
| Railroad yards/ maintenance/ fueling areas (H) |  |  |  |  |
| Septic systems - high density (>1/acre) (VH if in Zone A, otherwise M) |  |  |  |  |
| Sewer collection systems (H, if in Zone A, otherwise L) |  |  |  |  |
| Utility stations - maintenance areas (H) |  |  |  |  |
| Wastewater treatment plants (VH in Zone A, otherwise H) |  |  |  |  |
| Drinking water treatment plants (M) |  |  |  |  |
| Golf courses (M) |  |  |  |  |
| Housing - high density (>1 house/0.5 acres) (M) |  |  |  |  |
| Motor pools (M) |  |  |  |  |
| Parks (M) |  |  |  |  |
| Waste transfer/recycling stations (M) |  |  |  |  |
| Apartments and condominiums (L) |  |  |  |  |
| Campgrounds/ Recreational areas (L) |  |  |  |  |
| Fire stations (L) |  |  |  |  |
| RV Parks (L) |  |  |  |  |
| Schools (L) |  |  |  |  |
| Hotels, Motels (L) |  |  |  |  |

| PCA Checklist AGRICULTURAL/RURAL |  |  |  |  |
| --- | --- | --- | --- | --- |
| PCA (Risk Ranking) | PCA in Zone A? | PCA in Zone B5? | PCA in Zone B10? | Comments |
| Grazing (> 5 large animals or equivalent per acre) (H in Zone A, otherwise M) |  |  |  |  |
| Concentrated Animal Feeding Operations (CAFOs) as defined in federal regulation1 (VH in Zone A, otherwise H) |  |  |  |  |
| Animal Feeding Operations as defined in federal regulation2 (VH in Zone A, otherwise H) |  |  |  |  |
| Other Animal operations (H in Zone A, otherwise M) |  |  |  |  |
| Farm chemical distributor/ application service (H) |  |  |  |  |
| Farm machinery repair (H) |  |  |  |  |
| Septic systems - low density (<1/acre) (H in Zone A, otherwise L) |  |  |  |  |
| Lagoons / liquid wastes (H) |  |  |  |  |
| Machine shops (H) |  |  |  |  |
| Pesticide/fertilizer/ petroleum storage & transfer areas (H) |  |  |  |  |
| Agricultural Drainage (H in Zone A, otherwise M) |  |  |  |  |
| Wells - Agricultural/ Irrigation (H) |  |  |  |  |
| Managed Forests (M) |  |  |  |  |
| Crops, irrigated (Berries, hops, mint, orchards, sod, greenhouses, vineyards, nurseries, vegetable) (M) |  |  |  |  |
| Fertilizer, Pesticide/ Herbicide Application (M) |  |  |  |  |
| Sewage sludge/biosolids application (M) |  |  |  |  |
| Crops, nonirrigated (e.g., Christmas trees, grains, grass seeds, hay, pasture) (L) (includes drip-irrigated crops) |  |  |  |  |

| PCA Checklist OTHER ACTIVITIES |  |  |  |  |
| --- | --- | --- | --- | --- |
| PCA (Risk Ranking) | PCA in Zone A? | PCA in Zone B5? | PCA in Zone B10? | Comments |
| NPDES/WDR permitted discharges (H) |  |  |  |  |
| Underground Injection of Commercial/Industrial Discharges (VH) |  |  |  |  |
| Historic gas stations (VH) |  |  |  |  |
| Historic waste dumps/ landfills (VH) |  |  |  |  |
| Illegal activities/ unauthorized dumping (H) |  |  |  |  |
| Injection wells/ dry wells/ sumps (VH) |  |  |  |  |
| Known Contaminant Plumes (VH) |  |  |  |  |
| Military installations (VH) |  |  |  |  |
| Mining operations - Historic (VH) |  |  |  |  |
| Mining operations - Active (VH) |  |  |  |  |
| Mining - Sand/Gravel (H) |  |  |  |  |
| Wells - Oil, Gas, Geothermal (H) |  |  |  |  |
| Salt Water Intrusion (H) |  |  |  |  |
| Recreational area - surface water source (H) |  |  |  |  |
| Underground storage tanks - Confirmed leaking tanks (VH) |  |  |  |  |
| Underground storage tanks - Decommissioned - inactive tanks (L) |  |  |  |  |
| Underground storage tanks - Non-regulated tanks (tanks smaller than regulatory limit) (H) |  |  |  |  |
| Underground storage tanks - Not yet upgraded or registered tanks (H) |  |  |  |  |
| Underground storage tanks - Upgraded and/or registered - active tanks (L) |  |  |  |  |
| Above ground storage tanks (M) |  |  |  |  |
| Wells - Water supply (M) |  |  |  |  |
| Construction/demolition staging areas (M) |  |  |  |  |
| Contractor or government agency equipment storage yards (M) |  |  |  |  |
| Dredging (M) |  |  |  |  |
| Transportation corridors - Freeways/state highways (M) |  |  |  |  |
| Transportation corridors - Railroads (M) |  |  |  |  |
| Transportation corridors - Historic railroad right-of-ways (M) |  |  |  |  |
| Transportation corridors - Road Right-of-ways (herbicide use areas) (M) |  |  |  |  |
| Transportation corridors - Roads/ Streets (L) |  |  |  |  |
| Hospitals (M) |  |  |  |  |
| Storm Drain Discharge Points (M) |  |  |  |  |
| Storm Water Detention Facilities (M) |  |  |  |  |

| PCA Checklist OTHER ACTIVITIES (continued) |  |  |  |  |
| --- | --- | --- | --- | --- |
| PCA (Risk Ranking) | PCA in Zone A? | PCA in Zone B5? | PCA in Zone B10? | Comments |
| Artificial Recharge Projects - Injection wells (potable water) (L) |  |  |  |  |
| Artificial Recharge Projects - Injection wells (non-potable water) (M) |  |  |  |  |
| Artificial Recharge Projects - Spreading Basins (potable water) (L) |  |  |  |  |
| Artificial Recharge Projects - Spreading Basins (non-potable water) (M) |  |  |  |  |
| Medical/dental offices/clinics (L) |  |  |  |  |
| Veterinary offices/clinics (L) |  |  |  |  |
| Surface water - streams/ lakes/rivers (L) |  |  |  |  |
| Wells - monitoring, test holes (L) |  |  |  |  |

#### Instructions for Groundwater Assessment Map

The assessment map for a groundwater source should be submitted on USGS topographic maps (“quad maps”) at 1:24,000 scale.  The map should show:

- Location of the source

- Protection Zones

- Significant Possible Contaminating Activities (PCAs) within the zone (optional, but recommended)

The protection zone for groundwater sources are a set of three circles surrounding the source.  (For springs and horizontal wells, if determined to be groundwater sources, the protection zones need not include those portions of the circles down gradient of the source.)  The radius of the protection zone is determined in the Delineation section of the assessment and depends upon the aquifer material, well pumping rate, screened interval, and aquifer porosity.

USGS quad maps may be obtained from map or backpacking retailers.  There are also several computer software programs that include USGS quad maps.

At the discretion of the regulatory agency, the water system may request that the regulatory agency prepare a map displaying the source and zones.

An example map for a well source is attached.

##### Example Well Assessment Map