State Water Resources Control Board

Division of Drinking Water

50 D Street – Room 200, Santa Rosa, CA 95404

Phone (707) 576-2145 / FAX (707) 576-2722

Internet Address: www.cdph.ca.gov

9A

PUMP TEST PROCEDURES FOR WELLS IN ALLUVIAL SOILS

NOTE:   These testing procedures are based on the California Code of Regulations, Title 22, Section 64554(f).  Before beginning any well yield pump test, the drillers well log must be reviewed to determine if this is an alluvial or bedrock aquifer. Due to Sonoma volcanics and other formations, the determination often is not clear. It is recommended that you submit the driller’s well log to this Department to determine the type of pump test procedures to be used.

A pumping test to determine sustained yield of a well in alluvial soils should be conducted as described below.

Before the testing:

- Review the drillers log, if available, and confirm the well is drilled in alluvial soils (absence of bedrock).

- Choose pump and discharge rate.

- Ensure that the pumping test can be continued for a minimum of 8 hours.

- Ensure discharge from the pump is piped far enough away to avoid recharge.

Conducting the testing:

- Take an initial water level measurement (static water level).

- Pump the well continuously for a minimum of eight hours.

- Maintain a constant flow during the test.

- Measure the drawdown carefully in the pumping well.

- Take drawdown readings at a frequency no less than once every hour.

Enter the results on the attached spreadsheet. The pumping rate gallons must be constant for the last 4 hours of testing to reach “steady state”. If steady-state is not achieved, the pumping test must be run longer or the well must be allowed to recover to original static water level and test must be rerun at a lower flow rate in accordance with “Conducting the Testing” above, until steady-state is achieved.

Recovery Data:

Recovery data must be collected and recorded after termination of pumping.

- Discontinue pumping.

- Take measurements of the water level drawdown at a minimum of every 15 minutes for the first two hours and every hour thereafter for at least six hours.

- The data must indicate that, within a length of time not exceeding the duration of the pumping time of the well capacity test, the well has recovered to within two feet of the static water level measured at the beginning of the test or to a minimum of ninety-five percent of the total drawdown measured during the test, whichever is more stringent.

Well Capacity:

The capacity of the well will be the pumping discharge rate used during the test1.

Submittal to the Department:

A report must be submitted to the Department that includes, but is not limited to:

- Pumping test methods and calculations.

- Static water level and all recorded drawdown data.  If a transducer is used, provide an electronic file of the transducer data.

- Other pertinent observations associated with the well capacity test.

- Plot of the results as described above.

- Estimated well capacity.

. 1An assigned well capacity may be revised by the Department if subsequent pumping data collected during normal operations that the assigned capacity is not representative of the actual well capacity.