### INTRODUCTION

In order to determine compliance with the Surface Water Filtration and Disinfection Treatment Rule disinfection requirements, public water systems that use surface water sources must know the disinfectant contact time in their treatment process units.  The City of American Canyon, California operates a public water system that fits into this category.  On October 29, 1997, a tracer study was performed to estimate disinfectant contact time for the chlorine contact tank at the City of American Canyon Water Treatment Plant (CACWTP clearwell).

The CACWTP clearwell was designed with features to increase disinfectant contact time and minimize short-circuiting.  Appendix A contains a diagram of the CACWTP clearwell.  Water passes over a weir at the entrance, goes around two baffles that create serpentine flow, and then exits through an outlet that has no baffling.

The product of the chlorine concentration in the CACWTP clearwell and the time that the chlorine is in contact with the water (CT) is used to determine if sufficient inactivation of viruses and Giardia has been achieved.  Calculated CT values are compared with CT values found on tables in the 1989 USEPA Guidance Manual for Compliance with the Filtration and Disinfection Requirements for Public Water Systems Using Surface Water Sources (USEPA Guidance Manual).  These CT tables take into account the type and concentration of the disinfectant, contact time, pH, and temperature.  If a calculated CT value meets or exceeds the CT value on the table that corresponds to the required level of inactivation, adequate disinfection has occurred.

There are different methods by which CT is calculated.  The USEPA Guidance Manual recommends that the value used for T in the calculation of CT be T10.   For this reason, the USEPA Guidance Manual assigns estimated T10/T values for treatment process units based on the baffling conditions within the units.  The baffling condition within the CACWTP clearwell is most similar to what is classified as “average” in the USEPA Guidance Manual.  The USEPA Guidance Manual describes the “average” baffling condition as having a “baffled inlet or outlet with some intrabasin baffles” and assigns a T10/T value of 0.5 to this baffling condition.   This value can be used to estimate T10 for the CACWTP clearwell, but a T10 result from a tracer study is preferred.

The effluent chlorine residual concentration is often used in CT calculations.  When single concentration values such as the effluent concentration are used, chlorine concentration variations within process units are not taken into account.  Effective CT (introduced by Teefy and Singer, 1990) considers variations in chlorine concentrations and disinfectant contact times.  The effective CT is calculated based on first order kinetics of chlorine decay and a residence time distribution obtained from a tracer study.

The residence time distribution shows the amounts of time that incremental volumes of water spend in a treatment process unit.  By accounting for chlorine decay within each incremental volume of water, effective CT shows that the incremental volumes that pass through a process unit quickly have higher chlorine concentrations than the incremental volumes that pass through slowly.

### PURPOSE

The purpose of the tracer study was to measure the disinfectant contact time for the CACWTP clearwell.  Values of T10 and effective CT were obtained from the tracer study results.  The T10 value established by the tracer study was compared with a T10 value estimated using the USEPA Guidance Manual.  Both of these T10 values were used to calculate CT and to determine the corresponding degree of inactivation.  Lastly, these CT calculations were compared with the effective CT.

The California Department of Health Services, Division of Drinking Water and Environmental Management, Drinking Water Field Operations Branch wishes to collect disinfectant contact time information from tracer tests conducted on water treatment process units throughout California.  The T10 result and other information related to disinfection and flow characteristics within the CACWTP clearwell will be entered into the statewide database.

# EXPERIMENTAL AND ANALYTICAL PROCEDURES

The test parameters are summarized in Table 1.  A step-input test was conducted for 210 minutes using fluoride as the tracer.  During the test, the CACWTP clearwell contained 96,800 gallons of water and the flow rate through it was 1,400 gpm.

Powdered sodium fluoride was dissolved in water to create the tracer solution.  Injection and sampling points are shown on the CACWTP clearwell diagram in Appendix A.  Throughout the test, this solution was injected into a transmission pipe that leads from the filters to the CACWTP clearwell.  The CACWTP clearwell has no sample tap from which to collect effluent samples.  For this reason, effluent samples were collected near the opening of the CACWTP clearwell outlet pipe using a pump.  A weighted suction tube was used with the pump because the outlet pipe is near the bottom of the CACWTP clearwell.  In addition to the effluent samples, influent samples were collected downstream from the tracer injection point in the transmission pipe that leads from the filters to the CACWTP clearwell.  All samples were stored in 60-mL polyethylene bottles.  An ion-selective electrode was used for the fluoride analyses.

Table 1. Test Parameters

##### Step-input test

Plant flow rate during test = 100% design capacity = 1,400 gpm

#### Chlorine contact tank volume during test = minimum operating volume = 96,800 gallons

Theoretical detention time of chlorine contact tank = 69.1 minutes

Test run time = 3 * theoretical detention time = 207 min = 3.46 hours

Tracer: Sodium Fluoride manufactured by Chemtech

- pH at saturation = 7.6

- solubility at 25 oC = 4.05 g per 100 g H2O

- 45.25% fluoride ion

- 97% chemical purity

- 97 lb/ft3 bulk density

Tracer dose = 2.05 mg/L

13.70 lbs dry sodium fluoride required

40.6 gallons H2O minimum required to dissolve 13.70 lbs dry sodium fluoride

65.5 gallons H2O used

Solution concentration = 11,012 mg/L

Feed pump capacity = 497 gpd = 1306.4 mL/min

Feed pump setting = 1000.0 mL/min

In order to determine T10, a time series plot of the following function, F(t), was made:

Ft=Ci−CoCf−Co

Ci is the effluent fluoride concentration, Co is the background fluoride concentration, and Cf is the final or ultimate fluoride concentration.  (On a plot of F(t), T10 is the time at which F(t) equals 0.10.)

Effective CT was also determined.  The following equation was used to calculate effective CT:

Effective CT=tiEidtCoe−kti

Co is the influent or initial chlorine concentration, k is the chlorine decay rate constant and ti is the time.  Ei is the value of the residence time distribution function and is equal to F(t)/t.

RESULTS

The tracer study results are tabulated in Appendix B.  The targeted fluoride dose was 2.05 mg/l, but the final observed fluoride concentration was 1.30 mg/l.  Incomplete sodium fluoride dissolution in the tracer solution storage tank was the most likely cause of the difference between the targeted and observed fluoride doses.  At the end of the test, powder that resembled undissolved sodium fluoride was seen at the bottom of the tracer solution storage tank.  Some fluoride may have also been lost due to chemical reactions in the CACWTP clearwell, adsorption onto surfaces, and volatilization.

A time series plot of F(t) is shown in Figure 1.  From the plot of F(t), a T10 value of 21.3 minutes was obtained.  A T10 value of 35 minutes was computed using the T10/T value from the EPA Guidance Manual (0.5) and a theoretical detention time (T) of 69.1 minutes.  The difference between the tracer test T10 result and the value determined using the USEPA Guidance Manual may have been caused, in part, by use of maximum plant flow rate and minimum tank operating volume during the tracer test.  These conditions were selected in order to generate a “worst case” T10 value for the CACWTP clearwell.  A “worst case” value was desired because only one tracer test was planned.  If other tracer studies are conducted, lower flow rates and higher tank operating volumes should be used.

Figure 1.  Time Series Plot of F(t)

Factors associated with the design of the CACWTP clearwell could also explain the difference between the USEPA Guidance Manual T10 value and tracer test result.  According to Bishop et al (1993), low length-to-width and length-to-depth ratios are associated with increased axial dispersion within process units.  The CACWTP clearwell’s length-to-width and length-to-depth ratios (9:1 and 11:1, respectively) are relatively low and may allow a large degree of axial dispersion and “short-circuiting”.

Table 2 lists the results of CT values calculated by different methods and the corresponding log inactivations assigned by the USEPA Guidance Manual.  Although the CT values differ quite significantly, they all meet the required log inactivation.  Compliance may be demonstrated by using any of the three methods presented.

Table 2. CT Results

| Method | CT [(mg/L)-min] | Log Inactivation of Giardia * |
| --- | --- | --- |
| T = T10 = 35 min. assigned by USEPA Guidance Manual | 63.0 | 2.0 |
| T = T10 = 21.3 min. determined by tracer study | 38.3 | 1.2 |
| Effective CT determined by tracer study | 85.4 | 2.7 |

* Notes:	1. Required log inactivation of Giardia is 3 log.  CACWTP uses conventional filtration and receives 2.5 log removal credit.  Therefore, disinfection must meet 0.5 log inactivation.

2. CT table used to interpolate log inactivation of Giardia using free chlorine was for pH = 7.5, chlorine concentration = 1.7 mg/L, and temp = 15oC.

CONCLUSION

The CACWTP clearwell tracer study generated a T10 value of 21.3 minutes and a T10/T value of 0.31.  These values will be used in the future by the City of American Canyon to determine compliance with the disinfection requirements of the Surface Water Filtration and Disinfection Treatment Rule.

REFERENCES

BISHOP, M.M.; MORGAN, J.M.; CORNWELL, B. & JAMISON, D.K. Improving the Disinfection Detention Time of a Water Plant Clearwell. Jour AWWA, 85:3:68 (Mar. 1993).

LEVENSPIEL, O. Chemical Reaction Engineering. John Wiley and Sons, New York (2nd ed., 1962).

TEEFY, S.M. & SINGER, P.C. Performance and Analysis of Tracer Tests to Determine Compliance of a Disinfection Scheme With the SWTR. Jour AWWA, 82:12:88 (Dec. 1990).

USEPA. Guidance Manual for Compliance with the Filtration and Disinfection Requirements for Public Water Systems Using Surface Water Sources. Washington, D.C. (1989).

T10 is defined as the detention time at which 90 percent of the water passing through a tank or process unit is retained within the tank or process unit.  T is defined as the theoretical detention time of a tank or process unit. T10/T is sometimes called the “short-circuiting factor”.

An overflow weir entrance meets the USEPA definition of inlet baffling.

The Hach Combination Fluoride Electrode Model 50265 was used.