## Slide 1: FCSA #34 Millerton New Town CA1000484 Fresno County Jar Test
by Guy Schott, P.E.
May 20, 2021

## Slide 2: Millerton Lake

## Slide 3: Trident
Trident Filtration System

## Slide 4: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (254 nm) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: FCSA #34 Millerton New Town Source & Treated Water Characteristics, May 20, 2021
Source
pH: 7.46
Alkalinity: 13 mg/L as CaCO3
Turbidity: 0.41 NTU
UVT: 89.0%,
UVA: 0.050/cm
0.4 um Filtered
Turbidity: 0.11 NTU
UVT: 89.9%,
UVA: 0.046/cm
Plant Filtrate Water (pre-chlorination
Turbidity: 0.09 NTU
UVT: 90.4%,
UVA: 0.046/cm
UVA Reduction: 6.52%

## Slide 6: Applied Coagulants for Jar Testing (1)
Sterling Water Technologies 8809
40-60% Water (50%)
20-30% Aluminum Chlorohydrate (25%)
~11.8% Al2O3
~6.2% Al
83% Basicity
20-30% Polyquaternary amine (25%)
SG = 1.19 – 1.33
NSF limit: 20 mg/L (product)
Product dose 4 mg/L = 1.0 mg/L polyamines active
Pro Pac 9890 (NTU Technologies)
35-45% Aluminum Chlorohydrate
35-45% Water
~18.9% Al2O3
~10.5% Al
83% Basicity
20% polyamine (50% water, 50% active polyamines)
SG = 1.25-1.34
NSF limit: 50 mg/L as Product;
Product dose 10 mg/L = 1 mg/L polyamines active

## Slide 7: Applied Coagulants for Jar Testing (2)
BWS, Inc.
Greg Nieckarz, Ph.D.
Greg.niekarz@bws.works
541-953-5112
AdvFloc-CTC-00011
Polyaluminum Hydroxy Chlorosulfate
12.55% Al2O3
6.64% Al
64.9% Basicity
SG = 1.299
NSF limit: 250 mg/L as Product

## Slide 8: Polyamine C59H108N14O10 MW: 1,173.6 g/mol

## Slide 9: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.46
LCA #1: SWT 8809: 3.13 mg/L
LCA #2: 9890: 4.85 mg/L
LCA #3: AdvFloc CTC-00011: 25 mg/L

## Slide 10: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Aluminum Sulfate doses are reported as hydrated Al2(SO4)3*14.3H20.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 11: FCSA #34 Millerton New Town: Source: Millerton Lake Summary of Plant Coagulant/Dose Jar vs. Optimum Dose and Coagulants
Jar# | CTC-00011 mg/L | SWT 8809 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction
A | 0 | 1.8 | 0.09 | 92.7 | 0.032 | 30.4
vs. |  |  |  |  |  | 
B | 0 | 4.2 | 0.08 | 94.3 | 0.025 | 45.7
C | 15 | 2.8 | 0.04 | 95.9 | 0.017 | 63.0
Note: Jar A – due to poor filterability and floc interference of %UVT/UVA measurements, results are based on water filtered through a 0.6 um absolute Isopore membrane as opposed to a 1.2 um absolute Isopore membrane that is used for the filterability and UVT/UVA analysis.

## Slide 12: %UVA Reduction via Source Water Chlorination
Chart: Source Water %UVA Reduction (NaOCl = 2 mg/L Spiked)
| 0 | 5 | 12 | 24 | 40 | 60
 | 0 | 0.10638 | 0.14894 | 0.17021 | 0.14894 | 0.17021

## Slide 13: Jar Test – Filtrate Water Spiked with 2.2 mg/L NaOCl Plant Coagulant Dose vs. Optimum Dose and Coagulant
Chart: Chlorine Residual Over Time
| 0 | 1.1458333333333333 | 2.1666666666666665 | 3.1875 | 4.1875 | 5.1875 | 6.1875 | 7.1875 | 8.1875 | 11.1875 | 18.729166666666668 | 21.208333333333332 | 24.208333333333332 | 26.1875 | 27.8125
SWT 8809: 1.8 mg/L, UVA: 0.032/cm | 1.84 | 0.96 | 0.81 | 0.66 | 0.58 | 0.5 | 0.38 | 0.26 | 0.2 | 0.09 | 0 | 0 | 0 | 0 | 0
CTC-00011: 15 mg/L, SWT 8809: 2.8 mg/L, UVA: 0.017/cm | 1.91 | 1.42 | 1.25 | 1.14 | 1.04 | 0.95 | 0.86 | 0.8 | 0.74 | 0.61 | 0.37 | 0.29 | 0.22 | 0.18 | 0.14
7 days:
Blue line: TTHM: 71 ug/L, HAA5: 41 ug/L
Orange line: TTHM: 44 ug/L, HAA5: 29 ug/L

## Slide 14: Coagulants
Coagulant | Chemical Dose, mg/L | Alkalinity Consumed mg/L as CaCO3
SWT 8809 | 10 | 0.6
CTC-00011 | 10 | 1.3
9890 | 10 | 0.9

## Slide 15: FCSA #34 Millerton New Town : TTHMs/HAA5s Laboratory Results NaOCl dose after filtration: 2.2 mg/L (Hold Time 6 days)
Jar # | CTC-0001 mg/L | SWT 8809 mg/L | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | TTHM ug/L | HAA5 ug/L | Cl2 Residual mg/L
1 | 0 | 1.8 | 92.7 | 0.032 | 30.4 | 71 | 41 | 0.31
2 | 15 | 2.8 | 95.9 | 0.017 | 63.0 | 44 | 29 | 0.82
End of 6 days:
Jar #1: UVT: 95.3%, UVA: 0.020/cm (26.1% UVA additional reduction)
Jar #2: UVT: 97.0%, UVA: 0.013/cm (8.7% UVA additional reduction)

## Slide 16: FCSA #34 Millerton New Town; Jar Test 1 - 8 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | SWT 8809 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction
J1 | 1.8 | 0.27 | 90.9 | 0.041 | 10.9
J2 | 2.5 | 0.18 | 92.2 | 0.035 | 23.9
J3 | 3.2 | 0.06 | 93.4 | 0.029 | 37.0
J4 | 3.9 | 0.05 | 93.9 | 0.027 | 41.3
J5 | 4.2 | 0.12 | 93.5 | 0.029 | 37.0
J6 | 4.8 | 0.12 | 93.6 | 0.028 | 39.1
J7 | 5.4 | 0.24 | 92.3 | 0.034 | 26.1
J8 | 6.0 | 0.20 | 91.6 | 0.038 | 17.4

## Slide 17: FCSA #34 Millerton New Town; Jar Test 9 - 12 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | CTC-00011 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction
J9 | 24 | 0.05 | 95.0 | 0.022 | 52.2
J10 | 28 | 0.05 | 95.2 | 0.021 | 54.3
J11 | 32 | 0.05 | 95.4 | 0.020 | 56.5
J12 | 36 | 0.05 | 95.3 | 0.020 | 56.5
J13 | 12 | 0.12 | 93.2 | 0.030 | 34.8
J14 | 16 | 0.04 | 94.6 | 0.024 | 47.8
J15 | 20 | 0.05 | 94.7 | 0.023 | 50.0
J16 | 24 | 0.04 | 95.3 | 0.020 | 56.5

## Slide 18: FCSA #34 Millerton New Town; Jar Test 17 - 24 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction
J17 | 4.2 | 0.13 | 93.5 | 0.029 | 37.0
J18 | 4.8 | 0.10 | 94.0 | 0.026 | 43.5
J19 | 5.4 | 0.07 | 94.5 | 0.024 | 47.8
J20 | 6.0 | 0.09 | 94.5 | 0.024 | 47.8
J21 | 5.4 | 0.09 | 94.4 | 0.024 | 47.8
J22 | 6.0 | 0.10 | 94.5 | 0.024 | 47.8
J23 | 6.6 | 0.08 | 94.8 | 0.022 | 52.2
J24 | 7.2 | 0.13 | 94.4 | 0.024 | 47.8

## Slide 19: FCSA #34 Millerton New Town; Jar Test 25 - 32 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | CTC-00011 mg/L | SWT 8809 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction
J25 | 0.0 | 2.5 | 0.23 | 91.0 | 0.041 | 10.9
J26 | 10 | 2.5 | 0.07 | 95.0 | 0.022 | 52.2
J27 | 14 | 2.5 | 0.05 | 95.5 | 0.020 | 56.5
J28 | 18 | 2.5 | 0.05 | 95.6 | 0.019 | 58.7
J29 | 0.0 | 1.8 | 0.28 | 91.4 | 0.038 | 17.4
J30 | 0.0 | 3.8 | 0.16 | 93.5 | 0.029 | 37.0
J31 | 28 | 0.0 | 0.04 | 95.5 | 0.019 | 58.7
J32 | 18 | 2.5 | 0.04 | 95.6 | 0.019 | 58.7

## Slide 20: FCSA #34 Millerton New Town; Jar Test 33 - 40 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | CTC-00011 mg/L | SWT 8809 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction
J33 | 0 | 2.8 | 0.16 | 93.0 | 0.031 | 32.6
J34 | 0 | 3.2 | 0.13 | 93.3 | 0.030 | 34.8
J35 | 0 | 3.6 | 0.12 | 93.3 | 0.029 | 37.0
J36 | 0 | 4.0 | 0.10 | 94.0 | 0.026 | 43.5
J37 | 12 | 2.8 | 0.05 | 95.7 | 0.019 | 58.7
J38 | 12 | 3.2 | 0.05 | 95.8 | 0.018 | 60.9
J39 | 12 | 3.6 | 0.05 | 95.8 | 0.018 | 60.9
J40 | 12 | 4.0 | 0.07 | 95.7 | 0.019 | 58.7

## Slide 21: FCSA #34 Millerton New Town; Jar Test 41 - 48 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | CTC-00011 mg/L | SWT 8809 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction
J41 | 0 | 1.8 | 0.19/0.09 | 91.8/92.7 | 0.036/0.032 | 21.7/30.4
J42 | 0 | 3.2 | 0.11 | 93.8 | 0.028 | 39.1
J43 | 0 | 3.7 | 0.08 | 94.1 | 0.026 | 43.5
J44 | 0 | 4.2 | 0.08 | 94.3 | 0.025 | 45.7
J45 | 10 | 1.8 | 0.05 | 95.2 | 0.021 | 54.3
J46 | 15 | 1.8 | 0.05 | 95.4 | 0.020 | 56.5
J47 | 12 | 2.8 | 0.04 | 95.6 | 0.019 | 58.7
J48 | 15 | 2.8 | 0.04 | 95.9 | 0.017 | 63.0
Note: Jar41 – Results based on 1.2 & 0.6 um absolute filters.

## Slide 22: Jars 1-4 Test Flash Mix 200 RPM, 20 Sec Floc Mix 20 RPM, 5 min 25 mL sampled end of Floc Applied Coagulant SWT 8809

## Slide 23: Jars 1-4: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
1.8 mg/L SWT 8809
Filtrate 0.27 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 10.9%
2.5 mg/L SWT 8809
Filtrate 0.18 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction 23.9%
3.2 mg/L SWT 8809
Filtrate 0.06 NTU
UVT: 93.4%
UVA: 0.029/cm
UVA Reduction 37.0%
3.9 mg/L SWT 8809
Filtrate 0.05 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction 41.3%

## Slide 24: Jars 5-8 Test Flash Mix 200 RPM, 20 Sec Floc Mix 20 RPM, 5 min 25 mL sampled end of Floc Applied Coagulant SWT 8809

## Slide 25: Jars 5-8: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
4.2 mg/L SWT 8809
Filtrate 0.12 NTU
UVT: 93.5%
UVA: 0.029/cm
UVA Reduction 37.0%
4.8 mg/L SWT 8809
Filtrate 0.12 NTU
UVT: 93.6%
UVA: 0.028/cm
UVA Reduction 39.1%
5.4 mg/L SWT 8809
Filtrate 0.24 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction 26.1%
6.0 mg/L SWT 8809
Filtrate 0.20 NTU
UVT: 91.6%
UVA: 0.038/cm
UVA Reduction 17.4%

## Slide 26: Jars 9-12 Test Flash Mix 200 RPM, 20 Sec Floc Mix 20 RPM, 5 min 25 mL sampled end of Floc Applied Coagulant AdvFloc CTC-00011

## Slide 27: Jars 9-12: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
24 mg/L CTC-00011
Filtrate 0.05 NTU
UVT: 95.0%
UVA: 0.022/cm
UVA Reduction 52.2%
28 mg/L CTC-00011
Filtrate 0.05 NTU
UVT: 95.2%
UVA: 0.021/cm
UVA Reduction 54.3%
32 mg/L CTC-00011
Filtrate 0.05 NTU
UVT: 95.4%
UVA: 0.020/cm
UVA Reduction 56.5%
36 mg/L CTC-00011
Filtrate 0.05 NTU
UVT: 95.3%
UVA: 0.020/cm
UVA Reduction 56.5%

## Slide 28: Jars 13-16 Test Flash Mix 200 RPM, 20 Sec Floc Mix 20 RPM, 5 min 25 mL sampled end of Floc Applied Coagulant AdvFloc CTC-00011

## Slide 29: Jars 13-16: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
12 mg/L CTC-00011
Filtrate 0.12 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction 34.8%
16 mg/L CTC-00011
Filtrate 0.04 NTU
UVT: 94.6%
UVA: 0.024/cm
UVA Reduction 47.8%
20 mg/L CTC-00011
Filtrate 0.05 NTU
UVT: 94.7%
UVA: 0.023/cm
UVA Reduction 50.0%
24 mg/L CTC-00011
Filtrate 0.04 NTU
UVT: 95.3%
UVA: 0.020/cm
UVA Reduction 56.5%

## Slide 30: Jars 17-20 Test Flash Mix 200 RPM, 20 Sec Floc Mix 20 RPM, 5 min 25 mL sampled end of Floc Applied Coagulant 9890

## Slide 31: Jars 17-20: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
4.2 mg/L 9890
Filtrate 0.13 NTU
UVT: 93.5%
UVA: 0.029/cm
UVA Reduction 37.0%
4.8 mg/L 9890
Filtrate 0.10 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction 43.5%
5.4 mg/L 9890
Filtrate 0.07 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction 47.8%
6.0 mg/L 9890
Filtrate 0.09 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction 47.8%

## Slide 32: Jars 21-24 Test Flash Mix 200 RPM, 20 Sec Floc Mix 20 RPM, 5 min 25 mL sampled end of Floc Applied Coagulant 9890

## Slide 33: Jars 21-24: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
5.4 mg/L 9890
Filtrate 0.09 NTU
UVT: 94.4%
UVA: 0.024/cm
UVA Reduction 47.8%
6.0 mg/L 9890
Filtrate 0.10 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction 47.8%
6.6 mg/L 9890
Filtrate 0.08 NTU
UVT: 94.8%
UVA: 0.022/cm
UVA Reduction 52.2%
7.2 mg/L 9890
Filtrate 0.13 NTU
UVT: 94.4%
UVA: 0.024/cm
UVA Reduction 47.8%

## Slide 34: Jars 25-28 Test Flash Mix 200 RPM, 20 Sec Floc Mix 20 RPM, 5 min 25 mL sampled end of Floc Applied Coagulants AdvFloc CTC-00011 SWT 8809

## Slide 35: Jars 25-28: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
0 mg/L CTC-00011
2.5 mg/L SWT 8809
Filtrate 0.23 NTU
UVT: 91.0%
UVA: 0.041/cm
UVA Reduction 10.9%
10 mg/L CTC-00011
2.5 mg/L SWT 8809
Filtrate 0.07 NTU
UVT: 95.0%
UVA: 0.022/cm
UVA Reduction 52.2%
14 mg/L CTC-00011
2.5 mg/L SWT 8809
Filtrate 0.05 NTU
UVT: 95.5%
UVA: 0.020/cm
UVA Reduction 56.5%
18 mg/L CTC-00011
2.5 mg/L SWT 8809
Filtrate 0.05 NTU
UVT: 95.6%
UVA: 0.019/cm
UVA Reduction 58.7%

## Slide 36: Jars 29-32 Test Flash Mix 200 RPM, 20 Sec Floc Mix 20 RPM, 5 min 25 mL sampled end of Floc Applied Coagulants AdvFloc CTC-00011 SWT 8809

## Slide 37: Jars 29-32: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
0 mg/L CTC-00011
1.8 mg/L SWT 8809
Filtrate 0.28 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction 17.4%
0 mg/L CTC-00011
3.8 mg/L SWT 8809
Filtrate 0.16 NTU
UVT: 93.5%
UVA: 0.029/cm
UVA Reduction 37.0%
28 mg/L CTC-00011
0 mg/L SWT 8809
Filtrate 0.04 NTU
UVT: 95.5%
UVA: 0.019/cm
UVA Reduction 58.7%
18 mg/L CTC-00011
2.5 mg/L SWT 8809
Filtrate 0.04 NTU
UVT: 95.6%
UVA: 0.019/cm
UVA Reduction 58.7%

## Slide 38: Jars 33-36 Test Flash Mix 200 RPM, 20 Sec Floc Mix 20 RPM, 5 min 25 mL sampled end of Floc Applied Coagulant SWT 8809

## Slide 39: Jars 33-36: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
2.8 mg/L SWT 8809
Filtrate 0.16 NTU
UVT: 93.0%
UVA: 0.031/cm
UVA Reduction 32.6%
3.2 mg/L SWT 8809
Filtrate 0.13 NTU
UVT: 93.3%
UVA: 0.030/cm
UVA Reduction 34.8%
3.6 mg/L SWT 8809
Filtrate 0.12 NTU
UVT: 93.3%
UVA: 0.029/cm
UVA Reduction 37.0%
4.0 mg/L SWT 8809
Filtrate 0.10 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction 43.5%

## Slide 40: Jars 37-40 Test Flash Mix 200 RPM, 20 Sec Floc Mix 20 RPM, 5 min 25 mL sampled end of Floc Applied Coagulants AdvFloc CTC-00011 SWT 8809

## Slide 41: Jars 37-40: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
12 mg/L CTC-00011
2.8 mg/L SWT 8809
Filtrate 0.05 NTU
UVT: 95.7%
UVA: 0.019/cm
UVA Reduction 57.7%
12 mg/L CTC-00011
3.2 mg/L SWT 8809
Filtrate 0.05 NTU
UVT: 95.8%
UVA: 0.018/cm
UVA Reduction 60.9%
12 mg/L CTC-00011
3.6 mg/L SWT 8809
Filtrate 0.05 NTU
UVT: 95.8%
UVA: 0.018/cm
UVA Reduction 60.9%
12 mg/L CTC-00011
4.0 mg/L SWT 8809
Filtrate 0.07 NTU
UVT: 95.7%
UVA: 0.019/cm
UVA Reduction 58.7%

## Slide 42: Jars 41-44 Test Flash Mix 200 RPM, 20 Sec Floc Mix 20 RPM, 5 min 25 mL sampled end of Floc Applied Coagulant SWT 8809

## Slide 43: Jars 41-44: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
1.8 mg/L SWT 8809
**Filtrate 0.09 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction 30.4%
3.2 mg/L SWT 8809
Filtrate 0.11 NTU
UVT: 93.8%
UVA: 0.028/cm
UVA Reduction 39.1%
3.7 mg/L SWT 8809
Filtrate 0.08 NTU
UVT: 94.1%
UVA: 0.026/cm
UVA Reduction 43.5%
4.2 mg/L SWT 8809
Filtrate 0.08 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction 45.7%

## Slide 44: Jars 45-48 Test Flash Mix 200 RPM, 20 Sec Floc Mix 20 RPM, 5 min 25 mL sampled end of Floc Applied Coagulants AdvFloc CTC-00011 SWT 8809

## Slide 45: Jars 45-48: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
10 mg/L CTC-00011
1.8 mg/L SWT 8809
Filtrate 0.05 NTU
UVT: 95.2%
UVA: 0.021/cm
UVA Reduction 54.3%
15 mg/L CTC-00011
1.8 mg/L SWT 8809
Filtrate 0.05 NTU
UVT: 95.4%
UVA: 0.020/cm
UVA Reduction 56.5%
10 mg/L CTC-00011
2.8 mg/L SWT 8809
Filtrate 0.04 NTU
UVT: 95.6%
UVA: 0.019/cm
UVA Reduction 58.7%
15 mg/L CTC-00011
2.8 mg/L SWT 8809
Filtrate 0.04 NTU
UVT: 95.9%
UVA: 0.017/cm
UVA Reduction 63.0%

## Slide 46: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 47: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 48: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 49: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 50: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 51: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732