## Slide 1: Konocti Harbor Resort CA1710016 Lake County Jar Test
by Guy Schott, P.E.
April 23, 2021

## Slide 2: Konocti Harbor Resort Water Characteristics April 23, 2021
Source
pH: 7.98
Turbidity: 2.56 NTU
UVT: 85.3%,
UVA: 0.068/cm
0.4 um Filtered
Turbidity: 0.20 NTU
D-UVT: 87.7%,
UVA: 0.057/cm

## Slide 3: Schematice
CA1710016
Konocti Harbor & Resort
Conventional Treatment

## Slide 4: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (254 nm) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: Konocti Harbor Resort Source & Treated Water Characteristics, April 23, 2021
Source
pH: 7.98
Turbidity: 2.56 NTU
UVT: 85.3%,
UVA: 0.068/cm
0.4 um Filtered
Turbidity: 0.20 NTU
D-UVT: 87.7%,
UVA: 0.057/cm
Plant Filtrate Water (pre-NaOCl added)
Turbidity: 0.05 NTU
UVT: 93.2%,
UVA: 0.030/cm
GAC Filtrate Water
Turbidity: 0.09 NTU
UVT: 93.4%,
UVA: 0.029/cm
Clearwell (post-chlorine)
Turbidity: 0.06 NTU
UVT: 93.8%,
D-UVA: 0.027/cm

## Slide 6: Applied Coagulants for Jar Testing (1)
Pro Pac 9810 (NTU Technologies)
45-50% Aluminum Chlorohydrate
45-50% Water
~22.4% Al2O3
~11.9% Al
83% Basicity
5% polyamine (50% water, 50% active polyamines)
SG = 1.25-1.34
NSF limit: 200 mg/L as Product;
Product dose 40 mg/L = 1 mg/L polyamines active
Polydyne Incorporated
Clarifloc C-378
SG = 1.0 – 1.2
Viscosity: 800-1000 centipoise
pDADMAC (20% active, 80% H2O)
NSF limit: 50 mg/L (product)
Product dose 5 mg/L = 1 mg/L pDADMAC active

## Slide 7: Applied Coagulants for Jar Testing (2)
BWS, Inc.
AdvFloc-CTC-00011
Polyaluminum Hydroxy Chlorosulfate
12.55% Al2O3
6.64% Al
64.9% Basicity
SG = 1.299
NSF limit: 250 mg/L as Product
Gregory F. Nieckarz, Ph.D.
Principal Consultant
SWS Consulting, LLC.
+1.541.953.5112
gregn.swsc@gmail.com

## Slide 8: Diallyldimethylammonium chloride or N-allyl-N,N-dimethylprop-2-en-1-aminium chloride pDADMAC C8H16ClN MW: 161.67 g/mol
N
+
CH3
CH3
CH2
CH
CH2
CH2
CH
CH2
Cl-

## Slide 9: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.98
LCA #1: 9810: 19.2 mg/L
pH adjusted to 7.7 with acetic acid
LCA #2: AdvFloc CTC-00011: 126 mg/L
pH adjusted to 7.7 with acetic acid

## Slide 10: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Aluminum Sulfate doses are reported as hydrated Al2(SO4)3*14.3H20.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 11: Konocti Harbor Resort; Jar Test 1 - 8 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 20 | 0.06 | 90.8 | 0.041 | 28.1 | 0.30
J2 | 23 | 0.05 | 91.0 | 0.040 | 29.8 | 0.35
J3 | 26 | 0.04 | 91.2 | 0.039 | 31.6 | 0.24
J4 | 29 | 0.04 | 91.8 | 0.037 | 35.1 | 0.21
J5 | 32 | 0.05 | 91.6 | 0.037 | 35.1 | 0.26
J6 | 35 | 0.05 | 91.9 | 0.036 | 36.8 | 0.25
J7 | 38 | 0.05 | 92.1 | 0.035 | 38.6 | 0.26
J8 | 41 | 0.05 | 92.2 | 0.035 | 38.6 | 0.24

## Slide 12: Konocti Harbor Resort; Jar Test 9 - 12 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | AdvFloc CTC-0011 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 130 | 0.06 | 92.2 | 0.035 | 38.6 | 0.24
J10 | 140 | 0.06 | 92.5 | 0.033 | 42.1 | 0.32
J11 | 150 | 0.06 | 91.8 | 0.036 | 36.8 | 0.23
J12 | 160 | 0.06 | 92.0 | 0.036 | 36.8 | 0.16

## Slide 13: Konocti Harbor Resort; Jar Test 13 - 16 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | KMnO4 mg/L | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J13 | 0 | 32 | 0.06 | 91.6 | 0.037 | 35.1 | 0.19
J14 | 1.0 | 32 | 0.04 | 92.0 | 0.036 | 36.8 | 0.24
J15 | 2.0 | 32 | 0.05 | 91.5 | 0.038 | 33.3 | 0.27
J16 | 3.0 | 32 | 0.05 | 91.1 | 0.040 | 29.8 | 0.19
Note: KMnO4 was added and floc at 20 RPM for 75 minutes. At the end of the
floc period, coagulant was then added, flash and floc at 20 RPM for 5 minutes.

## Slide 14: Konocti Harbor Resort; Jar Test 17 - 20 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | KMnO4 mg/L | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 0 | 32 | 0.05 | 91.4 | 0.038 | 33.3 | 0.13
J18 | 1.0 | 32 | 0.05 | 91.6 | 0.037 | 35.1 | 0.15
J19 | 2.0 | 32 | 0.05 | 91.5 | 0.038 | 33.3 | 0.29
J20 | 3.0 | 32 | 0.07 | 90.9 | 0.041 | 28.1 | 0.36
Note: KMnO4 and coagulant were added at the same time and
floc at 20 RPM for 5 minutes.

## Slide 15: Konocti Harbor Resort; Jar Test 21 - 24 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | 9810 mg/L | C-378 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J21 | 32 | 0.0 | 0.06 | 91.7 | 0.037 | 35.1 | 0.16
J22 | 32 | 5.0 | 0.05 | 91.7 | 0.037 | 35.1 | 0.25
J23 | 50 | 0.0 | 0.04 | 92.0 | 0.036 | 36.8 | 0.22
J24 | 50 | 5.0 | 0.07 | 91.6 | 0.037 | 35.1 | 0.32

## Slide 16: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) No Pre-Oxidation Applied Coagulant 9810

## Slide 17: Jars 1-4: End of 5-minute flocculation (20 RPM) duration.
20 mg/L 9810
Filtrate 0.06 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 28.1%
Settled: 0.30 NTU
23 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 29.8%
Settled: 0.35 NTU
26 mg/L 9810
Filtrate 0.04 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 31.6%
Settled: 0.24 NTU
29 mg/L 9810
Filtrate 0.04 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction 35.1%
Settled: 0.21 NTU

## Slide 18: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 19: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
20 mg/L 9810
Filtrate 0.06 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 28.1%
Settled: 0.30 NTU
23 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 29.8%
Settled: 0.35 NTU
26 mg/L 9810
Filtrate 0.04 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 31.6%
Settled: 0.24 NTU
29 mg/L 9810
Filtrate 0.04 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction 35.1%
Settled: 0.21 NTU

## Slide 20: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) No Pre-Oxidation Applied Coagulant 9810

## Slide 21: Jars 5-8: End of 5-minute flocculation (20 RPM) duration.
32 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 35.1%
Settled: 0.26 NTU
35 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction 36.8%
Settled: 0.25 NTU
38 mg/L 9810
Filtrate 0.05 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction 38.6%
Settled: 0.26 NTU
41 mg/L 9810
Filtrate 0.05 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction 38.6%
Settled: 0.24 NTU

## Slide 22: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 23: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
32 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 35.1%
Settled: 0.26 NTU
35 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction 36.8%
Settled: 0.25 NTU
38 mg/L 9810
Filtrate 0.05 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction 38.6%
Settled: 0.26 NTU
41 mg/L 9810
Filtrate 0.05 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction 38.6%
Settled: 0.24 NTU

## Slide 24: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) No Pre-Oxidation Applied Coagulant AdvFloc CTC-00011

## Slide 25: Jars 9-12: End of 5-minute flocculation (20 RPM) duration.
130 mg/L CTC-0011
Filtrate 0.06 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction: 38.6%
Settled: 0.24 NTU
140 mg/L CTC-0011
Filtrate 0.06 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 42.1%
Settled: 0.32NTU
150 mg/L CTC-0011
Filtrate 0.06 NTU
UVT: 91.8%
UVA: 0.036/cm
UVA Reduction: 36.8%
Settled: 0.23 NTU
160 mg/L CTC-0011
Filtrate 0.06 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction: 36.8%
Settled: 0.16 NTU

## Slide 26: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 27: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
130 mg/L CTC-0011
Filtrate 0.06 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction: 38.6%
Settled: 0.24 NTU
140 mg/L CTC-0011
Filtrate 0.06 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 42.1%
Settled: 0.32NTU
150 mg/L CTC-0011
Filtrate 0.06 NTU
UVT: 91.8%
UVA: 0.036/cm
UVA Reduction: 36.8%
Settled: 0.23 NTU
160 mg/L CTC-0011
Filtrate 0.06 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction: 36.8%
Settled: 0.16 NTU

## Slide 28: Jars 13-16 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) Pre-Oxidation KMnO4 (75 min) Applied Coagulant 9810

## Slide 29: Jars 13-16: End of 5-minute flocculation (20 RPM) duration.
0 mg/L KMnO4
32 mg/L 9810
Filtrate 0.06 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 35.1%
Settled: 0.19 NTU
1.0 mg/L KMnO4
32 mg/L 9810
Filtrate 0.04 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction 36.8%
Settled: 0.24 NTU
2.0 mg/L KMnO4
32 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 33.3%
Settled: 0.27 NTU
2.0 mg/L KMnO4
32 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.1%
UVA: 0.040/cm
UVA Reduction 29.8%
Settled: 0.19 NTU

## Slide 30: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 31: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L KMnO4
32 mg/L 9810
Filtrate 0.06 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 35.1%
Settled: 0.19 NTU
1.0 mg/L KMnO4
32 mg/L 9810
Filtrate 0.04 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction 36.8%
Settled: 0.24 NTU
2.0 mg/L KMnO4
32 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 33.3%
Settled: 0.27 NTU
2.0 mg/L KMnO4
32 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.1%
UVA: 0.040/cm
UVA Reduction 29.8%
Settled: 0.19 NTU

## Slide 32: Jars 17-20 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) Pre-Oxidation KMnO4 (75 min with coagulant) Applied Coagulant 9810

## Slide 33: Jars 17-20: End of 5-minute flocculation (20 RPM) duration.
0 mg/L KMnO4
32 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction 33.3%
Settled: 0.13 NTU
1.0 mg/L KMnO4
32 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.6%
UVA: 0.036/cm
UVA Reduction 35.1%
Settled: 0.15 NTU
2.0 mg/L KMnO4
32 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 33.3%
Settled: 0.29 NTU
2.0 mg/L KMnO4
32 mg/L 9810
Filtrate 0.07 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 28.1%
Settled: 0.36 NTU

## Slide 34: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 35: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L KMnO4
32 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction 33.3%
Settled: 0.13 NTU
1.0 mg/L KMnO4
32 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.6%
UVA: 0.036/cm
UVA Reduction 35.1%
Settled: 0.15 NTU
2.0 mg/L KMnO4
32 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 33.3%
Settled: 0.29 NTU
2.0 mg/L KMnO4
32 mg/L 9810
Filtrate 0.07 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 28.1%
Settled: 0.36 NTU

## Slide 36: Jars 21-24 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) No Pre-Oxidation Applied Coagulant 9810 Clarifloc C-378

## Slide 37: Jars 21-24: End of 5-minute flocculation (30 RPM) duration.
32 mg/L 9810
Clarifloc C-378: 0 mg/L
Filtrate 0.06 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction 35.1%
Settled: 0.16 NTU
32 mg/L 9810
Clarifloc C-378: 5 mg/L
Filtrate 0.06 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction 35.1%
Settled: 0.25 NTU
50 mg/L 9810
Clarifloc C-378: 0 mg/L
Filtrate 0.04 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction 36.8%
Settled: 0.22 NTU
50 mg/L 9810
Clarifloc C-378: 5 mg/L
Filtrate 0.07 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 35.1%
Settled: 0.32 NTU

## Slide 38: Jars 21-24: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 39: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken.
32 mg/L 9810
Clarifloc C-378: 0 mg/L
Filtrate 0.06 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction 35.1%
Settled: 0.16 NTU
32 mg/L 9810
Clarifloc C-378: 5 mg/L
Filtrate 0.06 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction 35.1%
Settled: 0.25 NTU
50 mg/L 9810
Clarifloc C-378: 0 mg/L
Filtrate 0.04 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction 36.8%
Settled: 0.22 NTU
50 mg/L 9810
Clarifloc C-378: 5 mg/L
Filtrate 0.07 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 35.1%
Settled: 0.32 NTU

## Slide 40: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 41: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 42: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 43: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 44: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 45: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732