## Slide 1: Westport County Water District CA2300730 Mendocino County Jar Test
by Guy Schott, P.E.
May 5, 2025

## Slide 2: Westport CWD May 5, 2025
Wage Creek

## Slide 3: Westport CWS – Direct Filtration

## Slide 4: Westport County Water District – May 5, 2025
Source – Wage Creek
pH: 7.00
Fe: 0.259 mg/L
Mn: 100 ug/L
Alkalinity: 62 mg/L as CaCO3
Turbidity: 1.08 NTU
UVT: 92.65%,
UVA: 0.0332/cm
0.4 um Filtered
Turbidity: 0.25 NTU
UVT: 93.32%,
UVA: 0.030/cm
Post Filtration
Fe: 0.0 mg/L
Mn: 37 ug/L
Turbidity: 0.14 NTU
UVT: 97.04%,
UVA: 0.0131/cm
UVA Reduction: 56.3%

## Slide 5: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 6: Applied Coagulants for Jar Testing
NALCO 8186
10 - 30% Aluminum Chloride Hydroxide (ACH)
Polyamine (%?)
SG = 1.14 – 1.23
NSF limit: 100 mg/L as Product

## Slide 7: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 2.0, 1.0 or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 8: Filtrate and %UVT/UVA Analysis
For this study, all jars were samples for Filtrate and %UVT/UVA analysis immediately at the end of the flocculation period.

## Slide 9: Westport CWD; Jar Test 1 - 8 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | NALCO 8186 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction
J1 | 2.30 | 0.16 | 96.42 | 0.0159 | 47.0
J2 | 2.77 | 0.36 | 94.49 | 0.0247 | 17.7
J3 | 3.23 | 0.23 | 95.31 | 0.0209 | 30.3
J4 | 3.69 | 0.25 | 94.84 | 0.0230 | 23.3
J5 | 0.92 | 0.08 | 97.46 | 0.0112 | 62.7
J6 | 1.38 | 0.04 | 97.82 | 0.0096 | 68.0
J7 | 1.84 | 0.04 | 98.07 | 0.0085 | 71.7
J8 | 2.30 | 0.12 | 97.05 | 0.0130 | 56.7

## Slide 10: Westport CWD; Jar Test 9 - 16 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | NaOCl mg/L | NALCO 8186 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Cl2 mg/L | Mn ug/L
J9 | 0 | 1.15 | 0.15 | 97.18 | 0.0125 | 58.3 | - | -
J10 | 0 | 1.38 | 0.05 | 97.93 | 0.0091 | 69.7 | - | -
J11 | 0 | 1.61 | 0.04 | 98.12 | 0.0083 | 72.3 | - | -
J12 | 0 | 1.84 | 0.03 | 98.26 | 0.0076 | 74.7 | - | -
J13 | 0 | 1.61 | 0.04 | 98.02 | 0.0087 | 71.0 | - | -
J14 | 0 | 1.84 | 0.04 | 98.14 | 0.0082 | 72.7 | - | 94
J15 | 2.0 | 1.61 | 0.03 | 97.69 | 0.0102 | 66.0 | 2.0 | -
J16 | 2.0 | 1.84 | 0.03 | 97.90 | 0.0092 | 69.3 | 2.0 | 98

## Slide 11: Westport CWD; Jar Test 17 - 20 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | NaOCl mg/L | NALCO 8186 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Fe ug/L
J17 | 0 | 1.60 | 0.10 | 96.62 | 0.0150 | 50.0 | 23
J18 | 0 | 1.85 | 0.04 | 97.16 | 0.0125 | 58.3 | 5
J19 | 2.0 | 1.60 | 0.03 | 96.77 | 0.0143 | 52.3 | 0
J20 | 2.0 | 1.85 | 0.04 | 96.89 | 0.0138 | 54.0 | 0

## Slide 12: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant NALCO 8186

## Slide 13: Jars 1-4: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
NALCO 8186: 2.30 mg/L
Filtrate: 0.16 NTU
UVT: 97.1%
UVA: 0.0159/cm
UVA Reduction: 47.0%
NALCO 8186: 2.77 mg/L
Filtrate: 0.36 NTU
UVT: 94.49%
UVA: 0.0247/cm
UVA Reduction: 17.7%
NALCO 8186: 3.23 mg/L
Filtrate: 0.23 NTU
UVT: 94.49%
UVA: 0.0209/cm
UVA Reduction: 30.3%
NALCO 8186: 3.69 mg/L
Filtrate: 0.25 NTU
UVT: 94.84%
UVA: 0.0230/cm
UVA Reduction: 23.3%

## Slide 14: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant NALCO 8186

## Slide 15: Jars 5-8: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
NALCO 8186: 0.92 mg/L
Filtrate: 0.08 NTU
UVT: 97.46%
UVA: 0.0112/cm
UVA Reduction: 62.7%
NALCO 8186: 1.38 mg/L
Filtrate: 0.04 NTU
UVT: 97.82
UVA: 0.0096/cm
UVA Reduction: 68.0%
NALCO 8186: 1.84 mg/L
Filtrate: 0.04 NTU
UVT: 98.07
UVA: 0.0085/cm
UVA Reduction: 71.7%
NALCO 8186: 2.30 mg/L
Filtrate: 0.12 NTU
UVT: 98.07
UVA: 0.0085/cm
UVA Reduction: 71.7%

## Slide 16: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant NALCO 8186

## Slide 17: Jars 9-12: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
NALCO 8186: 1.15 mg/L
Filtrate: 0.15 NTU
UVT: 97.18%
UVA: 0.0125/cm
UVA Reduction: 58.3%
NALCO 8186: 1.38 mg/L
Filtrate: 0.05 NTU
UVT: 97.93%
UVA: 0.0091/cm
UVA Reduction: 69.7%
NALCO 8186: 1.61 mg/L
Filtrate: 0.04 NTU
UVT: 98.12%
UVA: 0.0083/cm
UVA Reduction: 72.3%
NALCO 8186: 1.84 mg/L
Filtrate: 0.03 NTU
UVT: 98.23%
UVA: 0.0076/cm
UVA Reduction: 74.7%

## Slide 18: Jars 13-16 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant NALCO 8186

## Slide 19: Jars 13-16: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
NaOCl: 0 mg/L
NALCO 8186: 1.61 mg/L
Filtrate: 0.04 NTU
UVT: 98.02%
UVA: 0.0087/cm
UVA Reduction: 71.0%
NaOCl: 0 mg/L
NALCO 8186: 1.84 mg/L
Filtrate: 0.04 NTU
UVT: 98.14%
UVA: 0.0082/cm
UVA Reduction: 72.7%
NaOCl: 2.0 mg/L
NALCO 8186: 1.61 mg/L
Filtrate: 0.03 NTU
UVT: 97.69%
UVA: 0.0102/cm
UVA Reduction: 66.0%
NaOCl: 2.0 mg/L
NALCO 8186: 1.84 mg/L
Filtrate: 0.03 NTU
UVT: 97.90%
UVA: 0.0092/cm
UVA Reduction: 69.3%

## Slide 20: Jars 17-20 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant NALCO 8186

## Slide 21: Jars 17-20: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA. Note: jar tested 12 days after collection.
NaOCl: 0 mg/L
NALCO 8186: 1.60 mg/L
Filtrate: 0.10 NTU
UVT: 96.62%
UVA: 0.0150/cm
UVA Reduction: 50.0%
NaOCl: 0 mg/L
NALCO 8186: 1.85 mg/L
Filtrate: 0.04 NTU
UVT: 97.16%
UVA: 0.0125/cm
UVA Reduction: 58.3%
NaOCl: 2.0 mg/L
NALCO 8186: 1.60 mg/L
Filtrate: 0.03 NTU
UVT: 96.77%
UVA: 0.0143/cm
UVA Reduction: 52.3%
NaOCl: 2.0 mg/L
NALCO 8186: 1.85 mg/L
Filtrate: 0.04 NTU
UVT: 96.89%
UVA: 0.0138/cm
UVA Reduction: 54.0%

## Slide 22: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 20-30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate). For this study, samples were taken immediately at the end of flocculation process.
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 23: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 24: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 25: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 26: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 27: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Jar Test Results/Procedures for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Jar Testing Done Right video training https://youtu.be/aGByyxhelkI
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732