## Slide 1: City of St. Helena CA2810004 Napa County Jar Test
by Guy Schott, P.E.
September 14, 2024

## Slide 2: Source Water: Bell Canyon Reservoir
Source Water Characteristics
Turbidity: 8.94 NTU
pH: 7.21
UVT: 69.21%
UVA: 0.1599/cm
0.4 um Filtered
UVT: 73.46%
UVA: 0.1340/cm

## Slide 3: Flocculation/Sedimentation Basins

## Slide 4: Bell Canyon Reservoir Source & Treated Water Characteristics, September 5, 2024
Source – Bell Canyon Reservoir
pH: 7.29
Alkalinity: 33.4 mg/L as CaCO3
Turbidity: 3.52 NTU
UVT: 66.54%,
UVA: 0.177/cm
0.4 um Filtered
Turbidity: 1.11 NTU
UVT: 68.60%,
UVA: 0.1637/cm
Filter 1 Water
pH: 6.50
Alkalinity: 12.6 mg/L as CaCO3
0.12 NTU
UVT: 91.25%,
UVA: 0.0398/cm
Clearwell Water
pH: 7.51
Alkalinity: 28.2 mg/L as CaCO3
0.63 NTU
UVT: 91.83%,
UVA: 0.0370/cm

## Slide 5: UVT/UVA, pathlength 40 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 6: Applied Coagulants for Jar Testing (1)
Aluminum Sulfate (Product)
Al2(SO4)3*14.3H20 (Liquid)
47.47% Aluminum Sulfate
52% Water
8.08% Al2O3
0% Basicity
SG = 1.325
NSF max use: 400 mg/L (product)
As hydrated Al2(SO4)3*14.3H20
17% Al2O3
Ferric Chloride
42.4% Ferric Chloride
47.6% Water
SG = 1.44
NSF limit: 250 mg/L as Product

## Slide 7: Applied Coagulants for Jar Testing (2)
Pro Pac 917 (NTU Technologies, Inc.)
10% polyamine (50% water, 50% active polyamines)
45% Aluminum Chlorohydrate (ACH)
~21.3% Al2O3
~11.3% Al
45% Water
83% Basicity
SG = 1.25-1.34
NSF limit: 100 mg/L as Product
NTU Technologies
Pro Pac 9810
45-50% Aluminum Chlorohydrate
45-50% Water
~22.4% Al2O3
~11.9% Al
83% Basicity
5% polyamine (50% water, 50% active polyamines)
SG = 1.25-1.34
NSF Max Use: 200 mg/L as Product;

## Slide 8: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.29
LCA #1
FeSO4: 61 mg/L
No pH adjustment.
LCA #2:
FeCl3: 40.6 mg/L
No pH adjustment

## Slide 9: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength). Aluminum sulfate is reported as Alum.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 10: City of St. Helena : Jar Test 1-4 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (9 min)
Jar # | Alum mg/L | FeCl3 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH
J1 | 50 | - | 0.05 | 89.07 | 0.0503 | 69.3 | 0.26 | 6.10
J2 | - | 36 | 0.16 | 85.84 | 0.0663 | 59.5 | 2.23 | 6.28
J3 | - | 40 | 0.40 | 82.90 | 0.0815 | 50.2 | 2.21 | 6.21
J4 | - | 44 | 0.27 | 86.47 | 0.0632 | 61.4 | 1.88 | 6.11
Source water jar testing was taken after Post NaMnO4

## Slide 11: City of St. Helena : Jar Test 5-8 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (8 min)
Jar # | FeSO4 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH
J5 | 50 | 0.08 | 90.41 | 0.0438 | 73.2 | 0.51 | 6.00
J6 | 55 | 0.12 | 90.15 | 0.0451 | 72.4 | 0.98 | 5.85
J7 | 60 | 0.13 | 90.82 | 0.0419 | 74.4 | 0.87 | 5.68
J8 | 65 | 0.09 | 91.71 | 0.0376 | 77.0 | 0.57 | 5.52
Source water jar testing was taken after Post NaMnO4

## Slide 12: City of St. Helena : Jar Test 9-12 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (9 min)
Jar # | FeCl3 mg/L | FeSO4 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH | Fe mg/L
J9 | 25 | - | 0.30 | 86.82 | 0.0614 | 62.5 | 1.04 | 6.28 | 0.000
J10 | 30 | - | 0.13 | 88.31 | 0.0540 | 67.0 | 0.57 | 6.09 | 0.033
J11 | - | 40 | 0.38 | 87.09 | 0.0601 | 63.3 | 2.06 | 6.22 | 0.032
J12 | - | 45 | 0.09 | 88.95 | 0.0509 | 68.9 | 0.52 | 6.10 | 0.051
Source water jar testing was taken after Post NaMnO4

## Slide 13: City of St. Helena : Jar Test 13-16 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (8 min)
Jar # | Alum mg/L | FeSO4 mg/L | Zeta Floc 20 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH
J13 | 50 | - | - | 0.06 | 88.83 | 0.0515 | 68.5 | 0.28 | 6.15
J14 | - | 60 | 1.0 | 0.05 | 91.54 | 0.0384 | 76.5 | 0.43 | 5.71
J15 | - | 65 | 1.0 | 0.05 | 92.22 | 0.0352 | 78.5 | 0.44 | 5.51
J16 | - | 70 | 1.0 | 0.05 | 92.64 | 0.0332 | 79.7 | 0.36 | 5.20
J17 | 50 | - | - | 0.05 | 89.11 | 0.0501 | 69.4 | 0.34 | 6.17
J18 | - | 70 | 1.0 | 0.04 | 93.03 | 0.0314 | 80.8 | 0.41 | 5.23
Source water jar testing was taken after Post NaMnO4
Jar 18 post filtrate Fe: 0.060 mg/L

## Slide 14: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 9 min (30 RPM) Post NaMnO4 Applied Coagulants Alum/FeCl3

## Slide 15: Jars 1-4: End of 7-minute flocculation (30 RPM) duration.
50 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.07%
UVA: 0.0503/cm
UVA Reduction: 69.3%
Settled: 0.26 NTU
pH: 6.10
50 mg/L FeCl3
Filtrate: 0.16 NTU
UVT: 88.84%
UVA: 0.0663/cm
UVA Reduction: 59.5%
Settled: 0.23 NTU
pH: 6.28
40 mg/L FeCl3
Filtrate: 0.40 NTU
UVT: 88.84%
UVA: 0.0815/cm
UVA Reduction: 50.2%
Settled: 2.21 NTU
pH: 6.21
44 mg/L FeCl3
Filtrate: 0.27 NTU
UVT: 88.47%
UVA: 0.0632/cm
UVA Reduction: 61.4%
Settled: 1.88 NTU
pH: 6.11

## Slide 16: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 17: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
50 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.07%
UVA: 0.0503/cm
UVA Reduction: 69.3%
Settled: 0.26 NTU
pH: 6.10
50 mg/L FeCl3
Filtrate: 0.16 NTU
UVT: 88.84%
UVA: 0.0663/cm
UVA Reduction: 59.5%
Settled: 0.23 NTU
pH: 6.28
40 mg/L FeCl3
Filtrate: 0.40 NTU
UVT: 88.84%
UVA: 0.0815/cm
UVA Reduction: 50.2%
Settled: 2.21 NTU
pH: 6.21
44 mg/L FeCl3
Filtrate: 0.27 NTU
UVT: 88.47%
UVA: 0.0632/cm
UVA Reduction: 61.4%
Settled: 1.88 NTU
pH: 6.11

## Slide 18: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 8 min (30 RPM) Post NaMnO4 Applied Coagulant FeSO4

## Slide 19: Jars 5-8: End of 8-minute flocculation (30 RPM) duration.
50 mg/L FeSO4
Filtrate: 0.08 NTU
UVT: 90.41%
UVA: 0.0438/cm
UVA Reduction: 73.4%
Settled: 0.51 NTU
pH: 6.00
55 mg/L FeSO4
Filtrate: 0.12 NTU
UVT: 90.15%
UVA: 0.0451/cm
UVA Reduction: 72.4%
Settled: 0.98 NTU
pH: 5.85
60 mg/L FeSO4
Filtrate: 0.13 NTU
UVT: 90.82%
UVA: 0.0419/cm
UVA Reduction: 74.4%
Settled: 0.87 NTU
pH: 5.68
65 mg/L FeSO4
Filtrate: 0.09 NTU
UVT: 91.71%
UVA: 0.0376/cm
UVA Reduction: 77.0%
Settled: 0.57 NTU
pH: 5.52

## Slide 20: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 21: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
50 mg/L FeSO4
Filtrate: 0.08 NTU
UVT: 90.41%
UVA: 0.0438/cm
UVA Reduction: 73.4%
Settled: 0.51 NTU
pH: 6.00
55 mg/L FeSO4
Filtrate: 0.12 NTU
UVT: 90.15%
UVA: 0.0451/cm
UVA Reduction: 72.4%
Settled: 0.98 NTU
pH: 5.85
60 mg/L FeSO4
Filtrate: 0.13 NTU
UVT: 90.82%
UVA: 0.0419/cm
UVA Reduction: 74.4%
Settled: 0.87 NTU
pH: 5.68
65 mg/L FeSO4
Filtrate: 0.09 NTU
UVT: 91.71%
UVA: 0.0376/cm
UVA Reduction: 77.0%
Settled: 0.57 NTU
pH: 5.52

## Slide 22: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 9 min (30 RPM) Post NaMnO4 Applied Coagulants FeCl3/FeSO4

## Slide 23: Jars 9-12: End of 9-minute flocculation (30 RPM) duration.
40 mg/L FeSO4
Filtrate: 0.38 NTU
UVT: 87.09%
UVA: 0.0601/cm
UVA Reduction: 63.3%
Settled: 2.06 NTU
pH: 6.22, Fe: 0.032 mg/L
45 mg/L FeSO4
Filtrate: 0.09 NTU
UVT: 88.9%
UVA: 0.0509/cm
UVA Reduction: 68.9%
Settled: 0.52 NTU
pH: 6.10, Fe: 0.051 mg/L
25 mg/L FeCl3
Filtrate: 0.30 NTU
UVT: 86.82%
UVA: 0.0614/cm
UVA Reduction: 62.5%
Settled: 1.04 NTU
pH: 6.28, Fe: 0.0 mg/L
30 mg/L FeCl3
Filtrate: 0.13 NTU
UVT: 88.31%
UVA: 0.0540/cm
UVA Reduction: 67.0%
Settled: 0.57 NTU
pH: 6.09, Fe: 0.033 mg/L

## Slide 24: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 25: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
40 mg/L FeSO4
Filtrate: 0.38 NTU
UVT: 87.09%
UVA: 0.0601/cm
UVA Reduction: 63.3%
Settled: 2.06 NTU
pH: 6.22, Fe: 0.032 mg/L
45 mg/L FeSO4
Filtrate: 0.09 NTU
UVT: 88.9%
UVA: 0.0509/cm
UVA Reduction: 68.9%
Settled: 0.52 NTU
pH: 6.10, Fe: 0.051 mg/L
25 mg/L FeCl3
Filtrate: 0.30 NTU
UVT: 86.82%
UVA: 0.0614/cm
UVA Reduction: 62.5%
Settled: 1.04 NTU
pH: 6.28, Fe: 0.0 mg/L
30 mg/L FeCl3
Filtrate: 0.13 NTU
UVT: 88.31%
UVA: 0.0540/cm
UVA Reduction: 67.0%
Settled: 0.57 NTU
pH: 6.09, Fe: 0.033 mg/L

## Slide 26: Jars 13-16 Test Flash Mix 30 Sec (200 RPM) Floc Mix 8 min (30 RPM) Post NaMnO4 Applied Coagulants Alum/FeSO4

## Slide 27: Jars 13-16: End of 8-minute flocculation (30 RPM) duration.
60 mg/L FeSO4
1.0 mg/L ZetaFloc 20
Filtrate: 0.05 NTU
UVT: 91.54%
UVA: 0.0384/cm
UVA Reduction: 76.5%
Settled: 0.43 NTU
pH: 5.71
65 mg/L FeSO4
1.0 mg/L ZetaFloc 20
Filtrate: 0.05 NTU
UVT: 92.22%
UVA: 0.0352/cm
UVA Reduction: 78.5%
Settled: 0.44 NTU
pH: 5.51
70 mg/L FeSO4
1.0 mg/L ZetaFloc 20
Filtrate: 0.05 NTU
UVT: 92.64%
UVA: 0.0332/cm
UVA Reduction: 79.7%
Settled: 0.36 NTU
pH: 5.20
50 mg/L Alum
Filtrate: 0.06 NTU
UVT: 88.83%
UVA: 0.0515/cm
UVA Reduction: 69.5%
Settled: 0.28 NTU
pH: 6.15

## Slide 28: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 29: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
60 mg/L FeSO4
1.0 mg/L ZetaFloc 20
Filtrate: 0.05 NTU
UVT: 91.54%
UVA: 0.0384/cm
UVA Reduction: 76.5%
Settled: 0.43 NTU
pH: 5.71
65 mg/L FeSO4
1.0 mg/L ZetaFloc 20
Filtrate: 0.05 NTU
UVT: 92.22%
UVA: 0.0352/cm
UVA Reduction: 78.5%
Settled: 0.44 NTU
pH: 5.51
70 mg/L FeSO4
1.0 mg/L ZetaFloc 20
Filtrate: 0.05 NTU
UVT: 92.64%
UVA: 0.0332/cm
UVA Reduction: 79.7%
Settled: 0.36 NTU
pH: 5.20
50 mg/L Alum
Filtrate: 0.06 NTU
UVT: 88.83%
UVA: 0.0515/cm
UVA Reduction: 69.5%
Settled: 0.28 NTU
pH: 6.15

## Slide 30: Jars 17-8 Test Flash Mix 30 Sec (200 RPM) Floc Mix 7 min (30 RPM) Post NaMnO4 Applied Coagulants Alum/FeSO4

## Slide 31: Jars 17-18: End of 8-minute flocculation (30 RPM) duration.
50 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.97%
UVA: 0.0501/cm
UVA Reduction: 69.4%
Settled: 0.34 NTU
pH: 6.17
70 mg/L FeSO4
1.0 mg/L ZetaFloc 20
Filtrate: 0.04 NTU
UVT: 92.99%
UVA: 0.0316/cm
UVA Reduction: 80.8%
Settled: 0.41 NTU
pH: 5.23, Fe: 0.06 mg/L

## Slide 32: Jars 17-18: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 33: Jars 17-18: After 25-minutes of settling, settled water turbidity is taken.
50 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.97%
UVA: 0.0501/cm
UVA Reduction: 69.4%
Settled: 0.34 NTU
pH: 6.17
70 mg/L FeSO4
1.0 mg/L ZetaFloc 20
Filtrate: 0.04 NTU
UVT: 92.99%
UVA: 0.0316/cm
UVA Reduction: 80.8%
Settled: 0.41 NTU
pH: 5.23, Fe: 0.06 mg/L

## Slide 34: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 35: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 36: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 37: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 38: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 39: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Jar Testing Done Right training video: https://www.youtube.com/watch?v=aGByyxhelkI
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732