## Slide 1: Nacimiento Water Company CA4010027 San Luis Obispo County Jar Test
by Guy Schott, P.E.
March 26, 2021

## Slide 2: Source Water: Nacimiento Lake

## Slide 3: Schematice
CA4010027
Nacimiento Water Company
653 Service Connections
Population 1828

## Slide 4: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (254 nm) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: Nacimiento Water Company Source & Treated Water Characteristics, March 26, 2021
Source
pH: 7.97
Alkalinity: 84 mg/L as CaCO3
Turbidity: 7.8 NTU
UVT: 67.2%,
UVA: 0.172/cm
0.4 um Filtered
Turbidity: 1.13 NTU
UVT: 73.2%,
UVA: 0.135/cm
Plant Filtrate Water (pre-chlorination
pH: 7.98
Alkalinity: 86 mg/L as CaCO3
Turbidity: 0.37 NTU
UVT: 85.6%,
UVA: 0.067/cm
0.4 um Filtered
Turbidity: 0.09 NTU
UVT: 85.7%,
UVA: 0.066/cm
Clearwell (post-chlorine)
Turbidity: 0.09 NTU
UVT: 90.3%,
UVA: 0.044/cm

## Slide 6: Applied Coagulants for Jar Testing (1)
Aluminum Sulfate (Product)
Al2(SO4)3*14.3H20 (Liquid)
48% Aluminum Sulfate
52% Water
8.2% Al2O3
4.3% Al
0% Basicity
SG = 1.32
NSF limit: 400 mg/L (product)
As hydrated Al2(SO4)3*14.3H20
17% Al2O3
Brenntag (559-485-4150)
Solenis
Praestol 186KH
SG = 1.0 – 1.2
Viscosity: 200-500 centipoise
MW: 250,00 g/moles
pDADMAC (20% active, 80% H2O)
NSF limit: 50 mg/L (product)
Product dose 5 mg/L = 1 mg/L pDADMAC active

## Slide 7: Applied Coagulants for Jar Testing (2)
Kemira Chemicals, Inc.
Superfloc 4814RS
SG = 1.0 – 1.1
Polyacrylamide
NSF limit: 3.5 mg/L (product)
BWS, Inc.
AdvFloc-CTC-00011
Polyaluminum Hydroxy Chlorosulfate
12.55% Al2O3
6.64% Al
64.9% Basicity
SG = 1.299
NSF limit: 250 mg/L as Product
Gregory F. Nieckarz, Ph.D.
Principal Consultant
SWS Consulting, LLC.
+1.541.953.5112
gregn.swsc@gmail.com

## Slide 8: Diallyldimethylammonium chloride or N-allyl-N,N-dimethylprop-2-en-1-aminium chloride pDADMAC C8H16ClN MW: 161.67 g/mol
N
+
CH3
CH3
CH2
CH
CH2
CH2
CH
CH2
Cl-

## Slide 9: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.8 (post KMnO4 oxidation)
LCA #1: Alum: 44 mg/L as hydrated
pH adjusted to 6.7 with acetic acid
LCA #2: AdvFloc CTC-00011: 142 mg/L
pH adjusted to 7.7 with acetic acid

## Slide 10: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Aluminum Sulfate doses are reported as hydrated Al2(SO4)3*14.3H20.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 11: Nacimiento Water Company; Source: Nacimiento Lake Summary of Plant Coagulant/Dose Jar vs. Optimum Dose and Coagulants
Jar# | KMnO4 mg/L | Alum mg/L | AdvFloc CTC-0011 mg/L | CatFloc 186KH mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
A | 3.0 | 35 | 0 | 6.0 | 0.04 | 89.9 | 0.046 | 65.9 | 2.01
vs. |  |  |  |  |  |  |  |  | 
B | 3.0 | 80 | 0 | 6.0 | 0.04 | 93.2 | 0.030 | 77.8 | 2.01
C | 3.0 | 0 | 200 | 6.0 | 0.04 | 93.5 | 0.029 | 78.5 | 0.42

## Slide 12: Jar Test – Filtrate Water Spiked with 2.2 mg/L NaOCl Plant Coagulant Dose vs. Optimum Dose and Coagulant
Chart: Chlorine Residual Over Time
| 0 | 0.21666666666666667 | 0.7416666666666667 | 1.2166666666666666 | 1.7208333333333332 | 2.1999999999999997 | 3.1999999999999997 | 4.166666666666667 | 5.166666666666667 | 6.166666666666667 | 6.645833333333333 | 7.916666666666667 | 0 | 0
Alum: 35 mg/L, CatFloc 186KH: 6.0 mg/L, UVA: 0.049/cm | 1.69 | 0.55 | 0.18 | 0.16 | 0.06 | 0.06 | 0.04
Alum: 80 mg/L, CatFloc 186KH: 6.0 mg/L, UVA: 0.031/cm | 1.98 | 1.11 | 0.8 | 0.66 | 0.54 | 0.43 | 0.3 | 0.2 | 0.12 | 0.08 | 0.05 | 0.03
CTC-0011: 200 mg/L, CatFloc 186KH: 6.0 mg/L, UVA: 0.029/cm | 1.99 | 1.24 | 0.98 | 0.85 | 0.72 | 0.67 | 0.54 | 0.45 | 0.42 | 0.34 | 0.3 | 0.2

## Slide 13: Source Water: (pH: 7.97, Alkalinity: 84 mg/L)
Coagulant | Chemical Dose, mg/L | Alkalinity Consumed mg/L as CaCO3 | Treated Water Alkalinity mg/L as CaCO3
Alum (dry) | 35 | 17.5 | 66.5
Alum (dry) | 80 | 40.1 | 43.9
AdvFloc | 200 | 25.9 | 58.1

## Slide 14: Nacimiento WC: TTHMs/HAA5s Laboratory Results NaOCl dose after filtration: 2.4 mg/L (72 hrs hold time, 3 days); Second NaOCl dose 1 mg/L (at 72 hrs), (48 hrs hold time, 2 days); DBPs measurements (5 days total hold time)
Coagulant (Dose, mg/L) | Filtrate Aluminum mg/L | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | TTHM ug/L | HAA5 ug/L | Cl2 Residual mg/L
Alum (35); 186KH (6.0) | - | 89.9 | 0.046 | 65.9 | 90 | 63 | 0.47
Alum (80); 186KH (6.0) | 0.031 | 93.2 | 0.030 | 77.8 | 59 | 40 | 0.77
CTC-0011 (200); 186KH (6.0) | 0.036 | 93.5 | 0.029 | 78.5 | 61 | 41 | 0.79

## Slide 15: Nacimiento WC; Nacimiento Lake; Jar Test 1 - 8 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | Alum mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 35 | 0.24 | 85.4 | 0.068 | 49.6 | 4.67
J2 | 40 | 0.79 | 84.4 | 0.073 | 45.9 | 5.29
J3 | 45 | 0.49 | 86.2 | 0.064 | 52.6 | 3.92
J4 | 50 | 0.22 | 87.9 | 0.055 | 59.3 | 2.48
J5 | 55 | 0.30 | 87.7 | 0.056 | 58.5 | 2.60
J6 | 60 | 0.08 | 88.9 | 0.051 | 62.2 | 2.78
J7 | 65 | 0.35 | 88.5 | 0.052 | 61.5 | 2.58
J8 | 70 | 0.26 | 89.2 | 0.049 | 63.7 | 2.35

## Slide 16: Nacimiento WC; Nacimiento Lake; Jar Test 9 - 16 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | Alum mg/L | CatFloc 186KH mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 70 | 0 | 0.09 | 89.9 | 0.046 | 65.9 | 2.25
J10 | 70 | 2.0 | 0.16 | 90.0 | 0.045 | 66.7 | 2.11
J11 | 70 | 4.0 | 0.08 | 90.6 | 0.042 | 68.9 | 2.57
J12 | 70 | 6.0 | 0.04 | 91.0 | 0.040 | 70.4 | 3.09
J13 | 65 | 6.0 | 0.06 | 91.3 | 0.039 | 71.1 | 2.45
J14 | 70 | 6.0 | 0.05 | 91.6 | 0.037 | 72.6 | 2.95
J15 | 75 | 6.0 | 0.04 | 91.9 | 0.036 | 73.3 | 2.67
J16 | 80 | 6.0 | 0.06 | 92.3 | 0.034 | 74.8 | 2.73

## Slide 17: Nacimiento WC; Nacimiento Lake; Jar Test 17 - 24 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | AdvFloc CTC-0011 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 140 | 0.07 | 90.5 | 0.043 | 68.1 | 0.58
J18 | 150 | 0.09 | 90.6 | 0.042 | 68.9 | 0.62
J19 | 160 | 0.11 | 90.5 | 0.043 | 68.1 | 0.71
J20 | 170 | 0.06 | 90.9 | 0.041 | 69.6 | 0.28
J21 | 180 | 0.09 | 91.0 | 0.040 | 70.4 | 0.57
J22 | 190 | 0.05 | 91.4 | 0.039 | 71.1 | 0.46
J23 | 200 | 0.09 | 91.4 | 0.039 | 71.1 | 0.51
J24 | 210 | 0.07 | 91.9 | 0.036 | 73.3 | 0.27

## Slide 18: Nacimiento WC; Nacimiento Lake; Jar Test 25 - 32 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | AdvFloc CTC-0011 mg/L | CatFloc 186KH mg/L | Superfloc 4814RS mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J25 | 160 | 0.0 | 0.0 | 0.10 | 90.7 | 0.042 | 68.9 | 0.60
J26 | 160 | 6.0 | 0.0 | 0.10 | 91.6 | 0.038 | 71.9 | 1.09
J27 | 200 | 0.0 | 0.0 | 0.10 | 91.4 | 0.039 | 71.1 | 0.65
J28 | 200 | 6.0 | 0.0 | 0.08 | 92.0 | 0.036 | 73.3 | 0.90
J29 | 200 | 0.0 | 0.0 | 0.09 | 91.5 | 0.038 | 71.9 | 0.44
J30 | 200 | 6.0 | 0.0 | 0.08 | 92.2 | 0.035 | 74.1 | 0.92
J31 | 200 | 0.0 | 0.3 | 0.08 | 91.5 | 0.038 | 71.9 | 0.50
J32 | 200 | 6.0 | 0.3 | 0.09 | 92.1 | 0.035 | 74.1 | 0.80

## Slide 19: Nacimiento WC; Nacimiento Lake; Jar Test 33 - 40 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | KMnO4 mg/L | Alum mg/L | AdvFloc CTC-0011 mg/L | CatFloc 186KH mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J33 | 0.0 | 80 | 0.0 | 6.0 | 0.05 | 91.5 | 0.038 | 71.9 | 2.86
J34 | 1.5 | 80 | 0.0 | 6.0 | 0.03 | 92.2 | 0.035 | 74.1 | 2.03
J35 | 2.5 | 80 | 0.0 | 6.0 | 0.06 | 92.5 | 0.033 | 75.6 | 2.38
J36 | 3.5 | 80 | 0.0 | 6.0 | 0.03 | 93.2 | 0.030 | 77.8 | xx
J37 | 3.0 | 35 | 0.0 | 6.0 | 0.06 | 89.2 | 0.049 | 63.7 | 2.13
J38 | 3.0 | 80 | 0.0 | 6.0 | 0.04 | 92.9 | 0.031 | 77.0 | 2.11
J39 | 0.0 | 0.0 | 200 | 6.0 | 0.09 | 92.8 | 0.032 | 76.3 | 0.53
J40 | 3.0 | 0.0 | 200 | 6.0 | 0.09 | 93.4 | 0.029 | 78.5 | 0.77

## Slide 20: Nacimiento WC; Nacimiento Lake; Jar Test 41 - 44 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min) Jars 41, 42 & 44 were used for TTHM/HAA5 analysis
Jar# | KMnO4 mg/L | Alum mg/L | AdvFloc CTC-0011 mg/L | CatFloc 186KH mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J41 | 3.0 | 35 | 0.0 | 6.0 | 0.04 | 89.9 | 0.046 | 65.9 | 2.01
J42 | 3.0 | 80 | 0.0 | 6.0 | 0.04 | 93.2 | 0.030 | 77.8 | 2.01
J43 | 3.0 | 0.0 | 180 | 6.0 | 0.07 | 93.1 | 0.030 | 77.8 | 0.71
J44 | 3.0 | 0.0 | 200 | 6.0 | 0.04 | 93.5 | 0.029 | 78.5 | 0.42

## Slide 21: Jars 1-4 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (20 RPM) No Pre-Oxidation Applied Coagulant Alum

## Slide 22: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
35 mg/L Alum
Filtrate 0.24 NTU
UVT: 85.4%
UVA: 0.068/cm
UVA Reduction 49.6%
Settled: 4.67 NTU
40 mg/L Alum
Filtrate 0.79 NTU
UVT: 84.4%
UVA: 0.073/cm
UVA Reduction 45.9%
Settled: 5.29 NTU
45 mg/L Alum
Filtrate 0.49 NTU
UVT: 86.2%
UVA: 0.064/cm
UVA Reduction 52.6%
Settled: 3.92 NTU
50 mg/L Alum
Filtrate 0.22 NTU
UVT: 87.9%
UVA: 0.055/cm
UVA Reduction 59.3%
Settled: 2.48 NTU

## Slide 23: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 24: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
35 mg/L Alum
Filtrate 0.24 NTU
UVT: 85.4%
UVA: 0.068/cm
UVA Reduction 49.6%
Settled: 4.67 NTU
40 mg/L Alum
Filtrate 0.79 NTU
UVT: 84.4%
UVA: 0.073/cm
UVA Reduction 45.9%
Settled: 5.29 NTU
45 mg/L Alum
Filtrate 0.49 NTU
UVT: 86.2%
UVA: 0.064/cm
UVA Reduction 52.6%
Settled: 3.92 NTU
50 mg/L Alum
Filtrate 0.22 NTU
UVT: 87.9%
UVA: 0.055/cm
UVA Reduction 59.3%
Settled: 2.48 NTU

## Slide 25: Jars 5-8 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (20 RPM) No Pre-Oxidation Applied Coagulant Alum

## Slide 26: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
55 mg/L Alum
Filtrate 0.30 NTU
UVT: 87.7%
UVA: 0.056/cm
UVA Reduction 58.5%
Settled: 2.60 NTU
60 mg/L Alum
Filtrate 0.08 NTU
UVT: 88.9%
UVA: 0.051/cm
UVA Reduction 62.2%
Settled: 2.78 NTU
65 mg/L Alum
Filtrate 0.35 NTU
UVT: 88.5%
UVA: 0.052/cm
UVA Reduction 61.5%
Settled: 2.58 NTU
70 mg/L Alum
Filtrate 0.26 NTU
UVT: 89.2%
UVA: 0.049/cm
UVA Reduction 63.7%
Settled: 2.35 NTU

## Slide 27: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 28: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
55 mg/L Alum
Filtrate 0.30 NTU
UVT: 87.7%
UVA: 0.056/cm
UVA Reduction 58.5%
Settled: 2.60 NTU
60 mg/L Alum
Filtrate 0.08 NTU
UVT: 88.9%
UVA: 0.051/cm
UVA Reduction 62.2%
Settled: 2.78 NTU
65 mg/L Alum
Filtrate 0.35 NTU
UVT: 88.5%
UVA: 0.052/cm
UVA Reduction 61.5%
Settled: 2.58 NTU
70 mg/L Alum
Filtrate 0.26 NTU
UVT: 89.2%
UVA: 0.049/cm
UVA Reduction 63.7%
Settled: 2.35 NTU

## Slide 29: Jars 9-12 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (20 RPM) No Pre-Oxidation Applied Coagulants Alum 186KH

## Slide 30: Jars 9-12: End of 5-minute flocculation (30 RPM) duration.
70 mg/L Alum
0.0 mg/L 186KH
Filtrate 0.09 NTU
UVT: 89.9%
UVA: 0.046/cm
UVA Reduction 65.9%
Settled: 2.25 NTU
70 mg/L Alum
2.0 mg/L 186KH
Filtrate 0.16 NTU
UVT: 90.0%
UVA: 0.045/cm
UVA Reduction 66.7%
Settled: 2.11 NTU
70 mg/L Alum
4.0 mg/L 186KH
Filtrate 0.08 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 68.9%
Settled: 2.57 NTU
70 mg/L Alum
6.0 mg/L 186KH
Filtrate 0.04 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 70.4%
Settled: 3.09 NTU

## Slide 31: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 32: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
70 mg/L Alum
0.0 mg/L 186KH
Filtrate 0.09 NTU
UVT: 89.9%
UVA: 0.046/cm
UVA Reduction 65.9%
Settled: 2.25 NTU
70 mg/L Alum
2.0 mg/L 186KH
Filtrate 0.16 NTU
UVT: 90.0%
UVA: 0.045/cm
UVA Reduction 66.7%
Settled: 2.11 NTU
70 mg/L Alum
4.0 mg/L 186KH
Filtrate 0.08 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 68.9%
Settled: 2.57 NTU
70 mg/L Alum
6.0 mg/L 186KH
Filtrate 0.04 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 70.4%
Settled: 3.09 NTU

## Slide 33: Jars 13-16 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (20 RPM) No Pre-Oxidation Applied Coagulants Alum 186KH

## Slide 34: Jars 13-16: End of 5-minute flocculation (30 RPM) duration.
65 mg/L Alum
6 mg/L 186KH
Filtrate 0.09 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction 71.1%
Settled: 2.45 NTU
70 mg/L Alum
6 mg/L 186KH
Filtrate 0.05 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 72.6%
Settled: 2.95 NTU
75 mg/L Alum
6 mg/L 186KH
Filtrate 0.04 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction 73.3%
Settled: 2.67 NTU
80 mg/L Alum
6 mg/L 186KH
Filtrate 0.06 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction 74.8%
Settled: 2.73 NTU

## Slide 35: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 36: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
65 mg/L Alum
6 mg/L 186KH
Filtrate 0.09 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction 71.1%
Settled: 2.45 NTU
70 mg/L Alum
6 mg/L 186KH
Filtrate 0.05 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 72.6%
Settled: 2.95 NTU
75 mg/L Alum
6 mg/L 186KH
Filtrate 0.04 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction 73.3%
Settled: 2.67 NTU
80 mg/L Alum
6 mg/L 186KH
Filtrate 0.06 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction 74.8%
Settled: 2.73 NTU

## Slide 37: Jars 17-20 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) No Pre-Oxidation Applied Coagulant AdvFloc CTC-00011

## Slide 38: Jars 17-20: End of 5-minute flocculation (30 RPM) duration.
140 mg/L CTC-0011
Filtrate 0.07 NTU
UVT: 90.5%
UVA: 0.043/cm
UVA Reduction 68.1%
Settled: 0.58 NTU
150 mg/L CTC-0011
Filtrate 0.09 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 68.9%
Settled: 0.62 NTU
160 mg/L CTC-0011
Filtrate 0.11 NTU
UVT: 90.5%
UVA: 0.043/cm
UVA Reduction 68.1%
Settled: 0.71 NTU
170 mg/L CTC-0011
Filtrate 0.06 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 69.6%
Settled: 0.28 NTU

## Slide 39: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 40: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.
140 mg/L CTC-0011
Filtrate 0.07 NTU
UVT: 90.5%
UVA: 0.043/cm
UVA Reduction 68.1%
Settled: 0.58 NTU
150 mg/L CTC-0011
Filtrate 0.09 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 68.9%
Settled: 0.62 NTU
160 mg/L CTC-0011
Filtrate 0.11 NTU
UVT: 90.5%
UVA: 0.043/cm
UVA Reduction 68.1%
Settled: 0.71 NTU
170 mg/L CTC-0011
Filtrate 0.06 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 69.6%
Settled: 0.28 NTU

## Slide 41: Jars 21-24 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) No Pre-Oxidation Applied Coagulant AdvFloc CTC-00011

## Slide 42: Jars 21-24: End of 5-minute flocculation (30 RPM) duration.
180 mg/L CTC-0011
Filtrate 0.09 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 70.4%
Settled: 057 NTU
190 mg/L CTC-0011
Filtrate 0.05 NTU
UVT: 91.4%
UVA: 0.039/cm
UVA Reduction 71.1%
Settled: 0.46 NTU
200 mg/L CTC-0011
Filtrate 0.09 NTU
UVT: 91.4%
UVA: 0.039/cm
UVA Reduction 71.1%
Settled: 0.51 NTU
210 mg/L CTC-0011
Filtrate 0.07 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction 73.3%
Settled: 0.27 NTU

## Slide 43: Jars 21-24: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 44: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken.
180 mg/L CTC-0011
Filtrate 0.09 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 70.4%
Settled: 0.57 NTU
190 mg/L CTC-0011
Filtrate 0.05 NTU
UVT: 91.4%
UVA: 0.039/cm
UVA Reduction 71.1%
Settled: 0.46 NTU
200 mg/L CTC-0011
Filtrate 0.09 NTU
UVT: 91.4%
UVA: 0.039/cm
UVA Reduction 71.1%
Settled: 0.51 NTU
210 mg/L CTC-0011
Filtrate 0.07 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction 73.3%
Settled: 0.27 NTU

## Slide 45: Jars 25-28 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) No Pre-Oxidation Applied Coagulants AdvFloc CTC-00011 186KH

## Slide 46: Jars 25-28: End of 5-minute flocculation (30 RPM) duration.
160 mg/L CTC-0011
0 mg/L 186KH
Filtrate 0.10 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction 68.9%
Settled: 0.60 NTU
160 mg/L CTC-0011
6 mg/L 186KH
Filtrate 0.10 NTU
UVT: 91.6%
UVA: 0.038/cm
UVA Reduction 71.9%
Settled: 1.09 NTU
200 mg/L CTC-0011
0 mg/L 186KH
Filtrate 0.10 NTU
UVT: 91.4%
UVA: 0.039/cm
UVA Reduction 71.1%
Settled: 0.65 NTU
200 mg/L CTC-0011
6 mg/L 186KH
Filtrate 0.08 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction 73.3%
Settled: 0.90 NTU

## Slide 47: Jars 25-28: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 48: Jars 25-28: After 25-minutes of settling, settled water turbidity is taken.
160 mg/L CTC-0011
0 mg/L 186KH
Filtrate 0.10 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction 68.9%
Settled: 0.60 NTU
160 mg/L CTC-0011
6 mg/L 186KH
Filtrate 0.10 NTU
UVT: 91.6%
UVA: 0.038/cm
UVA Reduction 71.9%
Settled: 1.09 NTU
200 mg/L CTC-0011
0 mg/L 186KH
Filtrate 0.10 NTU
UVT: 91.4%
UVA: 0.039/cm
UVA Reduction 71.1%
Settled: 0.65 NTU
200 mg/L CTC-0011
6 mg/L 186KH
Filtrate 0.08 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction 73.3%
Settled: 0.90 NTU

## Slide 49: Jars 29-32 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) No Pre-Oxidation Applied Coagulants AdvFloc CTC-00011 186KH Superfloc 4814RS

## Slide 50: Jars 29-32: End of 5-minute flocculation (30 RPM) duration.
200 mg/L CTC-0011
0 mg/L 186KH
Filtrate 0.09 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 71.9%
Settled: 0.44 NTU
200 mg/L CTC-0011
6 mg/L 186KH
Filtrate 0.08 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction 74.1%
Settled: 0.92 NTU
200 mg/L CTC-0011
6 mg/L 186KH
0.3 mg/L 4814RS
Filtrate 0.09 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction 74.1%
Settled: 0.80 NTU
200 mg/L CTC-0011
0 mg/L 186KH
0.3 mg/L 4814RS
Filtrate 0.08 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 71.9%
Settled: 0.50 NTU

## Slide 51: Jars 29-32: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 52: Jars 29-32: After 25-minutes of settling, settled water turbidity is taken.
200 mg/L CTC-0011
0 mg/L 186KH
Filtrate 0.09 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 71.9%
Settled: 0.44 NTU
200 mg/L CTC-0011
6 mg/L 186KH
Filtrate 0.08 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction 74.1%
Settled: 0.92 NTU
200 mg/L CTC-0011
6 mg/L 186KH
0.3 mg/L 4814RS
Filtrate 0.09 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction 74.1%
Settled: 0.80 NTU
200 mg/L CTC-0011
0 mg/L 186KH
0.3 mg/L 4814RS
Filtrate 0.08 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 71.9%
Settled: 0.50 NTU

## Slide 53: Jars 33-36 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) Pre-Oxidation KMnO4 (70 min) Applied Coagulants AdvFloc CTC-00011 186KH

## Slide 54: Jars 33-36: End of 5-minute flocculation (30 RPM) duration.
0 mg/L KMnO4
80 mg/L Alum
6 mg/L 186KH
Filtrate 0.05 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 71.9%
Settled: 2.86 NTU
1.5 mg/L KMnO4
80 mg/L Alum
6 mg/L 186KH
Filtrate 0.03 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction 74.1%
Settled: 2.03 NTU
2.5 mg/L KMnO4
80 mg/L Alum
6 mg/L 186KH
Filtrate 0.06 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 75.6%
Settled: 2.38 NTU
3.5 mg/L KMnO4
80 mg/L Alum
6 mg/L 186KH
Filtrate 0.03 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction 77.8%
Settled: 3.1 NTU

## Slide 55: Jars 33-36: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 56: Jars 33-36: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L KMnO4
80 mg/L Alum
6 mg/L 186KH
Filtrate 0.05 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 71.9%
Settled: 2.86 NTU
1.5 mg/L KMnO4
80 mg/L Alum
6 mg/L 186KH
Filtrate 0.03 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction 74.1%
Settled: 2.03 NTU
2.5 mg/L KMnO4
80 mg/L Alum
6 mg/L 186KH
Filtrate 0.06 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 75.6%
Settled: 2.38 NTU
3.5 mg/L KMnO4
80 mg/L Alum
6 mg/L 186KH
Filtrate 0.03 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction 77.8%
Settled: 3.1 NTU

## Slide 57: Jars 37-40 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) Pre-Oxidation KMnO4 Applied Coagulants Alum AdvFloc CTC-00011 186KH

## Slide 58: Jars 37-40: End of 5-minute flocculation (30 RPM) duration.
3 mg/L KMnO4
35 mg/L Alum
6 mg/L 186KH
Filtrate 0.06 NTU
UVT: 89.2%
UVA: 0.049/cm
UVA Reduction 63.7%
Settled: 2.13 NTU
3 mg/L KMnO4
80 mg/L Alum
6 mg/L 186KH
Filtrate 0.04 NTU
UVT: 92.9%
UVA: 0.031/cm
UVA Reduction 77.0%
Settled: 2.11 NTU
0 mg/L KMnO4
200 mg/L CTC-0011
6 mg/L 186KH
Filtrate 0.09 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction 76.3%
Settled: 0.53 NTU
3 mg/L KMnO4
200 mg/L CTC-0011
6 mg/L 186KH
Filtrate 0.09 NTU
UVT: 93.4%
UVA: 0.029/cm
UVA Reduction 78.4%
Settled: 0.77 NTU

## Slide 59: Jars 37-40: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 60: Jars 37-40: After 25-minutes of settling, settled water turbidity is taken.
3 mg/L KMnO4
35 mg/L Alum
6 mg/L 186KH
Filtrate 0.06 NTU
UVT: 89.2%
UVA: 0.049/cm
UVA Reduction 63.7%
Settled: 2.13 NTU
3 mg/L KMnO4
80 mg/L Alum
6 mg/L 186KH
Filtrate 0.04 NTU
UVT: 92.9%
UVA: 0.031/cm
UVA Reduction 77.0%
Settled: 2.11 NTU
0 mg/L KMnO4
200 mg/L CTC-0011
6 mg/L 186KH
Filtrate 0.09 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction 76.3%
Settled: 0.53 NTU
3 mg/L KMnO4
200 mg/L CTC-0011
6 mg/L 186KH
Filtrate 0.09 NTU
UVT: 93.4%
UVA: 0.029/cm
UVA Reduction 78.4%
Settled: 0.77 NTU

## Slide 61: Jars 41-44 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) Pre-Oxidation KMnO4 Applied Coagulants Alum AdvFloc CTC-00011 186KH

## Slide 62: Jars 41-44: End of 5-minute flocculation (30 RPM) duration.
3 mg/L KMnO4
35 mg/L Alum
6 mg/L 186KH
Filtrate 0.04 NTU
UVT: 89.9%
UVA: 0.046/cm
UVA Reduction 65.9%
Settled: 2.01 NTU
3 mg/L KMnO4
80 mg/L Alum
6 mg/L 186KH
Filtrate 0.04 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction 77.8%
Settled: 2.01 NTU
3 mg/L KMnO4
180 mg/L CTC-0011
6 mg/L 186KH
Filtrate 0.07 NTU
UVT: 93.1%
UVA: 0.030/cm
UVA Reduction 77.8%
Settled: 0.71 NTU
3 mg/L KMnO4
200 mg/L CTC-0011
6 mg/L 186KH
Filtrate 0.04 NTU
UVT: 93.5%
UVA: 0.029/cm
UVA Reduction 78.5%
Settled: 0.42 NTU

## Slide 63: Jars 41-44: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 64: Jars 41-44: After 25-minutes of settling, settled water turbidity is taken.
3 mg/L KMnO4
35 mg/L Alum
6 mg/L 186KH
Filtrate 0.04 NTU
UVT: 89.9%
UVA: 0.046/cm
UVA Reduction 65.9%
Settled: 2.01 NTU
3 mg/L KMnO4
80 mg/L Alum
6 mg/L 186KH
Filtrate 0.04 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction 77.8%
Settled: 2.01 NTU
3 mg/L KMnO4
180 mg/L CTC-0011
6 mg/L 186KH
Filtrate 0.07 NTU
UVT: 93.1%
UVA: 0.030/cm
UVA Reduction 77.8%
Settled: 0.71 NTU
3 mg/L KMnO4
200 mg/L CTC-0011
6 mg/L 186KH
Filtrate 0.04 NTU
UVT: 93.5%
UVA: 0.029/cm
UVA Reduction 78.5%
Settled: 0.42 NTU

## Slide 65: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 66: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 67: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 68: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 69: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 70: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732