## Slide 1: Sonoma County CSA 41 - Freestone CA4900549 Sonoma County Jar Test
by Guy Schott, P.E.
August 6, 2019

## Slide 2: Source Water: Wells/Spring Sources - Blended

## Slide 3: Sonoma County CSA 41 - Freestone Water Characteristics, August 6, 2019
Source
Turbidity: 8.4 NTU
pH: 7.57
Unfiltered
UVT: 87.2%
UVA/cm: 0.059
Filtered: 0.4 um absolute filter
UVT: 94.8% UVA: 0.023
Turbidity: 0.12 NTU

## Slide 4: UVT/UVA
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: Applied Coagulants for Jar Testing
NTU Technologies
Pro Pac 9810
45-50% Aluminum Chlorohydrate
45-50% Water
~22.4% Al2O3
~11.9% Al
83% Basicity
5% polyamine (50% water, 50% active polyamines)
SG = 1.25-1.34
NSF Max Use: 200 mg/L as Product;
Product dose 40 mg/L = 1 mg/L polyamines active
Pro Pac 9890 (NTU Technologies)
35-45% Aluminum Chlorohydrate
20% polyamine (50% water, 50% active polyamines)
35-45% Water
~18.9% Al2O3
~10.5% Al
83% Basicity
SG = 1.25-1.34
NSF limit: 50 mg/L as Product;
Product dose 10 mg/L = 1 mg/L polyamines active

## Slide 6: Applied Coagulants for Jar Testing Set 1
Pro Pac 9890 (NTU Technologies)
35-45% ACH
35-45% Water
20% Proprietary
SG = 1.25 – 1.34
Pro Pac 9810 (NTU Technologies)
45-50% Aluminum Chlorohydrate (ACH)
45-50% Water
5% Proprietary
SG = 1.25 - 1.34

## Slide 7: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.57
LCA #1:
9810: 7.5 mg/L as product
(no pH adjustment)
LCA #2:
7076: >270 mg/L as product
(no pH adjustment)

## Slide 8: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 9: Sonoma County CSA 41 – Freestone; Jar Test 1-4 Results Flash Mix 200 RPM (60 sec); Floc Mix 30 RPM (5 min)
Jar | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 7.0 | 0.17 | 96.5 | 0.015 | 34.8 | 6.6
J2 | 7.5 | 0.17 | 96.6 | 0.015 | 34.8 | 6.5
J3 | 8.0 | 0.18 | 96.2 | 0.017 | 26.1 | 6.7
J4 | 8.5 | 0.20 | 96.0 | 0.018 | 21.7 | 6.0

## Slide 10: Sonoma County CSA 41 – Freestone; Jar Test 5-12 Results Flash Mix 200 RPM (60 sec); Floc Mix 30 RPM (5 min)
Jar | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J5 | 7.0 | 0.07 | 97.2 | 0.012 | 47.8 | 5.5
J6 | 7.5 | 0.12 | 96.5 | 0.015 | 34.8 | 5.9
J7 | 8.0 | 0.12 | 96.8 | 0.014 | 39.1 | 7.0
J8 | 8.5 | 0.10 | 96.7 | 0.015 | 34.8 | 6.2
J9 | 6.0 | 0.18 | 97.0 | 0.013 | 43.5 | 6.3
J10 | 6.5 | 0.14 | 97.1 | 0.013 | 43.5 | 6.3
J11 | 7.0 | 0.15 | 97.1 | 0.013 | 43.5 | 7.0
J12 | 7.5 | 0.18 | 96.9 | 0.014 | 39.1 | 6.7

## Slide 11: Sonoma County CSA 41 – Freestone; Jar Test 13-20 Results Flash Mix 200 RPM (60 sec); Floc Mix 30 RPM (5 min)
Jar | Pre-NaOCl | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J13 | Yes | 7.0 | 0.09 | 96.8 | 0.014 | 39.1 | 4.3
J14 | Yes | 7.5 | 0.06 | 97.0 | 0.013 | 43.5 | 4.2
J15 | Yes | 8.0 | 0.10 | 96.6 | 0.015 | 34.8 | 4.8
J16 | Yes | 8.5 | 0.10 | 96.7 | 0.015 | 34.8 | 4.9
J17 | Yes | 7.0 | 0.19 | 96.6 | 0.015 | 34.8 | 6.2
J18 | Yes | 7.5 | 0.17 | 96.8 | 0.014 | 39.1 | 6.5
J19 | Yes | 8.0 | 0.13 | 96.8 | 0.014 | 39.1 | 7.0
J20 | Yes | 8.5 | 0.13 | 96.9 | 0.014 | 39.1 | 7.1

## Slide 12: Sonoma County CSA 41 – Freestone; Jar Test 21-24 Results Flash Mix 200 RPM (60 sec); Floc Mix 30 RPM (5 min)
Jar | Pre-NaOCl | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J21 | Yes | 7.0 | 0.14 | 96.8 | 0.014 | 39.1 | 5.3
J22 | Yes | 7.5 | 0.19 | 96.6 | 0.015 | 34.8 | 5.7
J23 | Yes | 8.0 | 0.15 | 96.9 | 0.014 | 39.1 | 5.5
J24 | Yes | 8.5 | 0.14 | 96.9 | 0.014 | 39.1 | 5.0

## Slide 13: Jars 1-4 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9810

## Slide 14: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
7.0 mg/L 9810
Filtrate 0.17 NTU
UVT: 96.5%
UVA: 0.015/cm
Settled: 6.6 NTU
7.5 mg/L 9810
Filtrate 0.17 NTU
UVT: 96.6%
UVA: 0.015/cm
Settled: 6.5 NTU
8.0 mg/L 9810
Filtrate 0.18 NTU
UVT: 96.2%
UVA: 0.017/cm
Settled: 6.7 NTU
8.5 mg/L 9810
Filtrate 0.20 NTU
UVT: 96.0%
UVA: 0.018/cm
Settled: 6.0 NTU

## Slide 15: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 16: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken
7.0 mg/L 9810
Filtrate 0.17 NTU
UVT: 96.5%
UVA: 0.015/cm
Settled: 6.6 NTU
7.5 mg/L 9810
Filtrate 0.17 NTU
UVT: 96.6%
UVA: 0.015/cm
Settled: 6.5 NTU
8.0 mg/L 9810
Filtrate 0.18 NTU
UVT: 96.2%
UVA: 0.017/cm
Settled: 6.7 NTU
8.5 mg/L 9810
Filtrate 0.20 NTU
UVT: 96.0%
UVA: 0.018/cm
Settled: 6.0 NTU

## Slide 17: Visual of Filterability of Jars 1-4

## Slide 18: Jars 5-8 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9890

## Slide 19: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
7.0 mg/L 9890
Filtrate 0.07 NTU
UVT: 97.2%
UVA: 0.012/cm
Settled: 5.5 NTU
7.5 mg/L 9890
Filtrate 0.12 NTU
UVT: 96.5%
UVA: 0.015/cm
Settled: 5.9 NTU
8.0 mg/L 9890
Filtrate 0.12 NTU
UVT: 96.8%
UVA: 0.014/cm
Settled: 7.0 NTU
8.5 mg/L 9890
Filtrate 0.10 NTU
UVT: 96.8%
UVA: 0.015/cm
Settled: 6.2 NTU

## Slide 20: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 21: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken
7.0 mg/L 9890
Filtrate 0.07 NTU
UVT: 97.2%
UVA: 0.012/cm
Settled: 5.5 NTU
7.5 mg/L 9890
Filtrate 0.12 NTU
UVT: 96.5%
UVA: 0.015/cm
Settled: 5.9 NTU
8.0 mg/L 9890
Filtrate 0.12 NTU
UVT: 96.8%
UVA: 0.014/cm
Settled: 7.0 NTU
8.5 mg/L 9890
Filtrate 0.10 NTU
UVT: 96.8%
UVA: 0.015/cm
Settled: 6.2 NTU

## Slide 22: Jars 9-12 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9890

## Slide 23: Jars 9-12: End of 5-minute flocculation (30 RPM) duration.
7.0 mg/L 9890
Filtrate 0.15 NTU
UVT: 97.1%
UVA: 0.013/cm
Settled: 7.0 NTU
7.5 mg/L 9890
Filtrate 0.18 NTU
UVT: 96.9%
UVA: 0.014/cm
Settled: 6.7 NTU
6.0 mg/L 9890
Filtrate 0.18 NTU
UVT: 97.0%
UVA: 0.013/cm
Settled: 6.3 NTU
6.5 mg/L 9890
Filtrate 0.14 NTU
UVT: 97.1%
UVA: 0.013/cm
Settled: 6.3 NTU

## Slide 24: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 25: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken
6.0 mg/L 9890
Filtrate 0.18 NTU
UVT: 97.0%
UVA: 0.013/cm
Settled: 6.3 NTU
6.5 mg/L 9890
Filtrate 0.14 NTU
UVT: 97.1%
UVA: 0.013/cm
Settled: 6.3 NTU
7.0 mg/L 9890
Filtrate 0.15 NTU
UVT: 97.1%
UVA: 0.013/cm
Settled: 7.0 NTU
7.5 mg/L 9890
Filtrate 0.18 NTU
UVT: 96.9%
UVA: 0.014/cm
Settled: 6.7 NTU

## Slide 26: Jars 13-16 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9810 w/NaOCl

## Slide 27: Jars 13-16: End of 5-minute flocculation (30 RPM) duration.
7.0 mg/L 9810
Filtrate 0.09 NTU
UVT: 96.8%
UVA: 0.014/cm
Settled: 4.3 NTU
7.5 mg/L 9810
Filtrate 0.06 NTU
UVT: 97.0%
UVA: 0.013/cm
Settled: 4.2 NTU
8.0 mg/L 9810
Filtrate 0.10 NTU
UVT: 96.6%
UVA: 0.015/cm
Settled: 4.8 NTU
8.5 mg/L 9810
Filtrate 0.10 NTU
UVT: 96.7%
UVA: 0.015/cm
Settled: 4.9 NTU

## Slide 28: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 29: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken
7.0 mg/L 9810
Filtrate 0.09 NTU
UVT: 96.8%
UVA: 0.014/cm
Settled: 4.3 NTU
7.5 mg/L 9810
Filtrate 0.06 NTU
UVT: 97.0%
UVA: 0.013/cm
Settled: 4.2 NTU
8.0 mg/L 9810
Filtrate 0.10 NTU
UVT: 96.6%
UVA: 0.015/cm
Settled: 4.8 NTU
8.5 mg/L 9810
Filtrate 0.10 NTU
UVT: 96.7%
UVA: 0.015/cm
Settled: 4.9 NTU

## Slide 30: Visual of Filterability of Jars 13-16

## Slide 31: Jars 17-20 Test No Flash Mixing Floc Mix 5 min (30 RPM) Applied Coagulant 9810 w/NaOCl

## Slide 32: Jars 17-20: End of 5-minute flocculation (30 RPM) duration.
7.0 mg/L 9810
Filtrate 0.19 NTU
UVT: 96.6%
UVA: 0.015/cm
Settled: 6.2 NTU
7.5 mg/L 9810
Filtrate 0.17 NTU
UVT: 96.8%
UVA: 0.014/cm
Settled: 6.5 NTU
8.0 mg/L 9810
Filtrate 0.13 NTU
UVT: 96.8%
UVA: 0.014/cm
Settled: 7.0 NTU
8.5 mg/L 9810
Filtrate 0.13 NTU
UVT: 96.9%
UVA: 0.014/cm
Settled: 7.1 NTU

## Slide 33: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 34: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken
7.0 mg/L 9810
Filtrate 0.19 NTU
UVT: 96.6%
UVA: 0.015/cm
Settled: 6.2 NTU
7.5 mg/L 9810
Filtrate 0.17 NTU
UVT: 96.8%
UVA: 0.014/cm
Settled: 6.5 NTU
8.0 mg/L 9810
Filtrate 0.13 NTU
UVT: 96.8%
UVA: 0.014/cm
Settled: 7.0 NTU
8.5 mg/L 9810
Filtrate 0.13 NTU
UVT: 96.9%
UVA: 0.014/cm
Settled: 7.1 NTU

## Slide 35: Visual of Filterability of Jars 17-20

## Slide 36: Jars 21-24 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9810 w/NaOCl

## Slide 37: Jars 21-24: End of 5-minute flocculation (30 RPM) duration.
7.0 mg/L 9810
Filtrate 0.14 NTU
UVT: 96.8%
UVA: 0.014/cm
Settled: 5.3 NTU
7.5 mg/L 9810
Filtrate 0.19 NTU
UVT: 96.6%
UVA: 0.015/cm
Settled: 5.7 NTU
8.0 mg/L 9810
Filtrate 0.15 NTU
UVT: 96.9%
UVA: 0.014/cm
Settled: 5.5 NTU
8.5 mg/L 9810
Filtrate 0.14 NTU
UVT: 96.9%
UVA: 0.014/cm
Settled: 5.0 NTU

## Slide 38: Jars 21-24: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 39: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken
7.0 mg/L 9810
Filtrate 0.14 NTU
UVT: 96.8%
UVA: 0.014/cm
Settled: 5.3 NTU
7.5 mg/L 9810
Filtrate 0.19 NTU
UVT: 96.6%
UVA: 0.015/cm
Settled: 5.7 NTU
8.0 mg/L 9810
Filtrate 0.15 NTU
UVT: 96.9%
UVA: 0.014/cm
Settled: 5.5 NTU
8.5 mg/L 9810
Filtrate 0.14 NTU
UVT: 96.9%
UVA: 0.014/cm
Settled: 5.0 NTU

## Slide 40: Visual of Filterability of Jars 21-24

## Slide 41: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 42: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 43: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 44: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 45: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 46: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Jar Testing Done Right training video: https://www.youtube.com/watch?v=aGByyxhelkI
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732