### INTRODUCTION

In order to determine compliance with the Surface Water Treatment Rule (SWTR) disinfection requirements, public water systems that use surface water sources must know the disinfectant contact time in their treatment process units.  The California Cities, California operates a public water system that fits into this category.  On November 20, 1997, a tracer study was performed to estimate disinfectant contact time for the chlorine contact tank at the California Cities Water Treatment Plant (Cal Cities clearwell).

The Cal Cities clearwell was retrofitted with three inter-hypalon baffles in 1996, to increase disinfectant contact time and minimize short-circuiting.  Appendix A contains a plain view diagram of the treatment facility and a diagram of the Cal Cities clearwell.  Water discharges out of a 12-inch pipe located at the bottom of the clearwell; goes around three baffles that create serpentine flow; and then exits through a 12-inch pipe located at the bottom of the clearwell.

The product of the chlorine concentration in the Cal Cities clearwell and the time that the chlorine is in contact with the water (CT) is used to determine if sufficient inactivation of viruses and Giardia has been achieved.  Calculated CT values are compared with CT values found on tables in the 1989 USEPA Guidance Manual for Compliance with the Filtration and Disinfection Requirements for Public Water Systems Using Surface Water Sources (USEPA Guidance Manual).  These CT tables take into account the type and concentration of the disinfectant, contact time, pH, and temperature.  If a calculated CT value meets or exceeds the CT value on the table that corresponds to the required level of inactivation, adequate disinfection has occurred.

There are different methods by which CT is calculated.  The USEPA Guidance Manual recommends that the value used for T in the calculation of CT be T10.   For this reason, the USEPA Guidance Manual assigns estimated T10/T values for treatment process units based on the baffling conditions within the units.  The baffling condition within the Cal Cities clearwell is most similar to what is classified as “average” in the USEPA Guidance Manual.  The USEPA Guidance Manual describes the “average” baffling condition as having a “baffled inlet or outlet with some intrabasin baffles” and assigns a T10/T value of 0.5 to this baffling condition.   This value can be used to estimate T10 for the Cal Cities clearwell, but a T10 result from a tracer study is preferred.

The effluent chlorine residual concentration is often used in CT calculations.  When single concentration values such as the effluent concentration are used, chlorine concentration variations within process units are not taken into account.  Effective CT (introduced by Teefy and Singer, 1990) considers variations in chlorine concentrations and disinfectant contact times.  The effective CT is calculated based on first order kinetics of chlorine decay and a residence time distribution obtained from a tracer study.

### PURPOSE

The purpose of the tracer study was to measure the disinfectant contact time for the Cal Cities clearwell.  Values of T10 and effective CT were obtained from the tracer study results.  The T10 value established by the tracer study was compared with a T10 value estimated using the USEPA Guidance Manual.  Both of these T10 values were used to calculate CT and to determine the corresponding degree of inactivation.  Lastly, these CT calculations were compared with the effective CT.

The California Department of Health Services, Division of Drinking Water and Environmental Management, Drinking Water Field Operations Branch wishes to collect disinfectant contact time information from tracer tests conducted on water treatment process units throughout California.  The T10 result and other information related to disinfection and flow characteristics within the Cal Cities clearwell will be entered into the statewide database.

# EXPERIMENTAL AND ANALYTICAL PROCEDURES

The test parameters are summarized in Table 1.  A step-input test was conducted for 387 minutes using fluoride as the tracer.  During the test, the Cal Cities clearwell contained approximately 132,560 gallons of water and the flow rate through it was 1,000 gpm.

Powdered sodium fluoride was dissolved in water to create the tracer solution.  Injection and sampling points are shown on the Cal Cities clearwell diagram in Appendix A.  Throughout the test, this solution was injected into a transmission pipe that leads from the GAC filters to the Cal Cities clearwell.  Effluent samples were collected on the discharge side of the high service pumps.  In addition to the effluent samples, influent samples were collected downstream from the tracer injection point in the transmission pipe that leads from the GAC filters to the Cal Cities clearwell.  All samples were stored in 60-mL polyethylene bottles.  An ion-selective electrode was used for the fluoride analyses.

Table 1. Test Parameters

##### Step-input test

Plant flow rate during test = 100% design capacity = 1,000 gpm

#### Chlorine contact tank volume during test = minimum operating volume = 132,560 gallons

Theoretical detention time of chlorine contact tank = 132.6 minutes

Test run time = 3 * theoretical detention time = 398 min = 6.63 hours

Tracer: Sodium Fluoride manufactured by Chemtech

- pH at saturation = 7.6

- solubility at 25 oC = 4.05 g per 100 g H2O

- 45.25% fluoride ion

- 97% chemical purity

- 97 lb/ft3 bulk density

Tracer dose = 2.10 mg/L

17.37 lbs. dry sodium fluoride required

51.4 gallons H2O minimum required to dissolve 17.37-lbs. dry sodium fluoride

113.7 gallons H2O used

Solution concentration = 8,042 mg/L

Feed pump capacity = 497 gpd = 1306.4 mL/min

Feed pump setting = 1000.0 mL/min

In order to determine T10, a time series plot of the following function, F(t), was made:

Ft=Ci−CoCf−Co

Ci is the effluent fluoride concentration, Co is the background fluoride concentration, and Cf is the final or ultimate fluoride concentration.  (On a plot of F(t), T10 is the time at which F(t) equals 0.10.)

Effective CT was also determined.  The following equation was used to calculate effective CT:

Effective CT=tiEidtCCloe−kti

CClo is the influent or initial chlorine concentration, k is the chlorine decay rate constant and ti is the time.  Ei is the value of the residence time distribution function and is equal to F(t)/t.

RESULTS

The tracer study results are tabulated in Appendix B.  The targeted fluoride dose was 2.10 mg/l, but the final observed fluoride concentration was 1.52 mg/l.  Incomplete sodium fluoride dissolution in the tracer solution storage tank was the most likely cause of the difference between the targeted and observed fluoride doses.  At the end of the test, powder that resembled undissolved sodium fluoride was seen at the bottom of the tracer solution storage tank.  In previous tracer tests, undissolved powdered fluoride was also observed.  Mr. Doug Boyer, a chemist with Chemtech Product was contacted afterwards in regards to this problem.  He said that coarse sodium fluoride is extremely difficult to dissolve regardless of the solution water temperature.  In Mr. Boyer’s laboratory work, the coarse fluoride is ground to a fine powder to get better dissolution.  Mr. Boyer recommends purchasing powdered fluoride, which will dissolve more readily.

To achieve three theroretical detention times, the target run length was 398 minutes.   However, the actual run length was 387 minutes.  This occurred because the feed pump setting was slightly greater than the required 1000 ml/min to offset the expected lower dose rate as seen in previous tracer studies.  As a result, the fluoride solution ran out before three theoretical detention times were achieved.

Figure 1.  Time Series Plot of F(t)

A time series plot of F(t) is shown above in Figure 1.  From the plot of F(t), a T10 value of 66 minutes was obtained.  A T10 value of 66 minutes was also computed using the T10/T value from the EPA Guidance Manual (0.5) and a theoretical detention time (T) of 132.6 minutes.  The tracer test required maximum plant flow rate and minimum tank operating volume.  These conditions were selected in order to generate a “worst case” T10 value for the Cal Cities clearwell.  A “worst case” value was desired because only one tracer test was planned.  If other tracer studies are conducted, lower flow rates and higher tank operating volumes should be used.

In conducting a step-input test, the test should run long enough to achieve steady-state concentration.  That is, the concentration applied to the influent of a tank should be equal to the tracer concentration at the effluent of the tank or cascade of tanks that are being evaluated to validate the data before the test is ended.  In general, it is best to run a tracer test for three to four theoretical detention times.  In basins that do not exhibit significant short-circuiting, steady-state tracer concentration for a step input test may be reached in as little as two theoretical detention times.

In the Cal Cities study, the effluent concentration did not reach steady-state even though the test length was approximately three theoretical detention times.  At the end of the test, the effluent fluoride concentration was showed to be increasing at a very small rate.  The most probable reason steady-state was not achieved is due in part that a small percent of water from the distribution system is continuously recycled back into the treatment process for use.  During the tracer study, the recycled water had the effect of increasing the background fluoride concentration over time.  Water from the distribution is recycled to three locations in the plant.  Approximately 15 gpm is used for solution water for post-chlorination, 20 gpm for the sprinklers in the sedimentation basins, and 15 gpm is used for solution water for pre-chlorination.  Because the recycle streams contained a significant fluoride concentration during the test, background fluoride concentration would increase incremental over time, which would result in the effluent concentration having small incremental increases.  Thus, effluent concentration from the contact tank would take a very long time to reach steady-state.

Applied mathematical calculations were used to subtract the increase in fluoride concentration due only to the recycle water used for post chlorination.  The basis for these calculations was an assumption that each incremental increase in fluoride concentration at the influent of the contact tank would take on the same hydraulic shape as the overall normalized concentration curve.  An equation was developed for this curve and used to develop a concentration versus time curve for each incremental increase in fluoride concentration at the inlet of the contact tank to obtain a family of concentration curves for the recycled water.  These curves were then summed to get one concentration versus time curve.  The concentration value per time on the recycled curve was then subtracted from the initially measured effluent minus background fluoride concentrations to obtain a new curve.  An equation was developed for this curve that was used to recalculate new recycled curves.  As previously done, these curve were then summed to get one concentration versus time curve.  Again, the concentration value per time on the new recycled curve was subtracted from the initially measured effluent minus background fluoride concentrations to obtain a new curve.  This iteration was repeated until the equation for the overall normalized curve remained constant.  By including the 15 gpm of recycled water, the final fluoride concentration changed by approximately 0.015 mg/L (1%), which was a very small change.

The recycled water streams for the pre chlorination and the sprinklers were not used in the calculations because these water streams go through other reactors with unknown hydraulic curves.  In addition, some of this recycled fluoride probably reacted with the coagulate chemical which would reduce the fluoride concentration.  Thus, not all of the incremental increases in fluoride concentration can be accounted for but it is suspected that the overall results would change little.

Influent samples, downstream of the sodium fluoride injection point, were taken periodically throughout the test.  Measurements of the influent samples can be used for validating a step-input test by determining if the test reached steady-state.  Influent samples were taken approximately forty-five feet down stream from the sodium fluoride injection point.  There were no bends in this section of pipe to increase mixing turbulence.  The measured influent fluoride samples ranged from 1.22 to 1.66 mg/L as F-.  Maximum measured fluoride concentration in the effluent was 1.67 mg/L.  It was suspected that there was inadequate mixing in the forty-five foot section pipe that would explain the range in measured influent concentrations.  In addition, as described above, the influent concentration would tend to increase due to the recycled fluoridated water.  Influent concentration showed to increase overtime.

There were bends in the influent pipe, after the influent sample point, that should have mixed the chemical completely in the pipeline before the contact tank.  As a rule of thumb, lengths equal to 50 pipe diameters are required to mix the chemical completely in a pipeline stream (introduced by AWWA, 1996).  Cal Cities had approximately 45 pipe diameters between the injection point and influent sample point.

Factors associated with the design of the Cal Cities clearwell could also explain the T10 result.  According to Bishop et al (1993), low length-to-width and length-to-depth ratios are associated with increased axial dispersion within process units.  The Cal Cities clearwell’s length-to-width and length-to-depth ratios (14:1 and 17:1, respectively) fall in the predictive range for the T10 value based on Bishop’s study.

Table 2 lists the results of CT values calculated by different methods and the corresponding log inactivations assigned by the USEPA Guidance Manual.  Although the CT values differ quite significantly, they all meet the required log inactivation.  Compliance may be demonstrated by using any of the three methods presented.

Table 2. CT Results

| Method | CT [(mg/L)-min] | Log Inactivation of Giardia * |
| --- | --- | --- |
| T = T10 = 66 min. assigned by USEPA Guidance Manual | 92.4 | 3.6 |
| T = T10 = 66 min. determined by tracer study | 92.4 | 3.6 |
| Effective CT determined by tracer study | 178.5 | 7.1 |

* Notes:	1. Required log reduction and inactivation of Giardia cyst is 3 log.  CA Cities uses conventional filtration and receives 2.5 log removal credit.  Therefore, disinfection must meet 0.5 log inactivation.

2. CT table used to interpolate log inactivation of Giardia cyst using free chlorine was for pH = 7.0, chlorine concentration = 1.4 mg/L, and temp = 15oC.

3.	The log inactivation credit for the effective CT can not be directly looked up on the CT tables since each elemental CT has a different chlorine residual.  However, the effluent chlorine residual can be used to approximate log inactivation of Giardia cyst.  The log inactivation value for the effective CT presented in the table was based on the weighted average of each fluid element.

CONCLUSION

The Cal Cities clearwell tracer study generated a T10 value of 66 minutes and a T10/T value of 0.50.  These values will be used in the future by the California Cities to determine compliance with the disinfection requirements of the Surface Water Treatment Rule.

REFERENCES

AWWA. Tracer Studies in Water Treatment Facilities: A Protocol and Case Studies. AWWA Research Foundation and American Water Works Association (1996).

BISHOP, M.M.; MORGAN, J.M.; CORNWELL, B. & JAMISON, D.K. Improving the Disinfection Detention Time of a Water Plant Clearwell. Jour AWWA, 85:3:68 (Mar. 1993).

LEVENSPIEL, O. Chemical Reaction Engineering. John Wiley and Sons, New York (2nd ed., 1962).

TEEFY, S.M. & SINGER, P.C. Performance and Analysis of Tracer Tests to Determine Compliance of a Disinfection Scheme With the SWTR. Jour AWWA, 82:12:88 (Dec. 1990).

USEPA. Guidance Manual for Compliance with the Filtration and Disinfection Requirements for Public Water Systems Using Surface Water Sources. Washington, D.C. (1989).

T10 is defined as the detention time at which 90 percent of the water passing through a tank or process unit is retained within the tank or process unit.  T is defined as the theoretical detention time of a tank or process unit. T10/T is sometimes called the “short-circuiting factor”.

? Cal Cities clearwell meets the USEPA definition of intrabasin baffling but does not meet the condition for inlet baffling.

The Hach Combination Fluoride Electrode Model 50265 was used.

(Measured fluoride concentration minus background fluoride concentration) divided by (final fluoride concentration – minus background fluoride concentration).