### INTRODUCTION

In order to determine compliance with the Surface Water Treatment Rule (SWTR) disinfection requirements, public water systems that use surface water sources must know the disinfectant contact time in their treatment process units.  The City of Cloverdale, California operates a public water system that fits into this category.  On August 9, 1996, a tracer study was performed to estimate disinfectant contact time for the chlorine contact tank at the City of Cloverdale’s Water Treatment Plant (City’s clearwell).

The City’s clearwells were designed with eight inter-hypalon baffles in 1996, to increase disinfectant contact time and minimize short-circuiting.  Appendix A contains a plain view diagram of the treatment facility and a diagram of one of the two identical clearwells.  Water discharges out of a 12-inch pipe located at the bottom of each clearwell; goes around eight baffles that create serpentine flow; and then exits through a 12-inch pipe located five feet off the bottom clearwell.

The product of the chlorine concentration in the City’s clearwell and the time that the chlorine is in contact with the water (CT) is used to determine if sufficient inactivation of viruses and Giardia has been achieved.  Calculated CT values are compared with CT values found on tables in the 1989 USEPA Guidance Manual for Compliance with the Filtration and Disinfection Requirements for Public Water Systems Using Surface Water Sources (USEPA Guidance Manual).  These CT tables take into account the type and concentration of the disinfectant, contact time, pH, and temperature.  If a calculated CT value meets or exceeds the CT value on the table that corresponds to the required level of inactivation, adequate disinfection has occurred.

There are different methods by which CT is calculated.  The USEPA Guidance Manual recommends that the value used for T in the calculation of CT be T10.   For this reason, the USEPA Guidance Manual assigns estimated T10/T values for treatment process units based on the baffling conditions within the units.  The baffling condition within the City’s clearwell is most similar to what is classified as “superior” in the USEPA Guidance Manual.  The USEPA Guidance Manual describes the “superior” baffling condition as having a “perforated inlet baffle; serpentine or perforated intrabasin baffles; outlet weir or perforated launders” and assigns a T10/T value of 0.7 to this baffling condition.   This value can be used to estimate T10 for the City’s clearwells, but a T10 result from a tracer study is preferred.

The effluent chlorine residual concentration is often used in CT calculations.  When single concentration values such as the effluent concentration are used, chlorine concentration variations within process units are not taken into account.  Effective CT (introduced by Teefy and Singer, 1990) considers variations in chlorine concentrations and disinfectant contact times.  The effective CT is calculated based on first order kinetics of chlorine decay and a residence time distribution obtained from a tracer study.

### PURPOSE

The purpose of the tracer study was to measure the disinfectant contact time for the City of Cloverdale clearwells.  Values of T10 and effective CT were obtained from the tracer study results.  The T10 value established by the tracer study was compared with a T10 value estimated using the USEPA Guidance Manual.  Both of these T10 values were used to calculate CT and to determine the corresponding degree of inactivation.  Lastly, these CT calculations were compared with the effective CT.

The California Department of Health Services, Division of Drinking Water and Environmental Management, Drinking Water Field Operations Branch wishes to collect disinfectant contact time information from tracer tests conducted on water treatment process units throughout California.  The T10 result and other information related to disinfection and flow characteristics within the City’s clearwell will be entered into the statewide database.

# EXPERIMENTAL AND ANALYTICAL PROCEDURES

The test parameters are summarized in Table 1.  A step-input test was conducted for 147 minutes using fluoride as the tracer.  During the test, the clearwell that was modeled contained approximately 47,400 gallons of water and the flow rate through it was 1,000 gpm.

Powdered sodium fluoride was dissolved in water to create the tracer solution.  Injection and sampling points are shown on the City’s clearwell diagram in Appendix A.  Throughout the test, this solution was injected into a transmission pipe that leads from the filters transmission pumps to the City’s clearwell.  Effluent samples were collected on the discharge side of the clearwell in service.  In addition to the effluent samples, influent samples were collected downstream from the tracer injection point in the transmission pipe that leads to the City’s clearwells.  All samples were stored in 100-mL polyethylene bottles.  The SPADNS Method was used for the fluoride analyses.

Table 1. Test Parameters

##### Step-input test

Plant flow rate during test = 100% design capacity = 1,000 gpm

#### Chlorine contact tank volume during test = operating volume = 47,400 gallons

Theoretical detention time of chlorine contact tank = 47.4 minutes

Test run time = 3.1 * theoretical detention time = 47.4 min = 2.45 hours

Tracer: Sodium Fluoride manufactured by Chemtech

- pH at saturation = 7.6

- solubility at 25 oC = 4.05 g per 100 g H2O

- 45.25% fluoride ion

- 97% chemical purity

- 97 lb/ft3 bulk density

Tracer dose = 1.89 mg/L

8.5 lbs. dry sodium fluoride required

25.2 gallons H2O minimum required to dissolve 8.5-lbs. dry sodium fluoride

49.3 gallons H2O used

Solution concentration = 9,077 mg/L

Feed pump capacity = 497 gpd = 1306.4 mL/min

Feed pump setting = 800.0 mL/min

In order to determine T10, a time series plot of the following function, F(t), was made:

Ft=Ci−CoCf−Co

Ci is the effluent fluoride concentration, Co is the background fluoride concentration, and Cf is the final or ultimate fluoride concentration.  On a plot of F(t), T10 is the time at which F(t) equals 0.10.

Effective CT was also determined.  The following equation was used to calculate effective CT:

Effective CT=tiEidtCCloe−kti

CClo is the influent or initial chlorine concentration, k is the chlorine decay rate constant and ti is the time.  Ei is the value of the residence time distribution function and is equal to F(t)/t.

RESULTS

The tracer study results are tabulated in Appendix B.  The targeted fluoride dose was 1.89 mg/l, but the final observed fluoride concentration was 1.36 mg/l.  Incomplete sodium fluoride dissolution in the tracer solution storage tank was the most likely cause of the difference between the targeted and observed fluoride doses.  At the end of the test, powder that resembled undissolved sodium fluoride was seen at the bottom of the tracer solution storage tank.  In tracer tests following the City of Cloverdale, undissolved powdered fluoride was also observed.  Mr. Doug Boyer, a chemist with Chemtech Product was contacted in regards to this problem.  He said that coarse sodium fluoride is extremely difficult to dissolve regardless of the solution water temperature.  In Mr. Boyer’s laboratory work, the coarse fluoride is ground to a fine powder to get better dissolution.  Mr. Boyer recommends purchasing powdered fluoride, which will dissolve more readily.

Figure 1.  Time Series Plot of F(t)

A time series plot of F(t) is shown above in Figure 1.  From the plot of F(t), a T10 value of 37 minutes was obtained.  A T10 value of 33 minutes was computed using the T10/T value from the EPA Guidance Manual (0.7) and a theoretical detention time (T) of 47.4 minutes.  The tracer test required maximum plant flow rate and near minimum tank operating volume.  These conditions were selected in order to generate a “worst case” T10 value for the City’s clearwell.  A “worst case” value was desired because only one tracer test was planned.  If other tracer studies are conducted, lower flow rates and higher tank operating volumes should be used.

In conducting a step-input test, the test should run long enough to achieve steady-state concentration.  That is, the concentration applied to the influent of a tank should be equal to the tracer concentration at the effluent of the tank or cascade of tanks that are being evaluated to validate the data before the test is ended.  In general, it is best to run a tracer test for three to four theoretical detention times.  In basins that do not exhibit significant short-circuiting, steady-state tracer concentration for a step input test may be reached in as little as two theoretical detention times.

In the City of Cloverdale study, the effluent concentration reach steady-state at approximately 2.1 theoretical detention times (100 minutes).  After 100 minutes, the effluent fluoride concentration was showed to be increasing at a very small rate.  The most probable reason is due in part that a small percent of water from the distribution system is continuously recycled back into the treatment process for use.  During the tracer study, the recycled water had the effect of increasing the background fluoride concentration over time.  Water from the distribution is used for solution water for post-chlorination.  Because the recycle streams contained a significant fluoride concentration during the test, background fluoride concentration would increase incremental over time, which would result in the effluent concentration having small incremental increases.  Thus, effluent concentration from the contact tank would take a very long time to reach steady-state.

Factors associated with the design of the City of Cloverdale clearwells could also explain the T10 result.  According to Bishop et al (1993), low length-to-width and length-to-depth ratios are associated with increased axial dispersion within process units.  The City of Cloverdale clearwells length-to-width and length-to-depth ratios (74:1 and 10.7:1, respectively) fall in the predictive range for the T10 value based on Bishop’s study (see Plot in Appendix B).

The calculated percent of plug flow, mixed flow, and dead space for the clearwell was also determined.  Approximately 70 percent of the clearwell modeled to be plug flow and 30 percent to be mixed.  Dead volume was calculated to be zero.  These values have an error up to 8 percent.

Table 2 lists the results of CT values calculated by different methods and the corresponding log inactivations assigned by the USEPA Guidance Manual.  All three methods meet the required log inactivation.  Compliance may be demonstrated by using any of the three methods presented.

Table 2. CT Results

| Method | CT [(mg/L)-min] | Log Inactivation of Giardia * |
| --- | --- | --- |
| T = T10 = 33 min. assigned by USEPA Guidance Manual | 26.9 | 1.2 |
| T = T10 = 37 min. determined by tracer study | 30.0 | 1.3 |
| Effective CT determined by tracer study | 44.3 | 2.0 |

* Notes:	1. Required log reduction and inactivation of Giardia cyst is 3 log.  City of Cloverdale uses conventional filtration and receives 2.5 log removal credit.  Therefore, disinfection must meet 0.5 log inactivation.

2. CT table used to interpolate log inactivation of Giardia cyst using free chlorine was for pH = 7.5, chlorine concentration = 0.81 mg/L, and temp = 20oC.

3.	The log inactivation credit for the effective CT can not be directly looked up on the CT tables since each elemental CT has a different chlorine residual.  However, the effluent chlorine residual can be used to approximate log inactivation of Giardia cyst.  The log inactivation value for the effective CT presented in the table was based on the weighted average of each fluid element.

CONCLUSION

The City’s clearwell tracer study generated a T10 value of 37 minutes and a T10/T value of 0.78.  These values will be used in the future by the City of Cloverdale to determine compliance with the disinfection requirements of the Surface Water Treatment Rule.

REFERENCES

AWWA. Tracer Studies in Water Treatment Facilities: A Protocol and Case Studies. AWWA Research Foundation and American Water Works Association (1996).

BISHOP, M.M.; MORGAN, J.M.; CORNWELL, B. & JAMISON, D.K. Improving the Disinfection Detention Time of a Water Plant Clearwell. Jour AWWA, 85:3:68 (Mar. 1993).

HUDSON, H. E. JR.  Residence Times in Pretreatment.  Jour AWWA, January 1975.

LEVENSPIEL, O. Chemical Reaction Engineering. John Wiley and Sons, New York (2nd ed., 1962).

TEEFY, S.M. & SINGER, P.C. Performance and Analysis of Tracer Tests to Determine Compliance of a Disinfection Scheme With the SWTR. Jour AWWA, 82:12:88 (Dec. 1990).

USEPA. Guidance Manual for Compliance with the Filtration and Disinfection Requirements for Public Water Systems Using Surface Water Sources. Washington, D.C. (1989).

T10 is defined as the detention time at which 90 percent of the water passing through a tank or process unit is retained within the tank or process unit.  T is defined as the theoretical detention time of a tank or process unit. T10/T is sometimes called the “short-circuiting factor”.

? City of Cloverdale clearwells meets the USEPA definition of intrabasin baffling but does not meet the condition for inlet baffling.

The Hach DR/2000 Spectrophotometer was used.