CALIFORNIA REGIONAL WATER QUALITY CONTROL BOARD

SAN FRANCISCO BAY REGION

1515 CLAY STREET, SUITE 1400

OAKLAND, CA  94612

(510) 622 - 2300     Fax: (510) 622 - 2460

FACT SHEET

for

NPDES PERMIT AND WASTE DISCHARGE REQUIREMENTS FOR

City of Petaluma

sonoma county

NPDES PERMIT NO. CA0037810

ORDER NO. R2-2005-0058

# PUBLIC NOTICE:

# Written Comments

- Interested persons are invited to submit written comments concerning this draft permit.

- Comments must be submitted to the Regional Water Board no later than 5:00 p.m. on September 27, 2005.

- Send comments to the Attention of Tong Yin.

# Public Hearing

- The draft permit will be considered for adoption by the Regional Water Board at a public hearing during the Regional Water Board’s regular monthly meeting at: Elihu Harris State Office Building, 1515 Clay Street, Oakland, CA; 1st floor Auditorium.

- This meeting will be held on:		October 19, 2005, starting at 9:00 am.

# Additional Information

- For additional information about this matter, interested persons should contact Regional Water Board staff member:   		Ms. Tong Yin, Phone: (510) 622-2418 								email: tyin@waterboards.ca.gov

This Fact Sheet contains information regarding a reissuance of waste discharge requirements and National Pollutant Discharge Elimination System (NPDES) permit for the City of Petaluma, Sonoma County, for discharging secondary-level treated municipal wastewater into the Petaluma River. The Fact Sheet describes the factual, legal, and methodological basis for the sections addressed in the proposed permit and provides supporting documentation to explain the rationale and assumptions used in deriving the effluent limitations.

I.	INTRODUCTION

The Discharger applied for reissuance of waste discharge requirements and a permit to discharge wastewater to waters of the State and the United States under the NPDES program.  The application and Report of Waste Discharge are dated March 22, 2002.

1.  Facility Description

The Discharger owns the municipal wastewater treatment plant (the WWTP or the plant) located at 950 Hopper Street in Petaluma and oxidation pond system located at 4400 Lakeville Highway, Sonoma County, and presently contracts with Veolia Water Operation Services Inc. to operate the facility. The WWTP provides secondary level treatment for combined domestic, commercial and industrial wastewater collected in the City, the nearby community of Penngrove, and unincorporated areas in the vicinity of Petaluma. The Discharger's service area currently has a population of approximately 56,632 for the City (Year 2005 data) and 1510 for Penngrove for a total of approximately 58,142 residents.

The U.S. Environmental Protection Agency (U.S. EPA) and the Regional Water Board have classified this Discharger as a major discharger.

2.  Treatment Process Description

The treatment facility is divided between the main plant located at 950 Hopper Street and the oxidation ponds located approximately 2.5 miles southeast of the plant, along Lakeville Highway.  The treatment process consists of rag and grit removal, pre-aeration, primary sedimentation, biological treatment (either biofiltration or activated sludge), secondary clarification, oxidation lagoon treatment, followed by chlorination/dechlorination.  The lagoon /oxidation pond treatment system consists of aeration and oxidation in a 162-acre pond system.  Sludge is treated by anaerobic and aerobic digestion, dewatered by either centrifuge or belt filter press, and disposed of in a landfill.

3.  Discharge Description

The WWTP has an average dry weather flow design capacity of 5.2 million gallons per day (mgd). The plant presently treats an average dry weather flow of 4.8 mgd (2000-2003) and an annual average flow of about 5.7 mgd (during January 2000 through March 2004). During the wet seasons of 2000 to 2004, the plant discharged an average effluent flow of 7.2 mgd to the Petaluma River; during the dry seasons of the same period, the plant reused an average flow of 4.2 mgd.

During the period from October 21 through April 30, treated wastewater is discharged into the Petaluma River. From May 1 through October 20, treated wastewater is reused for agricultural irrigation. In addition to agricultural irrigation, treated wastewater is applied to a golf course located at Frates Road and Ely Road on a year round basis. Discharges of treated wastewater to land are regulated by Water Reuse Requirements in Order No. 88-036, adopted by the Regional Water Board on March 16, 1988.  The Discharger has filed Notice of Intent for coverage under the General Water Reuse Permit, Order No. 96-011. If coverage under the General Permit is attained, Order No. 88-036 is no longer effective.

4.  Receiving Water Beneficial Uses

The beneficial uses of San Francisco Bay in the vicinity of the outfall, as identified in the Regional Water Board’s June 21, 1995 Water Quality Control Plan San Francisco Bay Basin (Region 2) (the Basin Plan) and based on known uses of the receiving water (Petaluma River) in the vicinity of the discharge, are:

- Cold Fresh Water habitat

- Marine Habitat*

- Fish Migration

- Navigation

- Preservation of Rare and Endangered Species

- Water Contact Recreation

- Noncontact Water Recreation

- Fish Spawning

- Warm Freshwater Habitat

- Wildlife Habitat

* The Discharger has stated its intent to petition the Regional Water Board to change the “Marine Habitat” beneficial use to “Estuarine” in the next Basin Plan review process.

5.  Receiving Water Salinity

The receiving waters for the subject discharge are the waters of the Petaluma River, which is a tributary of San Pablo Bay. The Petaluma River is tidally-influenced and has salinities in between the two categories as described in the Basin Plan and CTR.  Therefore, this Order’s effluent limitations are based on the lower of the marine and fresh water WQOs/WQC. This basis is also consistent with the previous permit.

6.  Receiving Water Hardness

Ambient hardness values are used to calculate freshwater WQOs/WQC that are hardness dependent. In determining the WQOs/WQC for this Order, Regional Water Board staff used a hardness value of 190 mg/L as CaCO3, which is the adjusted geometric mean (AGM) of 84 hardness values obtained from the Discharger’s monitoring of the Petaluma River, during the period of January 1994 through December 2003, while there were discharges to the Petaluma River.  The AGM represents the value that 30% of the data points fall below.  The hardness data set was reduced (from 240 data points to 84 data points) to eliminate hardness values above 400 mg/L and to eliminate hardness values obtained when the receiving water salinity was above 1.0 ppt.  Since salinity was not monitored for all sampling events, a linear regression analysis was performed on the available salinity and total dissolved solids (TDS) data.  The equation was used to predict the missing salinity values associated with hardness monitoring data collected on specific dates. The data and calculation can be found in Attachment 1 of this Fact Sheet. The following lists the procedure to calculate an AGM:

1. Calculate the logarithms of each hardness value.

2. Calculate the arithmetic mean of the logarithms.

3. Calculate the standard deviation (s) of the logarithms.

4. Calculate the standard error (SE) of the arithmetic mean:

SE = s/n

5. Calculate A = arithmetic mean - t0.7SE

where t0.7 is the value of Student's t statistics for a one-sided probability of 0.7 with n-1 degrees of freedom, n-sample size. With a sample size of 84, t0.7= 0.526.

6. Take the antilogarithm of A, antilog A is the AGM.

II.  DESCRIPTION OF EFFLUENT

Table A below presents the quality of the discharge, as indicated in the Discharger’s self-monitoring reports over the period of January 2000 through March 2004.

- Table A.  Summary of Effluent Data

| - Parameter | - Average | - Range of - Reported Values | - Number of Samples |
| --- | --- | --- | --- |
| - pH, standard units | - 7.86 | - 6.64 -9.21 | - 1420 |
| - Total Coliform Bacteria, - MPN/100 mL | - <2[1] | - <2 - 1600 | - 1236 |
| - BOD5, mg/L | - 18.8 | - 6.9 – 43.5 | - 682 |
| - Percent Removal, BOD5 | - 93.8 | - 86.3 – 97.0 | - 51 |
| - Chlorine, mg/L | - -- | - (Discharger please provided data) | - (Discharger please provided data) |
| - TSS, mg/L | - 40.7 | - 8.0 – 84.7 | - 711 |
| - Percent Removal, TSS | - 86.2 | - 77.4 – 93.0 | - 51 |
| - Settleable Solids, ml/L | - <0.1[1] | - <0.1 – 0.6 | - 1417 |
| - Dissolved Oxygen, mg/L | - 4.5 | - 0.7 – 11.4 | - 1389 |
| - Oil and Grease, mg/L | - <5[1] | - <2 – 8 | - 71 |
| - Temperature (C) | - 17.1 | - 7.5 – 27.0 | - 1417 |
| - Ammonia as Nitrogen, mg/L | - 8.2 | - 1.6 -19.0 | - 76 |
| - Acute Toxicity, Percent Survival | - -- | - 0[2]- 100 | - 33 |
| - Chronic Toxicity, TUc | - -- | - 1.00 – 2.0 | - 20 |
| - Antimony, g/L | - 0.33 | - 0.3 – 0.5 | - 8 |
| - Arsenic, g/L | - 1.85 [3] | - 0.9 – 3.6 | - 33 |
| - Beryllium, g/L | - All ND | - <0.1 - <1.0 | - 26 |
| - Cadmium, g/L | - 0.08 [3] | - 0.03 - <0.2 | - 33 |
| - Chromium VI, g/L | - 0.89 [3] | - 0.4 – 3.0 | - 33 |
| - Copper, g/L | - 3.3 [3] | - 1.7 – 6.0 | - 33 |
| - Lead, g/L | - 0.63 [3] | - 0.247 – <2.0 | - 33 |
| - Mercury, g/L | - 0.0071 | - 0.0005 – 0.021 | - 30 |
| - Nickel, g/L | - 4.05 [3] | - 2.7 – 6.8 | - 33 |
| - Selenium, g/L | - 0.7 [3] | - 0.6 – 2.0 | - 33 |
| - Silver, g/L | - 0.17 [3] | - 0.05 -0.5 | - 33 |
| - Thallium, g/L | - 0.08 [3] | - 0.06 – 0.2 | - 6 |
| - Zinc, g/L | - 20 [3] | - 10 - 40 | - 33 |
| - Cyanide, g/L | - 3.0 [3] | - 1.4 - 10 | - 33 |

- [1] Median value.

- [2] The Discharger observed acute toxicity in early 2004, after the Discharger switched to the 5th edition with younger fish.

[3] Averages were calculated with the non-detected values being replaced with half detection limit.

III.	GENERAL RATIONALE AND REGULATORY BASES

- the Federal Water Pollution Control Act, Sections 301 through 305, and 307, and amendments thereto, as applicable (the Clean Water Act – the CWA);

- the Regional Water Board’s June 21, 1995 Water Quality Control Plan San Francisco Bay Basin (Region 2) (the Basin Plan), and amendments thereto, as subsequently approved by the State Water Resources Control Board (the State Water Board), the Office of Administrative Law (OAL) and the U.S. EPA;

- the State Water Resource Control Board’s (the State Water Board’s) March 2, 2000 Policy for Implementation of Toxics Standards for Inland Surface Waters, Enclosed Bays, and Estuaries of California (the State Implementation Plan - the SIP), as subsequently approved by the OAL and the U.S. EPA;

- the U.S. EPA’s May 18, 2000 Water Quality Standards; Establishment of Numeric Criteria for Priority Toxic Pollutants for the State of California (the California Toxics Rule – the CTR);

- the U.S. EPA’s National Toxics Rule as promulgated [Federal Register Volume 57, 22 December 1992, page 60848] and subsequently amended (the NTR);

- the U.S. EPA’s Quality Criteria for Water [EPA 440/5-86-001, 1986], and subsequent amendments, (the U.S. EPA Gold Book);

- applicable Federal Regulations [40 CFR Parts 122 and 131];

- 40 CFR Part 131.36(b) and amended [Federal Register Volume 60, Number 86, 4 May 1995, pages 22229-22237];

- the U.S. EPA’s December 10, 1998 National Recommended Water Quality Criteria compilation [Federal Register Vol. 63, No. 237, pp. 68354-68364];

- the U.S. EPA’s December 27, 2002 Revision of National Recommended Water Quality Criteria compilation [Federal Register Vol. 67, No. 249, pp. 79091-79095]; and

- guidance provided with State Water Board actions remanding permits to the Regional Water Board for further consideration.

IV.	SPECIFIC RATIONALE

Several specific factors affecting the development of limitations and requirements in the proposed Order are discussed as follows:

- Recent Facility Performance

Section 402(o) of the Clean Water Act (CWA) and 40 CFR § 122.44(l) require that water quality-based effluent limitations (WQBELs) in re-issued permits be at least as stringent as in the previous permit. The SIP specifies that interim effluent limitations, if required, must be based on current facility performance or on previous permit limitations whichever is more stringent (unless anti-backsliding requirements are met).  In determining what constitutes “recent plant performance,” best professional judgment (BPJ) was used.  Effluent data collected from January 2000 through March 2004 for conventional and toxic pollutants are considered representative of recent plant performance.

- Impaired Water Bodies on 303(d) List

On June 6, 2003, the U.S. EPA approved a revised list of impaired water bodies prepared by the State (hereinafter referred to as the 2002 303(d) list), prepared pursuant to provisions of Section 303(d) of the federal CWA requiring identification of specific water bodies where it is expected that water quality standards will not be met after implementation of technology-based effluent limitations on point sources.  The pollutants impairing San Pablo Bay include diazinon, dieldrin, dioxin compounds, furan compounds, mercury, nickel, PCBs, dioxin-like PCBs, and selenium. The San Pablo Bay is also listed as impaired by exotic species. Copper, which was previously identified as impairing San Pablo Bay, was not included as impairing pollutant in the 2002 303(d) list and has been placed on the new Monitoring List. The Petaluma River (tidal portion) has been listed as impaired by diazinon, nickel, pathogens, and nutrients.

The SIP requires final effluent limitations for all 303(d)-listed pollutants to be based on total maximum daily loads (TMDLs) and associated waste load allocations (WLAs).  The SIP and U.S. EPA regulations also require that final concentration-based WQBELs be included for all pollutants having reasonable potential to cause or contribute to an exceedence of applicable water quality standards (having reasonable potential or RP).  The SIP requires that where the discharger has demonstrated infeasibility to meet the final WQBELs, interim performance-based limitations (IPBLs) or previous permit limitations (whichever is more stringent) be established in the permit, together with a compliance schedule that shall remain in effect until final effluent limitations are adopted.  The SIP also requires the inclusion of appropriate provisions for waste minimization and source control where interim limitations are established.

3.  Basis for Prohibitions

a.	Discharge Prohibition A.1. (no discharge receiving less than 10:1 dilution or to dead-end sloughs):  This prohibition is based on the Basin Plan and is the previous permit. The Basin Plan prohibits discharges not receiving a minimum10:1 initial dilution or to dead-end sloughs (Chapter 4, Discharge Prohibition No. 1). The Regional Water Board has granted an exception to the discharge prohibition for discharges to Petaluma River as described in the findings of the Order.

b.	Discharge Prohibition A.2 & A.4 & A.6 (no bypass or overflow of untreated wastewaters, no discharge of anything other than storm water to storm drains, unless as authorized by this permit):  This prohibition is based on the Basin Plan. The Basin Plan prohibits the discharge of partially treated and untreated wastes (Chapter 4, Discharge Prohibition No.15).  This prohibition is based on general concepts contained in Sections 13260 through 13264 of the California Water Code that relate to the discharge of waste to State waters without filing for and being issued a permit. Under certain circumstances, as stated in 40 CFR 122.41 (m), the facilities may bypass waste streams to waters of the State in order to prevent loss of life, personal injury, or severe property damage, or if there were no feasible alternatives to the bypass and the Discharger submitted notices of the anticipated bypass to waters of the State.

c.	Discharge Prohibition A.3.  (average dry weather flow not to exceed 5.2 mgd, may increase up to 6.7 mgd after the new WWTP is operatoinal):  This prohibition is based on the historic reliable treatment capacity of the plant.  Exceedance of the treatment plant's average dry weather flow design capacity may result in lowering the reliability of achieving compliance with water quality requirements, unless the Discharger demonstrates otherwise through an antidegradation study.  This prohibition is based on 40 CFR 122.41(l). The Discharger is upgrading the aeration ponds, and is building a new WWTP. During the permit term, upon the Executive Officer’s approval of an antidegradation analysis, the WWTP may get two flow capacity increases, from 5.2 mgd to 5.7 mgd upon the completion of the aeration capacity project, and from 5.7 mgd to 6.7 mgd upon the completion and operation of the new WWTP, respectively.

e.	Discharge Prohibition A.5.  (no discharge to Petaluma River from May 1 through October 20):  Discharge to the Petaluma River during the dry weather season is prohibited by the Basin Plan, Chapter 4, Discharge Prohibition No. 1. However, an exception may be authorized by the Executive Officer under certain emergency situations such as prolonged wet season that prohibits normal reclamation.

4.  Basis for Effluent Limitations

## a.   Effluent Limitations B(1) (Conventional Pollutants)

| Permit Limitation | Constituent | Units | Monthly Average | Weekly Average | Daily Maximum | Instantaneous Maximum |
| --- | --- | --- | --- | --- | --- | --- |
| B(1)(a) | Biochemical Oxygen Demand (BOD5, 20°C) | mg/L | 30 | 45 | -- | -- |
| B(1)(b)(i) | Total Suspended Solids[1] | mg/L | 45 | 65 | -- | -- |
| B(1)(c) | Oil & Grease | mg/L | 10 | -- | 20 | -- |
| B(1)(d) | Chlorine Residual [2] | mg/L | -- | -- | -- | 0.0 |

- [1]After the new WWTP is operational, TSS effluent limitations for the discharges are specified as follows.

| Permit Limitation | Constituent | Units | Monthly Average | Weekly Average | Daily Maximum | Instantaneous Maximum |
| --- | --- | --- | --- | --- | --- | --- |
| B(1)(b)(ii) | Total Suspended Solids | mg/L | 30 | 45 | -- | -- |

- [2] Requirement defined as below the limit of detection in the latest officially approved edition of “Standard Methods for Examination of Water and Wastewater.”

- The effluent limitations B(1)(a), B(1)(b)(ii), and B(1)(c) are technology-based limitations.  These limitations are based on the Basin Plan (Chapter 4, page 4-8, and Table 4-2, at page 4-69). B(1)(b)(i) are retained from the previous permit as the Discharger has had difficulty complying with B(1)(b)(ii). The alternate limitations (45 and 65 mg/l for monthly and weekly averages, respectively) were originally granted in 1985.  The Federal Regulations specify that alternative limitations may only be applied if (1) the BOD and TSS effluent concentrations, consistently achievable through proper operation and maintenance of the treatment works, exceed the minimum level of the effluent quality set forth in 133.102(a) and 133.102(b); and, (2) waste stabilization ponds or trickling filters are the principal process used for secondary treatment. The Discharger’s secondary treatment processes include the trickling filters, activated sludge unit, and oxidation ponds.  The trickling filters and oxidation ponds, together, treat over 50% of the wastewater.  However, the BOD effluent quality is not compromised by the Discharger’s ponds or the trickling filters.  This Order maintains the alternate limitations provided that the Discharger maintains and manages the treatment facilities properly. After the new WWTP becomes operational, the Discharger shall comply with B(1)(b)(ii).

Effluent limitation B(1)(d): This effluent limitation was in the previous permit, and is from Chapter 4 of the Basin Plan. The Discharger may elect to use a continuous on-line monitoring system(s) for measuring flow, chlorine, and sodium bisulfite dosage (including a safety factor) and concentration to prove that chlorine residual exceedances are false positives.  If convincing evidence is provided, Regional Water Board staff may conclude that these false positives of chlorine residual exceedances are not violations of the permit limit.

## b.  Effluent Limitation B(2) (pH, minimum 6.5, maximum 8.5):

These effluent limitations are technology-based limit and are unchanged from the previous permit.  These limitations are based on the Basin Plan (Chapter 4, Table 4-2), which are derived from federal requirements (40 CFR 133.102).  These are previous permit effluent limitations and compliance has been demonstrated by existing plant performance. The Discharger may elect to use continuous on-line monitoring system(s) for measuring pH.  In this case, 40 CFR 401.17 (pH Effluent Limitations under Continuous Monitoring), and BPJ are the basis for the compliance provisions for pH limitations.  Excursions of the pH effluent limitations are permitted, provided that both of the following conditions are satisfied: (i) The total time during which the pH values are outside the required range of pH values shall not exceed 7 hours and 26 minutes in any calendar month; and (ii) No individual excursion from the range of pH values shall exceed 60 minutes. For dry season discharges, since it is unlikely that the discharge lasts longer than a month, the condition for complying with pH limit under continuous monitoring is limited to (ii) above.

## c.  Effluent Limitation B.3 (BOD and TSS monthly average 85 percent removal):

These are technology-based limitations and existing permit effluent limitations based on Basin Plan requirements, derived from federal requirements (40 CFR 133.102; definition in 133.101).  During the past 5 years, the Discharger has consistently met these removal efficiency limits.

## d. Effluent Limitation B.4 (Total Coliform):

The total coliform limitations require that the moving median value for the MPN of total coliform bacteria in any five consecutive samples shall not exceed 23 MPN/100ml and any single sample shall not exceed 240 MPN/100mL, the daily maximum limitation is from Basin Plan, Table 4-2; the median limitation is allowed by Footnote (e), Table 4-2 of the Basin Plan. The Regional Water Board has granted an exception to the 2.2 median limitation in Table 4-2 of the Basin Plan, since the Discharger submitted a preliminary analysis of the total coliform in the effluent and Petaluma River both upstream and downstream of the discharge (see Attachment 7 of the Fact Sheet). The analysis shows that the effluent has total coliform levels that are in compliance with the water quality objectives for water contact recreation (as specified in Table 3-1 of Basin Plan), and are of much better quality than the ambient bacterial level. The purpose of these effluent limitations is to ensure adequate disinfection of the discharge in order to protect beneficial uses of the receiving waters. Therefore, the discharge does not compromise the beneficial uses of the receiving water, and as a result, an exception to the Basin Plan Table 4-2 total coliform effluent limitations has been granted to the discharge.

Effluent limitations based on WQOs for bacteriological parameters for receiving water beneficial uses are given in terms of parameters which serve as surrogates for pathogenic organisms. The traditional parameter in this regard is coliform bacteria, either as total coliform or as fecal coliform.  The Regional Water Board can allow the Discharger to use alternate limitations of bacteriological quality if the Discharger can establish to the satisfaction of the Board that the use of the fecal coliform or enterococci limitations will not result in unacceptable adverse impacts on the beneficial uses of the receiving water.

## e. Effluent Limitation B.5 (Whole Effluent Acute Toxicity):

The Basin Plan specifies a narrative objective for toxicity, requiring that all waters shall be maintained free of toxic substances in concentrations that are lethal to or produce other detrimental response on aquatic organisms.  Detrimental response includes but is not limited to decreased growth rate, decreased reproductive success of resident or indicator species, and/or significant alternations in population, community ecology, or receiving water biota.  These effluent toxicity limitations are necessary to ensure that this objective is protected.  The acute toxicity limit is based on the Basin Plan.

## f. Effluent Limitation B.6 (Whole Effluent Chronic Toxicity):

The chronic toxicity limit is based on the Basin Plan.  Chronic toxicity shall be monitored by using critical life stage test(s) and the most sensitive test species identified by screening phase testing.  The Discharger shall conduct routine monitoring with the species approved by the Executive Officer.  At the time of this permit adoption, the approved species is Americamysis bahia (mysid), which is the most sensitive species identified during the chronic toxicity screening study conducted between December 2002 and February 2003, on Macrocystis pyrifera (giant kelp), Americamysis bahia (mysid), Atherinops affinis (topsmelt), and Pimephales promelas (fathead minnow).

## g.	Effluent Limitation B(i)(4) and B(ii)(4) (Toxic Substances):

- Reasonable Potential Analysis (RPA)

- Code of Federal Regulations Title 40, Part 122.44(d)(1)(i) (40 CFR 122.44(d)(1)(i)) specifies that permits must include WQBELs for all pollutants “which the Director determines are or may be discharged at a level which will cause, have the reasonable potential to cause, or contribute to an excursion above any State water quality standard” (have Reasonable Potential or RP).  Thus, assessing whether a pollutant has RP is the fundamental step in determining whether or not a WQBEL is required.  The following sections describe the RPA and the results of such an analysis for the pollutants identified in the Basin Plan and the CTR.

- i)	WQOs/WQC:  The RPA uses Basin Plan WQOs, including narrative toxicity objectives in the Basin Plan, and applicable WQC in the CTR/NTR, or site-specific objectives (SSOs) if available, after adjusting for site-specific hardness and translators, if applicable.  The governing WQOs/WQC are shown in Attachment 3 of this Fact Sheet.

- ii)	Methodology:  The RPA uses the methods and procedures prescribed in Section 1.3 of the SIP.  Regional Water Board staff has analyzed the effluent and background data and the nature of facility operations to determine if the discharge shows reasonable potential with respect to the governing WQOs/WQC.  Attachment 3 of this Fact Sheet shows the step-wise process described in Section 1.3 of the SIP.

  - Effluent and background data:  The RPA is based on effluent data collected by the Discharger from January 2000 through March 2004 for most priority pollutants.  Ambient data collected in 2002 and 2003 on the Petaluma River near the Discharger’s outfall were used in evaluating background water quality for this Order.

  - RPA determination: The RPA results are shown below in Table B and Attachment  3 of this Fact Sheet.  The pollutants that exhibit reasonable potential are copper, mercury, nickel, selenium, cyanide, TCDD TEQ, and bis(2-ethyhexyl)phthalate.

#### Table B.  Summary of Reasonable Potential Results

| - # in CTR | - Priority Pollutants | - Governing WQO/WQC (μg/L) | - MEC or Minimum MDL1 - (g/L) | - Maximum Background or Minimum MDL1 - (g/L) | - RPA Results2 |
| --- | --- | --- | --- | --- | --- |
| 1 | Antimony | 4,300 | 0.5 | 1.1 | No |
| 2 | Arsenic | 36 | 3.6 | 29 | No |
| 3 | Beryllium | No Criteria | 0.1 | 0.06 | Uo |
| 4 | Cadmium | 1.9 | 0.2 | 0.03 | No |
| 5a | Chromium (III) | 350 | NA |  | Ud |
| 5b | Chromium (VI) | 11.43 | 3 | 2.8 | No |
| 6 | Copper | 3.7 | 6 | 14.7 | Yes |
| 7 | Lead | 7.2 | 0.6 | 0.83 | No |
| 8 | Mercury | 0.025 | 0.021 | 0.018 | Yes |
| 9 | Nickel | 8.3 | 6.8 | 24.5 | Yes |
| 10 | Selenium | 5.00 | 2 | 12 | Yes |
| 11 | Silver | 2.2 | 0.5 | 0.02 | No |
| 12 | Thallium | 6.3 | 0.2 | 0.2 | No |
| 13 | Zinc | 85.6 | 40 | 20 | No |
| 14 | Cyanide | 1.0 | 10 | 3 | Yes |
| 15 | Asbestos | No Criteria | NA |  | Uo |
| 16 | 2,3,7,8 TCDD | 0.000000014 | 6.3710-7 | 6.3710-7 | No |
|  | TCDD TEQ | 0.000000014 | 8.7310-6 | 5.2710-8 | Yes |
| 17 | Acrolein | 780 | 5 | 1 | No |
| 18 | Acrylonitrile | 0.66 | 2 | 1 | No |
| 19 | Benzene | 71 | 1.4 | 0.3 | No |
| 20 | Bromoform | 360 | 0.5 | 0.2 | No |
| 21 | Carbon Tetrachloride | 4.4 | 0.5 | 0.42 | No |
| 22 | Chlorobenzene | 21,000 | 0.5 | 0.3 | No |
| 23 | Chlorodibromomethane | 34 | 2.4 | 0.3 | No |
| 24 | Chloroethane | No Criteria | 0.5 | 0.34 | Uo |
| 25 | 2-Chloroethylvinyl ether | No Criteria | 6 | 0.32 | Uo |
| 26 | Chloroform | No Criteria | 8 | 0.3 | Uo |
| 27 | Dichlorobromomethane | 46 | 3.8 | 0.2 | No |
| 28 | 1,1-Dichloroethane | No Criteria | 0.5 | 0.34 | Uo |
| 29 | 1,2-Dichloroethane | 99 | 0.5 | 0.2 | No |
| 30 | 1,1-Dichloroethylene | 3.2 | 0.5 | 0.49 | No |
| 31 | 1,2-Dichloropropane | 39 | 0.5 | 0.2 | No |
| 32 | 1,3-Dichloropropylene | 1,700 | NA | 0.2 | No |
| 33 | Ethylbenzene | 29,000 | 0.5 | 0.4 | No |
| 34 | Methyl Bromide | 4,000 | 85 |  | No |
| 35 | Methyl Chloride | No Criteria | NA |  | Uo |
| 36 | Methylene Chloride | 1,600 | 0.9 | 0.4 | No |
| 37 | 1,1,2,2-Tetrachloroethane | 11 | 0.5 | 0.3 | No |
| 38 | Tetrachloroethylene | 8.85 | 2.4 | 0.44 | No |
| 39 | Toluene | 200,000 | 4.6 | 0.32 | No |
| 40 | 1,2-Trans-Dichloroethylene | 140,000 | NA | 0.43 | No |
| 41 | 1,1,1-Trichloroethane | No Criteria | 0.5 | 0.49 | Uo |
| 42 | 1,1,2-Trichloroethane | 42 | 0.5 | 0.3 | No |
| 43 | Trichloroethylene | 81 | 0.5 | 0.3 | No |
| 44 | Vinyl Chloride | 525 | 0.5 | 0.47 | No |
| 45 | 2-Chlorophenol | 400 | 5 | 0.6 | No |
| 46 | 2,4-Dichlorophenol | 790 | 5 | 0.7 | No |
| 47 | 2,4-Dimethylphenol | 2,300 | 2 | 0.9 | No |
| 48 | 2-Methyl- 4,6-Dinitrophenol | 765 | 5 | 0.9 | No |
| 49 | 2,4-Dinitrophenol | 14,000 | 5 | 0.6 | No |
| 50 | 2-Nitrophenol | No Criteria | 5 | 0.7 | Uo |
| 51 | 4-Nitrophenol | No Criteria | 5 | 0.6 | Uo |
| 52 | 3-Methyl 4-Chlorophenol | No Criteria |  | 0.5 | Uo |
| 53 | Pentachlorophenol | 7.90 | 1 | 0.9 | No |
| 54 | Phenol | 4,600,000 | 1 | 0.4 | No |
| 55 | 2,4,6-Trichlorophenol | 6.50 | 5 | 0.6 | No |
| 56 | Acenaphthene | 2,700 | 0.3 | 0.17 | No |
| 57 | Acenaphthylene | No Criteria | 0.2 | 0.03 | Uo |
| 58 | Anthracene | 110,000 | 0.3 | 0.16 | No |
| 59 | Benzidine | 0.00054 | 5 | 1 | No |
| 60 | Benzo(a)Anthracene | 0.049 | 0.3 | 0.12 | No |
| 61 | Benzo(a)Pyrene | 0.049 | 0.3 | 0.09 | No |
| 62 | Benzo(b)Fluoranthene | 0.049 | 0.3 | 0.11 | No |
| 63 | Benzo(ghi)Perylene | No Criteria | 0.1 | 0.06 | Uo |
| 64 | Benzo(k)Fluoranthene | 0.049 | 0.3 | 0.16 | No |
| 65 | Bis(2-Chloroethoxy)Methane | No Criteria | 5 | 0.9 | Uo |
| 66 | Bis(2-Chloroethyl)Ether | 1.40 | 1 | 0.7 | No |
| 67 | Bis(2-Chloroisopropyl)Ether | 170,000 | 2 | 0.6 | No |
| 68 | Bis(2-Ethylhexyl)Phthalate | 5.90 | 12 | 0.8 | Yes |
| 69 | 4-Bromophenyl Phenyl Ether | No Criteria | 5 | 0.4 | Uo |
| 70 | Butylbenzyl Phthalate | 5,200 |  | 0.8 | No |
| 71 | 2-Chloronaphthalene | 4,300 | 5 | 0.5 | No |
| 72 | 4-Chlorophenyl Phenyl Ether | No Criteria | 5 | 0.5 | Uo |
| 73 | Chrysene | 0.049 | 0.3 | 0.14 | No |
| 74 | Dibenzo(a,h)Anthracene | 0.049 | 0.1 | 0.04 | No |
| 75 | 1,2-Dichlorobenzene | 17,000 | 0.5 | 0.2 | No |
| 76 | 1,3-Dichlorobenzene | 2,600 | 0.5 | 0.3 | No |
| 77 | 1,4-Dichlorobenzene | 2,600 | 0.5 | 0.3 | No |
| 78 | 3,3 Dichlorobenzidine | 0.077 | 5 | 0.3 | No |
| 79 | Diethyl Phthalate | 120,000 | 2 | 0.7 | No |
| 80 | Dimethyl Phthalate | 2,900,000 | 2 | 0.7 | No |
| 81 | Di-n-Butyl Phthalate | 12,000 | 5 | 1 | No |
| 82 | 2,4-Dinitrotoluene | 9.10 | 5 | 0.6 | No |
| 83 | 2,6-Dinitrotoluene | No Criteria | 5 | 0.6 | Uo |
| 84 | Di-n-Octyl Phthalate | No Criteria | 5 | 0.9 | Uo |
| 85 | 1,2-Diphenylhydrazine | 0.54 | 1 | 0.6 | No |
| 86 | Fluoranthene | 370 | 0.05 | 0.03 | No |
| 87 | Fluorene | 14,000 | 0.1 | 0.02 | No |
| 88 | Hexachlorobenzene | 0.00077 | 1 | 0.4 | No |
| 89 | Hexachlorobutadiene | 50 | 1 | 0.7 | No |
| 90 | Hexachlorocyclopentadiene | 17,000 | 5 | 0.4 | No |
| 91 | Hexachloroethane | 8.90 | 1 | 0.6 | No |
| 92 | Indeno(1,2,3-cd)Pyrene | 0.049 | 0.05 | 0.04 | No |
| 93 | Isophorone | 600 | 1 | 0.8 | No |
| 94 | Naphthalene | No Criteria | 0.2 | 0.05 | Uo |
| 95 | Nitrobenzene | 1,900 | 1 | 0.7 | No |
| 96 | N-Nitrosodimethylamine | 8.10 | 5 | 0.6 | No |
| 97 | N-Nitrosodi-n-Propylamine | 1.40 | 5 | 0.8 | No |
| 98 | N-Nitrosodiphenylamine | 16 | 1 | 0.7 | No |
| 99 | Phenanthrene | No Criteria | 0.05 | 0.03 | Uo |
| 100 | Pyrene | 11,000 | 0.05 | 0.03 | No |
| 101 | 1,2,4-Trichlorobenzene | No Criteria | 5 | 0.6 | Uo |
| 102 | Aldrin | 0.00014 | 0.005 | 0.003 | No |
| 103 | alpha-BHC | 0.013 | 0.01 | 0.003 | No |
| 104 | beta-BHC | 0.046 | 0.02 | 0.004 | No |
| 105 | gamma-BHC | 0.063 | 0.01 | 0.003 | No |
| 106 | delta-BHC | No Criteria | 0.005 | 0.002 | Uo |
| 107 | Chlordane | 0.00059 | 0.02 | 0.005 | No |
| 108 | 4,4'-DDT | 0.00059 | 0.01 | 0.003 | No |
| 109 | 4,4'-DDE (linked to DDT) | 0.00059 | 0.01 | 0.002 | No |
| 110 | 4,4'-DDD | 0.00084 | 0.01 | 0.002 | No |
| 111 | Dieldrin | 0.00014 | 0.01 | 0.002 | No |
| 112 | alpha-Endosulfan | 0.0087 | 0.01 | 0.002 | No |
| 113 | beta-Endolsulfan | 0.0087 | 0.01 | 0.002 | No |
| 114 | Endosulfan Sulfate | 240 | 0.01 | 0.002 | No |
| 115 | Endrin | 0.0023 | 0.01 | 0.002 | No |
| 116 | Endrin Aldehyde | 0.81 | 0.01 | 0.002 | No |
| 117 | Heptachlor | 0.00021 | 0.01 | 0.003 | No |
| 118 | Heptachlor Epoxide | 0.00011 | 0.01 | 0.003 | No |
| 119-125 | PCBs sum (2) | 0.00017 | 0.1 | 0.03 | No |
| 126 | Toxaphene | 0.00020 | 0.5 | 0.4 | No |
|  | Tributylin | 0.0074 | 0.002 | 0.00128 | No |
|  | Total PAHs | 15 | 0.3 | 0.17 | No |

- [1]	Values for MEC or maximum background in bold are the actual detected concentrations, otherwise the values shown are the minimum detection levels.

- NA = Not Available (there is no monitoring data or WQO/WQC for this constituent).

- [2]	RP =Yes, if either MEC or background > WQO/WQC.

- RP = No, if both MEC or background < WQO/WQC or all effluent concentrations non-detect and background <WQO/WQC or no background available.

- RP = Uo (undetermined if no objective promulgated).

- RP =  Ud (undetermined due to lack of effluent data).

- v)	Pollutants with no reasonable potential:  WQBELs are not included in the Order for constituents that do not have reasonable potential to cause or contribute to exceedance of applicable WQOs/WQC.  However, monitoring for those pollutants is still required. If concentrations of these constituents are found to increase significantly, the Discharger will be required to investigate the source(s) of the increase(s).  Remedial measures are required if the increases pose a threat to water quality in the receiving water. If the Discharger has fulfilled the sampling requirements according to its approved sampling plan submitted per the August 6, 2001 Letter, the Discharger shall perform a minimum of one sampling event of all 126 priority pollutants during the life of the permit, and submit the results at least 180 days prior to permit expiration (with the permit renewal application).

- vi) Permit reopener:  The permit includes a reopener provision to allow numeric effluent limitations to be added for any constituent that in the future exhibits reasonable potential to cause or contribute to exceedance of a WQO/WQC.  This determination, based on monitoring results, will be made by the Regional Water Board.

- Applicable WQOs/WQC for WQBEL Calculation

- Toxic substances are regulated by WQBELs derived from the Basin Plan, Tables 3-3 and 3-4, the CTR, the NTR, and/or best professional judgment (BPJ). WQBELs in this Order are revised and updated from the limitations in the previous Order, and their presence in this Order is based on the evaluation of the Discharger’s data as described below under the Reasonable Potential Analysis. Numeric WQBELs are required for all constituents that have a reasonable potential to cause or contribute to an excursion above any State water quality standard. Reasonable potential is determined and final WQBELs are developed using the methodology outlined in the SIP. If the Discharger demonstrates that the final limitations will be infeasible to meet and provides justification for a compliance schedule, then interim limitations are established, with a compliance schedule to achieve the final limits. The WQOs/WQC used for each pollutant with Reasonable Potential is indicated in Table C below as well as in Attachment 3 of the Fact Sheet.

#### Table C. Water Quality Objectives/Criteria for Pollutants with Reasonable Potential

| - Pollutant | - Chronic WQO/WQC (μg/L) | - Acute WQO/WQC (μg/L) | - Human Health - WQC - (μg/L) | - Basis of Lowest WQO /WQC - Used in RP[1] |
| --- | --- | --- | --- | --- |
| - Copper | - 3.7 | - 5.8 | - -- | - CTR, T=0.83 |
| - Mercury | - 0.025 | - 2.1 | - 0.051 | - BP, sw |
| - Nickel | - 8.3 | - 75 | 4,600 | BP, sw |
| - Selenium | - 5.0 | - 20 | NA | NTR, sw/fw |
| - Cyanide | - 1 | - 1 | 220,000 | NTR, sw |
| - TCDD TEQ | - -- | - -- | 1.410-8 | BP, narrative |
| - Bis(2-ethylhexyl) phthalate | - -- | - -- | 5.9 | CTR, hh |

[1] BP = Basin Plan, sw = salt water, fw = fresh water, NTR = National Toxics Rule, hh = human health

- Interim Limitations

- Interim effluent limitations were derived for those constituents (copper and cyanide) for which the Discharger has shown infeasibility of complying with the respective final limitations and has demonstrated that compliance schedules are justified based on the Discharger’s source control and pollution minimization efforts in the past and continued efforts in the present and future.  The interim effluent concentration limitations are based on statistical analysis of the effluent data for both pollutants. The interim limitations are discussed in more detail below.

- Feasibility Evaluation and Final WQBELs

The Discharger submitted an infeasibility to comply report on August 22, 2005 for copper and cyanide.  Regional Water Board performed statistical analysis on copper and cyanide self-monitoring data from January 2000 through March 2004 to compare the mean, 95th percentile, and 99th percentile with the long-term average (LTA), AMEL, and MDEL to confirm if it is feasible for the Discharger to comply with WQBELs.  If any of the LTA, AMEL, and MDEL exceeds the mean, 95th percentile, and 99th percentile, the infeasibility for the Discharger to comply with WQBELs is confirmed statistically. Table D below shows these comparisons in g/L:

- Table D:  Summary of Feasibility Analysis (unit: g/L)

| Constituent | - Mean / LTA | - 95th / AMEL | - 99th / MDEL | - Feasible to Comply |
| --- | --- | --- | --- | --- |
| - Copper | - 3.3>2.6 | - 5.2>3.3 | - 6.4 >5.3 | - No |
| - Cyanide | - 3.1>0.3 | - 7.1>0.5 | - 10.8>1.0 | - No |

- In addition, the Discharger asserted that it is infeasible to achieve immediate compliance with mercury effluent limit contained in the previous Order. Regional Water Board staff compared the MEC with the effluent limitation, and concurred with this assertion. The new WQBELs were calculated using the Basin Plan mercury objectives and SIP procedures.

- For bis(2-ethylhexyl)phthalate (BEHP), there are only two detected values; therefore, it is not feasible to perform a meaningful statistical analysis to determine compliance. The MEC is higher than the AMEL, therefore, it is not feasible for the Discharger to achieve immediate compliance. Due to limited data, this Order does not establish an interim limitation for BEHP. This Order requires the Discharger to continue monitoring BEHP and develop pollution prevention activities to reduce concentrations in the effluent. The permit will be reopened, as appropriate, to include BEHP limitations when additional data become available. Final WQBELs for BEHP may be considered by the Regional Water Board in the next permit reissuance if the effluent continues to show reasonable potential.

- For dioxin compounds, there are only three effluent data during 2002 through 2004. Due to the limited effluent data, there is uncertainty in determining compliance or establishing an interim limitation. In addition, the MLs developed for 2,3,7,8-TCDD and 16 congeners (referred to as dioxins) by the Regional Water Board and BACWA range from 5 pg/L to 50 pg/L, which are higher than the WQBELs. As a result, this permit does not contain an interim limitation for dioxin.  The final limitations for dioxins will be based on the WLA assigned to the Discharger in the TMDL.

- Table E below summarizes the calculated WQBELs, and the feasibility to comply analysis for all pollutants with effluent limitations. The WQBELs calculation is attached as Attachment 4 of this Fact Sheet.

- Table E.  Final WQBELs and Feasibility to Comply (Unit: g/L)

| - Pollutant | MDEL g/L | AMEL g/L | - Feasible - to Comply? | - Interim Limit |
| --- | --- | --- | --- | --- |
| - Copper | - 5.2 | - 3.3 | - No | - 7.9 |
| - Mercury | - 0.040 | - 0.021 | Yes | -- |
| - Nickel | - -- | - 7.1 | Yes | -- |
| - Selenium | - 8.2 | - 4.1 | Yes | -- |
| - Cyanide | - 1.0 | - 0.5 | No | 14 |
| - TCDD TEQ | - 2.810-8 | - 1.410-8 | No | -- |
| - Bis(2-Ethylhexyl)Phthalate | - 11.8 | - 5.9 | No | -- |

- Interim Limitations and Compliance Schedules

- This Order establishes a compliance schedule until May 17, 2010 for copper and April 27, 2010 for cyanide. The final WQBELs for copper and cyanide shall become effective on May 18, 2010 and April 28, 2010, respectively, or until the Regional Water Board adopts the SSOs for copper and cyanide.

During the compliance schedules, interim limitations are included based on current treatment facility performance or on previous permit limitations, whichever is more stringent, unless antibacksliding and antidegradation requirements are satisfied, to maintain existing water quality.  Attachment  5 details the general basis for final compliance dates. The Regional Water Board may take appropriate enforcement actions if interim limitations and requirements are not met.

i). 	Copper – Further Discussion and Rationale for Interim Effluent Limitation:  Interim effluent limitations are required for copper since the Discharger has demonstrated and the Regional Water Board verified that the final effluent limitations calculated according to the SIP will be infeasible to meet.  The SIP requires the interim numeric effluent limitation for the pollutant be based on either current treatment facility performance, or on the previous Order’s limitation, whichever is more stringent.  Regional Water Board staff calculated an interim performance-based limitation (IPBL) of 7.9 g/L (3 standard deviations above the mean), which is more less stringent than the previous permit’s effluent limitation of 4.9 g/L. However, the Discharger has asserted that it is infeasible to achieve immediate compliance with the previous permit effluent limit. The Discharger asserts that its oxidation pond system provides metal removal usually equivalent to a tertiary-level treatment plant. The Discharger’s copper effluent monitoring concentrations have been consistently low in the past (MEC is 6 µg/L); but there were samples exceeding the previous limit of 4.9 µg/L. An interim limit based on recent performance is necessary; therefore, 7.9 µg/L is established as the interim limitation, expressed as a daily maximum. Antibacksliding does not apply to interim effluent limits, so long as there is compliance with antidegradation. The interim limit in this permit is in compliance with antidegradation, because it is based on current plant performance and will limit the discharge to existing treatment level. Even if antidegradation applies to interim limits, the interim limit in this permit is exempt pursuant to CWA 402(o)(2)(c). Therefore, 7.9 g/L is established in this Order as the interim limitation, and will remain in effect until May 17, 2010, or until the Regional Water Board amends the limitation based on SSO or additional data.

ii).	Cyanide – Further Discussion and Rationale for Interim Effluent Limitation:  Interim effluent limitations are required for cyanide since the Discharger has demonstrated and the Regional Water Board verified that the final effluent limitations calculated according to the SIP will be infeasible to meet.  The SIP requires the interim numeric effluent limitation for the pollutant be based on either current treatment facility performance, or on the previous Order’s limitation, whichever is more stringent.  Regional Water Board staff calculated an interim performance-based limitation (IPBL) of 16.5 g/L (3 standard deviations above the mean), which is less stringent than the previous permit interim limit of 14 µg/L. Therefore, 14 µg/L is retained in this Order as the interim limitation, and shall remain in effect until April 27, 2010, or until the Regional Water Board amends the limitation based on addition information or an SSO.

- Attainability of Interim Performance-Based Limitations

i). Copper

During the period of January 2000 through March 2004, the Discharger’s effluent concentrations for copper ranged from <2 µg/L to 6 µg/L (33 samples).  All 33 samples are below the interim limitation of 7.9 µg/L.  It is therefore expected that the facility can comply with the interim limitation for copper.

ii). Cyanide

During the period of January 2000 through March 2004, the Discharger’s effluent concentrations ranged from <3 g/L to 10 g/L (33 samples). All 33 samples are below the interim limitation of 14 µg/L.  It is therefore expected that the facility can comply with the interim limitation for cyanide.

- Mercury Interim Mass Emission Limitation/Mass Trigger

This Order includes an interim mercury mass-based effluent limitation of 0.60 kilograms per year (kg/yr) and a mass trigger of 0.0051 kg/month. This mass-based effluent limitation is intended to maintain the Discharger at current loadings while encouraging recycling and providing a buffer for growth. The mass trigger is recalculated using the ultra-clean data collected from January 2000 through March 2004 as it better reflects the plant’s performance. The recalculated mass trigger is a reflection of better mercury effluent data (sampling and analytical techniques have improved) (See Attachment 6 for the mercury trigger calculation). The mass limit will maintain current loadings until a TMDL is established for San Pablo Bay. The final mercury effluent limitations will be based on the Discharger’s WLA in the TMDL. If the mass trigger is exceeded, then the actions specified in Provision F.8 are initiated.

The inclusion of interim performance-based mass limits for bioaccumulative pollutants is consistent with the guidance described in section 2.1.1 of the SIP.  Because of their bioaccumulative nature, an uncontrolled increase in the total mass loads of these pollutants in the receiving water will have significant adverse impacts on the aquatic ecosystem.

Waterkeeper Appeal on Previous Order’s Mercury Mass Limit/Trigger. The San Francisco Baykeeper (now known as the San Francisco Water Keeper) petitioned to the State Water Board the Discharger’s NPDES permit, Order No. 98-076, in August 1998.  In November 1999, the State Water Board dismissed the Baykeeper’s appeal.  In December 1999, Baykeeper filed a lawsuit against the Regional and State Water Boards in Sacramento County Superior Court.  After a change of venue request by the plaintiff and the real parties in interest, the case was transferred to the Sonoma County Superior Court.  In early 2002, the Sonoma Court ruled that the Regional Water Board appropriately set the mass limit/trigger for mercury while complying with antidegradation requirements.  In May 2002, Baykeeper filed an appeal of the Sonoma Court ruling.  This case was heard before the State Appellate Court in April 2003.  In May 2003, the State Appellate Court upheld the Sonoma Court’s ruling.

Antidegradation. In an unpublished decision, the Court of Appeal, in its ruling, concluded that the interim limits for mercury in Order No. 98-076 do not violate the antidegradation policy and that substantial evidence supports the superior court’s decision, as illustrated below. The appeal decision is cited as the San Francisco Baykeeper, the California State Water Resources Control Board et al., Court of Appeal, filed on May 28, 2003, case No. A 098908.

The Sonoma County Superior Court concluded that the antidegradation policy for Tier 1 waters (which the Discharger’s receiving water is categorized) does not necessarily prohibit an increase in the discharge of mercury. The court further concluded that the Regional Water Board’s decision to include trigger level that approximates the actual mass discharged to water as well as mass limitation that rewards reuse was a policy choice the Regional Water Board was authorized to make. The Appellate court upheld the Superior Court’s decision.

The Regional Water Board included a mass limit and trigger level for mercury in the permit to maintain ambient water quality. The combination of limit and trigger would protect the receiving water and would not cause further degradation of the water’s beneficial uses. The Regional Water Board based the mercury mass limit on plant performance, but because the plant has substantial reuse programs, the mass limit is higher than the actual mass of mercury discharged to water. “[T]he way in which the mass load was calculated gives the discharger who reclaims more allowance or relative allocation… than the discharger who does not reclaim. The incentive is meant to increase reclamation [in the South Bay]”. The Regional Water Board reasoned that rigidly holding dischargers to their current levels of performance would result in higher limits for POTWs that make little effort to reuse or otherwise reduce their polluted discharge, while POTWs that aggressively work to reduce their environmental impact would find themselves bound by increasingly more stringent limits. Mass trigger levels in the permit require the Discharger when loading exceeds the trigger to take certain specified actions to determine the cause of the higher load and to bring mercury mass back below the trigger.

- Comparison to Previous Permit Limitations

- The effluent limitations for TSS, oil and grease, pH, and chlorine residual have been retained from the previous Order. Settleable solids effluent limitations are no longer required. The interim effluent limitation for cyanide is unchanged from the previous Order. Copper and mercury have higher effluent limits, and the relaxation is in compliance with antibacksliding and antidegradation requirements. Effluent limitations for cadmium, chromium (VI), lead, lindane, and PAHs were removed from this Order as there is no reasonable potential for these pollutants. The effluent limitations for acute and chronic toxicity are unchanged from the previous Order.

7.   Basis for Pond Management Requirements

These requirements are from the previous permit and are based on BPJ. The triggers are specified for odor control.  If the triggers are exceeded or if there is an odor nuisance, the facility shall identify and address the issue.

8.  Basis for Receiving Water Limitations

a.	Receiving Water Limitations D.1 and D.2.  These limitations are in the existing permit and are based on water quality objectives for physical, chemical, and biological characteristics from Chapter III of the Basin Plan.

b. Receiving Water Limitation D.3.  This limitation is in the existing permit, requires compliance with Federal and State law, and is self-explanatory.

c. Receiving Water Limitation D.4.  This limitation is based on storm water regulations intended to protect beneficial uses of receiving waters from storm water pollutants.

9. Basis for Sludge Management Practices

Sludge Requirements E.1 through E.10.  These requirements come from the Basin Plan (Chapter IV) and 40 CFR 257 and 503.

10.	Basis for Self-Monitoring Requirements

Part A of the monitoring program is a standard requirement in almost all NPDES permits issued by the Regional Water Board.  Most of the requirements also existing requirements for the Discharger.  Part A contains definitions, specifies general sampling and analytical protocols, and specifies reporting of spills, violations, and routine monitoring data in accordance with NPDES regulations, the California Water Code, and Regional Water Board policy.  Part B of the monitoring program is specific for the Discharger.  It defines the stations, constituents, and frequency of monitoring, and additional reporting requirements. Constituents required to be monitored include all parameters for which effluent limitations are specified.  This is to allow determination of compliance with permit limitations in accordance with 40 CFR 122.44(i).

The SMP Part B includes monitoring at the outfall for conventional, non-conventional, and toxic pollutants, and acute and chronic toxicity.  The sampling requirement for conventional and non-conventional pollutants has retained from the previous permit. Monthly acute bioassay is required to determine compliance with effluent limitations: This is the same as in the previous permit. Quarterly chronic toxicity test is required to determine compliance with the effluent limitations. For copper, mercury, nickel, selenium, and cyanide, the Discharger will perform monthly monitoring to demonstrate compliance with effluent limitations. Moreover, the Discharger shall collect annual samples for bis(2-ethylhexyl)phthalate and all the 2,3,7,8-TCDD congeners using the minimum detection limit that can be achieved. In lieu of near field discharge specific ambient monitoring, it is generally acceptable that the Discharger participate in collaborative receiving water monitoring with other dischargers under the provisions of the Regional Water Board’s August 6, 2001 Letter and the RMP. During the permit life, the Discharger shall perform a minimum one sampling event of the 126 priority pollutants, and submit the results with permit renewal application, at least 180 days prior to permit expiration.

12.    Basis for Provisions

- Provision F.1. (Permit Compliance and Rescission of Previous Permit): Time of compliance is based on 40 CFR 122.  The basis of this Order superceding and rescinding the previous permit is based on 40 CFR 122.46.

- Provision F.2 (Effluent Characterization Study):  This provision is based on the Basin Plan and the SIP.

- Provision F.3 (Receiving Water Study):  This provision is based on the Basin Plan and the SIP.

- Provision F.4 (Cyanide Compliance Schedule and Site-Specific Objective (SSO) Study). This provision, based on BPJ, requires the Discharger to characterize background ambient cyanide concentrations and to participate in an on-going group effort to develop an SSO for cyanide.

- Provision F.5 (Regional Copper Study and Schedule): This provision, based on BPJ, requires the Discharger to continue its participation in the regional discharger-funded effort to develop site-specific saltwater aquatic life-based WQOs for copper in San Francisco Bay north of the Dumbarton Bridge.

- Provision F.6 (Pollutant Prevention and Minimization Program):  This provision is based on the Basin Plan, pages 4-25 – 4-28, and the SIP, Section 2.1.

- Provision F.7 (Disinfection Effectiveness Study): This provision is based on BPJ. During the period from January 2000 through April 2004, the Discharger has had over 40 total coliform limitation exceedances.  The Discharger is required by this provision, to conduct a disinfection study, which can be jointly conducted with Provision F.13 (alternate bacterial limitation study), to investigate measures to prevent bacterial limitation violations as well as the chlorine residual violations.

- Provision F.8 (Mercury Mass Loading Reduction): This provision will help to ensure no increases in mercury mass loadings until a TMDL and WLA are established.  The Regional Water Board’s determination of the need to maintain mass loadings at current levels for this bioaccumulative pollutant are based on Section 2.1.1 of the SIP.

- Provision F.9 (Whole Effluent Acute Toxicity):  This provision establishes conditions by which compliance with permit effluent limitations for acute toxicity will be demonstrated.  Conditions include the use of 96-hour flow-through bioassays, the use of fathead minnows and rainbow trout as the test species, and the use of approved test methods.  These conditions are based on the effluent limitations for acute toxicity given in the Basin Plan, Chapter 4, and BPJ.

- Provision F.10. (Whole Effluent Chronic Toxicity):  This provision establishes conditions and protocol by which compliance with the Basin Plan narrative WQO for toxicity will be demonstrated.  Conditions include required monitoring and evaluation of the effluent for chronic toxicity and numerical values for chronic toxicity evaluation to be used as 'triggers' for initiating accelerated monitoring and toxicity reduction evaluation(s).  These conditions apply to the discharges to the Petaluma River and the numerical values for chronic toxicity evaluation. This provision also requires the Discharger to conduct screening phase monitoring when there is significant treatment process or facility change, or for permit reissuance, and implement toxicity identification and reduction evaluations when there is consistent chronic toxicity in the discharge.  The screening phase monitoring is important to help determine which test species is most sensitive to the toxicity of the effluent for future compliance monitoring.  The conditions in the permit for chronic toxicity are based on the Basin Plan narrative WQO for toxicity, Basin Plan effluent limitations for chronic toxicity (Basin Plan, Chapter 4), U.S. EPA and State Water Board Task Force guidance, applicable federal regulations [40 CFR 122.44(d)(1)(v)], and BPJ.

- Provision F.11 (Sanitary Sewer Management Plan): This provision requires the Discharger to actively participate in the BACWA and the Regional Water Board collaborative effort to address Sanitary Sewer Overflows. The effort is consistent with Regional Water Board Resolution No. R2-2003-0095, and Executive Officer’s letters, dated November 15, 2004 and July 7, 2005, respectively.

- Provision F.12 (Optional Mass Offset):  This option is provided to encourage the Discharger to further implement aggressive reduction of mass loads to the Petaluma River/San Pablo Bay.

- Provision F.13 (Optional Receiving Water Beneficial Use and Alternative Bacteriological Limitations Study): This provision allows the Discharger, at its option, to conduct a bacteriological assessment study. The study will evaluate impacts of the Discharger's effluent on the receiving waters (including worst case conditions). The Basin Plan allows alternate bacteria limitations, e.g., fecal coliform, enterococci, or E. Coli, provided that the Discharger conclusively demonstrates "through a program approved by the Regional Water Board that such substitution will not result in unacceptable adverse impacts on the beneficial uses of the receiving waters". If the study demonstrates that the exceedances of the total coliform limitations are solely due to the study, and that there is compliance in the receiving water with the bacteriological objectives specified in the Basin Plan, the Regional Water Board may consider establishing alternate bacteria limitations.

- Provision F.14 (Optional Copper Translator Study and Schedule): The Discharger has difficulty complying with the copper WQBELs. Without site-specific data, the CTR default translator will be used.  This provision is retained from the previous Order. The Discharger has collected field data for translator development during a previous study, but the study was insufficient.

- Provision F.15 (Status Reports on New or Upgraded Facility): This provision is based on BPJ and is retained from the previous Order. These reports are intended to keep the Regional Water Board informed as to progress towards the construction of the new WWTP.

- Provision F.16 (Permitted Treatment Plant Flows): This Provision is based on 40 CFR 122.41(l) (Reporting requirements).

- Provision F.17 (Storm Water Pollution Prevention Plan (SWPPP)): This provision is retained from the previous Order. This provision requires ongoing implementation of the Storm Water Pollution Prevention Plan, to ensure compliance with Federal storm water pollution controls.

- Provision F. 18 (Pretreatment Program): This provision requires the Discharger to implement and enforce its approved pretreatment program in accordance with Federal pretreatment regulations (40 CFR Part 403).

- Provision F. 19 (Wastewater Facilities, Review and Evaluation, Status Reports): This provision is based on the previous Order and the Basin Plan.

- Provision F.20 (Operations and Maintenance Manual, Review and Status Reports) and F.21 (Contingency Plan, Review and Status Report):  These provisions are based on the Basin Plan, the requirements of 40 CFR 122, and the previous permit.

- Provision F.22 (303(d)-listed Pollutants Site-Specific Objective and TMDL Status Review):  Consistent with the SIP, the Discharger shall participate in the development of region-wide TMDL or SSO studies.  By January 31 of each year, the Discharger shall submit an update to the Regional Water Board to document progress made on source control and pollutant minimization measures and development of TMDL or SSO.  Regional Water Board staff shall review the status of TMDL development.  This Order may be reopened in the future to reflect any changes required by TMDL development.

- Provision F.23 (New Water Quality Objectives):  This provision allows future modification of the permit and permit effluent limitations as necessary in response to updated WQOs that may be established in the future.  This provision is based on 40 CFR 123.

- Provision F.24 (Self-Monitoring Program):  The Discharger is required to conduct monitoring of the permitted discharges in order to evaluate compliance with permit conditions.  Monitoring requirements are contained in the Self Monitoring Program (SMP) of the Permit.  This provision requires compliance with the SMP, and is based on 40 CFR 122.63.  The SMP is a standard requirement in almost all NPDES permits issued by the Regional Water Board, including this Order.  It contains definitions of terms, specifies general sampling and analytical protocols, and sets out requirements for reporting of spills, violations, and routine monitoring data in accordance with NPDES regulations, the California Water Code, and Regional Water Board’s policies.  The SMP also contains a sampling program specific for the facility.  It defines the sampling stations and frequency, the pollutants to be monitored, and additional reporting requirements.  Pollutants to be monitored include all parameters for which effluent limitations are specified.  Monitoring for additional constituents, for which no effluent limitations are established, is also required to provide data for future completion of RPAs for them.

- Provision F.25 (Standard Provisions and Reporting Requirements):  The purpose of this provision is to require compliance with the standard provisions and reporting requirements given in this Regional Water Board's document titled Standard Provisions and Reporting Requirements for NPDES Surface Water Discharge Permits, August 1993 (the Standard Provisions), or any amendments thereafter.  That document is incorporated in the permit as an attachment to it. Where provisions or reporting requirements specified in the permit are different from equivalent or related provisions or reporting requirements given in the Standard Provisions, the permit specifications shall apply.  The standard provisions and reporting requirements given in the above document are based on various state and federal regulations with specific references cited therein.

- Provision F.26 (Change in Control or Ownership):  This provision is based on 40 CFR 122.61.

- Provision F.27 (Permit Reopener): This provision is based on 40 CFR 123.

- Provision F.28 (NPDES Permit): This provision is based on 40 CFR 123.

- Provisions F.29 (Order Expiration and Reapplication):  This provision is based on 40 CFR 122.46(a).

V.     WASTE DISCHARGE REQUIREMENT APPEALS

Any person may petition the State Water Resources Control Board to review the decision of the Regional Water Board regarding the Waste Discharge Requirements.  A petition must be made within 30 days of the Regional Water Board public hearing.

VI.    ATTACHMENTS

Attachment 1:  Representative Ambient Hardness Value Calculation

Attachment 2:  Effluent Data (Priority Inorganic Pollutants)

Attachment 3:  RPA Results for Priority Pollutants

Attachment 4:  Calculation of Final WQBELs

Attachment 5:  General Basis for Final Compliance Dates

Attachment 6:  Mercury Mass Trigger Calculation

Attachment 7:  Total Coliform Conditions in the Petaluma River

Attachment 1

Representative Ambient Hardness Value Calculation

Attachment 2

Effluent Data

(Priority Inorganic Pollutants)

Attachment 3

RPA Results for Priority Pollutants

Attachment 4

Calculation of Final WQBELs

Attachment 5

General Basis for Final Compliance Dates

Attachment 6

Mercury Mass Trigger Calculation

Attachment 7

Total Coliform Conditions in the Petaluma River

(Technical Memorandum)