# ATTACHMENT F

# DEFINITION OF TERMS

Coagulated Wastewater: Oxidized wastewater in which colloidal and finely divided suspended

matter have been destabilized and agglomerated upstream from a filter by the addition of

suitable floc-forming chemicals.

Conventional Tertiary Treatment: A treatment chain that utilizes a sedimentation unit process

between the coagulation and filtration processes and produces an effluent that meets the

definition for disinfected tertiary recycled water.

Disinfected Secondary-23: Adequately disinfected, oxidized wastewater in which the median

number of coliform organisms in the effluent does not exceed 23 per 100 milliliters, as

determined from the bacteriological results of the last seven days for which analyses have been

completed, and the number of coliform organisms does not exceed 240 per 100 milliliters in

more than one sample in any 30 day period.

Disinfected Secondary-2.3: Adequately disinfected, oxidized wastewater in which the median

number of coliform organisms in the effluent does not exceed 2.3 per 100 milliliters, as

determined from the bacteriological results of the last seven days for which analyses have been

completed, and the number of coliform organisms does not exceed 23 per 100 milliliters in

more than one sample in any 30 day period.

Disinfected Tertiary: Adequately disinfected, oxidized, coagulated, clarified, filtered wastewater

in which meets the following criteria:

(a)  	A filtered wastewater which has been disinfected by either:

(1) 	A chlorine disinfection process that provides a CT (chorine concentration

times modal contact time) value of not less than 300 milligram-minutes per

liter at all times with a modal contact time of at least 90 minutes, based on

peak daily design flow (or an equivalent combination of chlorine residual

concentration and contact time subject to Executive Officer approval); or

2)  	A disinfection process that, when combined with the filtration process, has been 				demonstrated to reduce the concentration of plaque-forming units of F-specific 				bacteriophage MS-2, or polio virus, per unit volume of water in the wastewater to one 				hundred thousandths (1/100,000) of the initial concentration in the filter

influent throughout the range of qualities of wastewater that will occur during the reuse 			process. A virus that is at least a resistant to disinfection as polio virus may be used 				for purposes of the demonstration.

(b)  	The median concentration of total coliform bacteria measured in the disinfected effluent does 		not exceed an MPN of 2.2 per 100 milliliters utilizing the bacteriological results of the last 			seven days for which analyses have been completed and the number of total coliform bacteria

does not exceed maximum an MPN of 23 per 100 milliliters in more than one sample in any 30 		day period. No sample shall exceed an MPN of 240 total coliform bacteria per 100 milliliters.

1

(c)  	The turbidity of filtered recycled water shall not exceed any of the following:

1)     	2 NTU daily average, 5 NTU more than 5 percent of the time, or 10 NTU at any time.

Coagulation need not be used as part of the treatment process provided the turbidity of the 			influent to the filters does not exceed 5 NTU more than 5 percent of the time.

Disinfected Wastewater: Wastewater in which the pathogenic organisms have been destroyed by chemical, physical or biological means.

Distributor: A municipal or water service agency which receives recycled water from a

Producer for the purpose of distribution to users. The Distributor may provide additional treatment to the water, depending upon the intended use.

Dual Plumbed System: A system that utilizes separate piping systems for recycled water and potable water within a facility and where the reclaimed water is used for either of the following purposes:

a) 	To serve multiple plumbed outlets used by the public within a building.

b) 	Landscape irrigation at individual residences.

Filtered Wastewater: An oxidized and coagulated wastewater which has been passed through natural undisturbed soils or filter media so that the turbidity does not exceed any of the following:

(a) 	a daily average of 2 NTU

(b)  	5 NTU more than 5 percent of the time

(c)  	10 NTU at any time

F-specific bacteriophage MS-2: A strain of a specific type of virus that infects coliform bacteria

that is traceable to the American Type Culture Collection (ATCC 15597B1 1) and is grown on

lawns of E. Coli (ATCC 15597).

Landscape Impoundment: A body of water which is used for aesthetic enjoyment or landscape

irrigation or which otherwise serves a similar function and is not intended to include public contact.

Modal Contact Time: The amount of time elapsed between the time a tracer, such as salt or dye,

is injected into the effluent at the entrance to a chamber and the time that the highest

concentration of the tracer is observed in the effluent from the chamber.

Nonrestricted Recreational Impoundment: An impoundment of recycled water, in which no

limitations are imposed on body-contact water recreational activities.

NTU (Nephelometric turbidity unit): A measurement of turbidity as determined by the ratio of

the intensity of light scattered by the sample to the intensity of incident light using approved

laboratory methods.

Oxidized Wastewater. Wastewater in which the organic matter has been stabilized, is

nonputrescible, and contains dissolved oxygen.

2

Producer: The entity which treats domestic wastewater to obtain reclaimed water.

Reclaimed (Recycled): Water: Water which. as a result of treatment of waste, is suitable for a

direct beneficial use or a controlled use that would not otherwise occur.

Recycled Water Supervisor: A person designated, by the Producer of recycled water, to

discharge the responsibility of the Producer for: (a) acting as the supplier’s coordinator and

direct contact between the supplier and the owner or manager of the property upon which

recycled water will be used; (b) proper operation of the system for transporting/distributing

recycled water; (c) providing orientation to personnel involved in transporting/distributing

recycled water; (d) implementing and complying with conditions of all Water Reuse

Orders/Permits and associated documents relevant to use of recycled water; and (e) monitoring

operations at the recycled water use area(s) for prevention of potential hazards.

Restricted access golf course: A golf course where public access is controlled so that areas

irrigated with recycled water cannot be used as if they were part of a park, playground, or

school yard and where irrigation is conducted only in areas and during periods when the golf

course Is not being used by golfers.

Restricted Recreational Impoundment: An impoundment of recycled water in which recreation

is limited to fishing, boating, and other non-body-contact water recreational activities.

Spray Irrigation: The application of recycled water to crops to maintain vegetation or support

growth of vegetation by applying it from sprinklers or orifices in piping. Spray irrigation does

not include drip irrigation.

Surface Irrigation: Application of recycled water by means other than spraying such that

contact between the edible portion of any food crop and recycled water is prevented (i.e., drip

or flood irrigation).

Use Site Area: An area of recycled water use with defined boundries. A use site area may contain

one or more facilities.

User Supervisor: A person designated, by the owner or manager of the property upon which

recycled water will be applied, to discharge the responsibility of the owner or manager of the

property for: (a) installation, operation and maintenance of a system that enables recycled

water to be used; (b) for prevention of potential hazards; (C) implementing and complying with

conditions of all Water Reuse Orders/Permits and associated documents; and

(d) coordination with the cross-connection control program of the supplier of drinking water

and the local health/environmental health agency. (A Recycled Water Supervisor and User

Supervisor may be one in the same in some instances).

3